## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-W007S-PEDCO-110-IN-DT-0004 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1680 |  |  | Transmital Date: 12/10/2022
Document Title: Data Sheets For Pressure & Safety Relief Valves - Extension of Binak B/C Manifold |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-IN-TR-1680 |  |  | Transmital Date: 12/10/2022
[5 empty] | CRS No: NISOC-CRS-BK-W007S-PEDCO-110-IN-DT-0004_D02 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | در خصوص متریال اعلام شده تطابق مشخصات با PMS تایید شده الزامی است. در ضمن با توجه به اینکه تعیین نهایی متریال با سازنده می باشد ضروری است در محله TBE با سازندگان در خصوص جنس شفاف سازی گردد. |  | 1401-2294-385253 | 1401/10/11 | به توجه به نظر کارفرمای محترم مدرک متناسب با آخرین نسخه مدارک مرجع تهیه گردید.
2 | مبنای دمای در نظر گرفته شده Relieving temp.°c جهت شیرهای TRV و PRV بیان گردد. |  | 1401-2294-385253 | 1401/10/11 | مبنای دمای در نظر گرفته شده Relieving temp.°c جهت شیر های PRV همان دمای عملیاتی می باشد چرا که سناریو غالب BLOCKED OUTLET می باشد و برای TRV ها نیز مبنای Relieving temp.°c بر اساس ماژول Thermal Expansion نرم افزار hysys می باشد.
3 | ویرایش درج شده جهت مدرک PID اصلاح گردد. |  | 1401-2294-385253 | 1401/10/11 | به توجه به نظر کارفرمای محترم مدرک متناسب با آخرین نسخه مدارک مرجع تهیه گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: |  |  |  |  | Date: