## Cover
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
ELECTRICAL POWER & CONTROL CABLE SCHEDULE
شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 13
9184 – 073 - 053 |  |  | BK |  | GCS | PEDCO | 120 |  | EL | LI | 0002 | D01
طرح نگهداشت و افزایش تولید 27 مخزن
ELECTRICAL POWER & CONTROL CABLE SCHEDULE نگهداشت و افزایش تولید میدان نفتی بینک
D01 |  | Nov.2023 |  | IFA |  |  |  | H.Shakiba |  |  | M.Fakharian |  | S.Faramarzpour
D00 |  | June.2022 |  | IFC |  |  |  | H.Shakiba |  |  | M.Fakharian |  | M.Mehrshad
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
Class: 1 |  |  |  | CLIENT Doc. Number: F0Z-709067
status: | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved

## REVISION
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
ELECTRICAL POWER & CONTROL CABLE SCHEDULE
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 13
9184 – 073 - 053 |  |  | BK | GCS |  | PEDCO | 120 | EL | LI | 0002 |  | D01
REVISION RECORD SHEET
Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D01 |  | D02 | D03 | D04
1 | X | X | [6 empty] | 51
2 | X | X | [6 empty] | 52
3 | X | X | [6 empty] | 53
4 | X | X | [6 empty] | 54
5 | X | X | [6 empty] | 55
6 | X | X | [6 empty] | 56
7 | X | X | [6 empty] | 57
8 | X | X | [6 empty] | 58
9 | X | X | [6 empty] | 59
10 |  | X | [6 empty] | 60
11 |  | X | [6 empty] | 61
12 |  | X | [6 empty] | 62
13 |  | X | [6 empty] | 63
14 | [8 empty] | 64
15 | [8 empty] | 65
16 | [8 empty] | 66
17 | [8 empty] | 67
18 | [8 empty] | 68
19 | [8 empty] | 69
20 | [8 empty] | 70
21 | [8 empty] | 71
22 | [8 empty] | 72
23 | [8 empty] | 73
24 | [8 empty] | 74
25 | [8 empty] | 75
26 | [8 empty] | 76
27 | [8 empty] | 77
28 | [8 empty] | 78
29 | [8 empty] | 79
30 | [8 empty] | 80
31 | [8 empty] | 81
32 | [8 empty] | 82
33 | [8 empty] | 83
34 | [8 empty] | 84
35 | [8 empty] | 85
36 | [8 empty] | 86
37 | [8 empty] | 87
38 | [8 empty] | 88
39 | [8 empty] | 89
40 | [8 empty] | 90
41 | [8 empty] | 91
42 | [8 empty] | 92
43 | [8 empty] | 93
44 | [8 empty] | 94
45 | [8 empty] | 95
46 | [8 empty] | 96
47 | [8 empty] | 97
48 | [8 empty] | 98
49 | [8 empty] | 99
50 | [8 empty] | 100

## LEGEND
1. ELECTRICAL CABLE NUMBERING SYSTEM
XXX-XXXXX- XX 1 2 3
(1) 1ST Group (Cable Type Commodity Code):
H: High Voltage Power Cable (20 KV & Above)
M: Medium Voltage Power Cable (3.3, 6 KV & up to 20 KV)
L: Low Voltage Power Cable (Voltage Less Than 1KV)
C: Control Cables
I: Instrument Cable
(2) 2ND Group
From Equipment
(3) 3RD Group
Consumer Description: To Equipment Which will be fed.
2. CABLE TYPE
A: Cu/XLPE/Bd/Lsh/Bd/SWA/PVC - N2XKYRY (LV MULTI-CORE WITH LEAD SHEATH)
B: Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE)
C: Cu/XLPE/Bd/AWA/PVC - N2XRY (LV SINGLE-CORE)
D: Cu/PVC/Bd/Lsh/Bd/SWA/PVC - NYKYRY (CONTROL MULTI-CORE WITH LEAD SHEATH)
E: Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE)
F: Cu/SC/XLPE/SC/SCT/Lsh/Bd/SWA/PVC - N2XSEYKYRY (MV MULTI-CORE WITH LEAD SHEATH)
G: Cu/SC/XLPE/SC/SCT/Lsh/Bd/AWA/PVC - N2XSYKYRY (MV SINGLE-CORE WITH LEAD SHEATH)
H: Cu/SC/XLPE /SC/SCT/CWS/Bd/AWA/PVC - N2XSYRY (MV SINGLE-CORE)
I: Cu/SC/XLPE/SC/SCT/ICWS/Bd/SWA/PVC - N2XSEYRY (MV MULTI-CORE)
J: CU/SM/XLPE/SM/SC/PVC/SWA/PVC - N2XSEYRY (HV MULTI-CORE)
K: CU/SM/XLPE/SM/SC/PVC/AWA/PVC - N2XSYRY (HV SINGLE-CORE)
R: Cu/PVC/OSCR/Bd/LSH/Bd/SWA/PVC (RTD CABLE)
S: CU/XLPE/PVC - N2XY (LV SINGLE-CORE FLEXIBLE)
Z: FIRE RESISTANT OR MICC LIGHTING CABLE (FOR HAZARDOUS AREAS SUCH AS BATTERY ROOMS ...)
Notes:
1- The control cable of IRP Pump will be supplied by vendor
Reference documents are as below:
Area Electrical Cable Route & Section Layout of Well Pads (BK-SSGRL-PEDCO-110-EL-PY-0006)
Electrical Cable Route & Section Layout For Switchgear Building of Well Pads (BK-SSGRL-PEDCO-110-EL-PY-0007)
تسهیلات
ELECTRICAL POWER & CONTROL CABLE SCHEDULE
شماره صفحه: 3 از 13
NISOC
شماره پیمان:
9184 – 073 - 053
نگهداشت و افزایش تولید میدان نفتی بینک
سطح‌الارض
احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
120
EL
LI
0002
D01
بسته کاری
GCS
پروژه
BK

## GCS
Item | Rev | Cable Tag No. | Service Voltage (KV) | Equipment Tag |  | Rating (KW) | Size | Cable Size (mm) |  |  |  | Length (m) | Cable Gland Size |  | O.D (mm) | Cable Type | Description | Rout
|  |  |  | From | To |  |  | Core | Phase | N | E |  | Source | Field
1 | D01 | M-11SWGA-TR001 | 11 | GCS-11-SWG-001A | GCS-TR-001 | 1250KVA | 3×95 | 3C | 95 | - | - | 70 | M90 | M90 | 79.1 | I | Transformer-001 11/.42 KV | -
2 | D01 | C-11SWGA-RCP-01 | 0.11DC | GCS-11-SWG-001A | RCP | - | 12×2.5 | 12C | 2.5 | - | - | 40 | M25 | M25 | 24.4 | E | From 11KV Switchgear A to RCP | -
3 | D01 | L-NSWGA-TR001-A1 | 0.4 | GCS-400-NSWG-001A | GCS-TR-001 | 1250KVA | 1×300 | 1C | 300 | - | - | 20 | M40 | M40 | 34.2 | C | from Secondary Side of Transformer 001 to LV Switchgear | -
4 | D01 | L-NSWGA-TR001-A2 | 0.4 | GCS-400-NSWG-001A | GCS-TR-001 | 1250KVA | 1×300 | 1C | 300 | - | - | 20 | M40 | M40 | 34.2 | C | from Secondary Side of Transformer 001 to LV Switchgear | -
5 | D01 | L-NSWGA-TR001-A3 | 0.4 | GCS-400-NSWG-001A | GCS-TR-001 | 1250KVA | 1×300 | 1C | 300 | - | - | 20 | M40 | M40 | 34.2 | C | from Secondary Side of Transformer 001 to LV Switchgear | -
6 | D01 | L-NSWGA-TR001-A4 | 0.4 | GCS-400-NSWG-001A | GCS-TR-001 | 1250KVA | 1×300 | 1C | 300 | - | - | 20 | M40 | M40 | 34.2 | C | from Secondary Side of Transformer 001 to LV Switchgear | -
7 | D01 | L-NSWGA-TR001-B1 | 0.4 | GCS-400-NSWG-001A | GCS-TR-001 | 1250KVA | 1×300 | 1C | 300 | - | - | 20 | M40 | M40 | 34.2 | C | from Secondary Side of Transformer 001 to LV Switchgear | -
8 | D01 | L-NSWGA-TR001-B2 | 0.4 | GCS-400-NSWG-001A | GCS-TR-001 | 1250KVA | 1×300 | 1C | 300 | - | - | 20 | M40 | M40 | 34.2 | C | from Secondary Side of Transformer 001 to LV Switchgear | -
9 | D01 | L-NSWGA-TR001-B3 | 0.4 | GCS-400-NSWG-001A | GCS-TR-001 | 1250KVA | 1×300 | 1C | 300 | - | - | 20 | M40 | M40 | 34.2 | C | from Secondary Side of Transformer 001 to LV Switchgear | -
10 | D01 | L-NSWGA-TR001-B4 | 0.4 | GCS-400-NSWG-001A | GCS-TR-001 | 1250KVA | 1×300 | 1C | 300 | - | - | 20 | M40 | M40 | 34.2 | C | from Secondary Side of Transformer 001 to LV Switchgear | -
11 | D01 | L-NSWGA-TR001-C1 | 0.4 | GCS-400-NSWG-001A | GCS-TR-001 | 1250KVA | 1×300 | 1C | 300 | - | - | 20 | M40 | M40 | 34.2 | C | from Secondary Side of Transformer 001 to LV Switchgear | -
12 | D01 | L-NSWGA-TR001-C2 | 0.4 | GCS-400-NSWG-001A | GCS-TR-001 | 1250KVA | 1×300 | 1C | 300 | - | - | 20 | M40 | M40 | 34.2 | C | from Secondary Side of Transformer 001 to LV Switchgear | -
13 | D01 | L-NSWGA-TR001-C3 | 0.4 | GCS-400-NSWG-001A | GCS-TR-001 | 1250KVA | 1×300 | 1C | 300 | - | - | 20 | M40 | M40 | 34.2 | C | from Secondary Side of Transformer 001 to LV Switchgear | -
14 | D01 | L-NSWGA-TR001-C4 | 0.4 | GCS-400-NSWG-001A | GCS-TR-001 | 1250KVA | 1×300 | 1C | 300 | - | - | 20 | M40 | M40 | 34.2 | C | from Secondary Side of Transformer 001 to LV Switchgear | -
15 | D01 | L-NSWGA-TR001-N1 | 0.4 | GCS-400-NSWG-001A | GCS-TR-001 | 1250KVA | 1×300 | 1C | - | 300 | - | 20 | M40 | M40 | 34.2 | C | from Secondary Side of Transformer 001 to LV Switchgear | -
16 | D01 | L-NSWGA-TR001-N2 | 0.4 | GCS-400-NSWG-001A | GCS-TR-001 | 1250KVA | 1×300 | 1C | - | 300 | - | 20 | M40 | M40 | 34.2 | C | from Secondary Side of Transformer 001 to LV Switchgear | -
17 | D01 | C-NSWGA-TR001-1 | 0.11DC | GCS-400-NSWG-001A | GCS-TR-001 | - | 12×2.5 | 12C | 2.5 | - | - | 20 | M25 | M25 | 24.4 | E | Transformer 001 Mechanical Protection | -
18 | D01 | C-NSWGA-TR001-2 | - | GCS-400-NSWG-001A | GCS-TR-001 | - | 3×4 | 3C | 4 | - | - | 20 | M20 A | M20 A | 16.6 | E | Neutral CT of Transformer 001 | -
19 | D01 | C-NSWGA-TR001-3 | 0.11DC | GCS-400-NSWG-001A | GCS-TR-001 | - | 12×2.5 | 12C | 2.5 | - | - | 50 | M25 | M25 | 24.4 | E | Interlock/Intertrip to Upstrem | -
20 | D01 | M-11SWGB-TR002 | 11 | GCS-11-SWG-001B | GCS-TR-002 | 1250KVA | 3×95 | 3C | 95 | - | - | 70 | M90 | M90 | 79.1 | I | Transformer-002 11/.42 KV | -
21 | D01 | C-11SWGB-RCP-02 | 0.11DC | GCS-11-SWG-001B | RCP | - | 12×2.5 | 12C | 2.5 | - | - | 40 | M25 | M25 | 24.4 | E | From 11KV Switchgear B to RCP | -
22 | D01 | L-NSWGB-TR002-A1 | 0.4 | GCS-400-NSWG-001B | GCS-TR-002 | 1250KVA | 1×300 | 1C | 300 | - | - | 20 | M40 | M40 | 34.2 | C | from Secondary Side of Transformer 002 to LV Switchgear | -
23 | D01 | L-NSWGB-TR002-A2 | 0.4 | GCS-400-NSWG-001B | GCS-TR-002 | 1250KVA | 1×300 | 1C | 300 | - | - | 20 | M40 | M40 | 34.2 | C | from Secondary Side of Transformer 002 to LV Switchgear | -
24 | D01 | L-NSWGB-TR002-A3 | 0.4 | GCS-400-NSWG-001B | GCS-TR-002 | 1250KVA | 1×300 | 1C | 300 | - | - | 20 | M40 | M40 | 34.2 | C | from Secondary Side of Transformer 002 to LV Switchgear | -
25 | D01 | L-NSWGB-TR002-A4 | 0.4 | GCS-400-NSWG-001B | GCS-TR-002 | 1250KVA | 1×300 | 1C | 300 | - | - | 20 | M40 | M40 | 34.2 | C | from Secondary Side of Transformer 002 to LV Switchgear | -
26 | D01 | L-NSWGB-TR002-B1 | 0.4 | GCS-400-NSWG-001B | GCS-TR-002 | 1250KVA | 1×300 | 1C | 300 | - | - | 20 | M40 | M40 | 34.2 | C | from Secondary Side of Transformer 002 to LV Switchgear | -
27 | D01 | L-NSWGB-TR002-B2 | 0.4 | GCS-400-NSWG-001B | GCS-TR-002 | 1250KVA | 1×300 | 1C | 300 | - | - | 20 | M40 | M40 | 34.2 | C | from Secondary Side of Transformer 002 to LV Switchgear | -
28 | D01 | L-NSWGB-TR002-B3 | 0.4 | GCS-400-NSWG-001B | GCS-TR-002 | 1250KVA | 1×300 | 1C | 300 | - | - | 20 | M40 | M40 | 34.2 | C | from Secondary Side of Transformer 002 to LV Switchgear | -
29 | D01 | L-NSWGB-TR002-B4 | 0.4 | GCS-400-NSWG-001B | GCS-TR-002 | 1250KVA | 1×300 | 1C | 300 | - | - | 20 | M40 | M40 | 34.2 | C | from Secondary Side of Transformer 002 to LV Switchgear | -
30 | D01 | L-NSWGB-TR002-C1 | 0.4 | GCS-400-NSWG-001B | GCS-TR-002 | 1250KVA | 1×300 | 1C | 300 | - | - | 20 | M40 | M40 | 34.2 | C | from Secondary Side of Transformer 002 to LV Switchgear | -
31 | D01 | L-NSWGB-TR002-C2 | 0.4 | GCS-400-NSWG-001B | GCS-TR-002 | 1250KVA | 1×300 | 1C | 300 | - | - | 20 | M40 | M40 | 34.2 | C | from Secondary Side of Transformer 002 to LV Switchgear | -
32 | D01 | L-NSWGB-TR002-C3 | 0.4 | GCS-400-NSWG-001B | GCS-TR-002 | 1250KVA | 1×300 | 1C | 300 | - | - | 20 | M40 | M40 | 34.2 | C | from Secondary Side of Transformer 002 to LV Switchgear | -
33 | D01 | L-NSWGB-TR002-C4 | 0.4 | GCS-400-NSWG-001B | GCS-TR-002 | 1250KVA | 1×300 | 1C | 300 | - | - | 20 | M40 | M40 | 34.2 | C | from Secondary Side of Transformer 002 to LV Switchgear | -
34 | D01 | L-NSWGB-TR002-N1 | 0.4 | GCS-400-NSWG-001B | GCS-TR-002 | 1250KVA | 1×300 | 1C | - | 300 | - | 20 | M40 | M40 | 34.2 | C | from Secondary Side of Transformer 002 to LV Switchgear | -
35 | D01 | L-NSWGB-TR002-N2 | 0.4 | GCS-400-NSWG-001B | GCS-TR-002 | 1250KVA | 1×300 | 1C | - | 300 | - | 20 | M40 | M40 | 34.2 | C | from Secondary Side of Transformer 002 to LV Switchgear | -
36 | D01 | C-NSWGA-TR002-1 | 0.11DC | GCS-400-NSWG-001B | GCS-TR-002 | - | 12×2.5 | 12C | 2.5 | - | - | 20 | M25 | M25 | 24.4 | E | Transformer 002 Mechanical Protection | -
37 | D01 | C-NSWGA-TR002-2 | - | GCS-400-NSWG-001B | GCS-TR-002 | - | 3×4 | 3C | 4 | - | - | 20 | M20 A | M20 A | 16.6 | E | Neutral CT of Transformer 002 | -
38 | D01 | C-NSWGA-TR002-3 | 0.11DC | GCS-400-NSWG-001B | GCS-TR-002 | - | 12×2.5 | 12C | 2.5 | - | - | 50 | M25 | M25 | 24.4 | E | Interlock/Intertrip to Upstrem | -
39 | D01 | M-11SWGB-TR003 | 11 | GCS-11-SWG-001B | GCS-TR-03 | 800 kVA | 3×95 | 3C | 95 | - | - | 70 | M90 | M90 | 79.1 | I | from Switchgear 11SWGB to Fire Water Transformer 003 | -
40 | D01 | C-11SWGB-RCP-03 | 0.11DC | GCS-11-SWG-001B | RCP | - | 12×2.5 | 12C | 2.5 | - | - | 40 | M25 | M25 | 24.4 | E | From 11SWGB Switchgear to RCP for Fire Water | -
41 | D01 | M-TR003-NGR | 3.3 | GCS-TR-003 | GCS-3.3-NGR-01 | - | 1×95 | 1C | 95 | - | - | 10 | M40 | M40 | 35.7 | H | NGR | -
42 | D01 | C-3.3SWG-TR003-1 | 0.11DC | GCS-3.3-SWG-001 | GCS-TR-03 | - | 12×2.5 | 12C | 2.5 | - | - | 70 | M25 | M25 | 24.4 | E | Transformer 003 Mechanical Protection | -
43 | D01 | C-3.3SWG-TR003-2 | - | GCS-3.3-SWG-001 | GCS-TR-03 |  | 3×4 | 3C | 4 | - | - | 70 | M20 A | M20 A | 16.6 | E | Neutral CT of Transformer 003 | -
44 | D01 | M-3.3SWG-TR003 | 3.3 | GCS-3.3-SWG-001 | GCS-TR-03 | - | 3×95 | 3C | 95 | - | - | 70 | M75 | M75 | 68.8 | I | from 3.3 Switchgear to Transformer 003 | -
45 | D01 | M-3.3SWG-P2301A | 3.3 | GCS-3.3-SWG-001 | P-2301A | 300 | 3×95 | 3C | 95 | - | - | 250 | M75 | M75 | 68.8 | I | Fire Water Electric Pump | 36/40/41/42/56
46 | D01 | C-3.3SWG-LCS | 0.11DC | GCS-3.3-SWG-001 | P-2301A | - | 10×2.5 | 10C | 2.5 | - | - | 250 | M32 | M32 |  | E | LCS for P-2301A | 36/40/41/42/56
47 | D01 | C-3.3SWG-IRP | 0.11DC | GCS-3.3-SWG-001 | IRP (DCS) | - | 7×2.5 | 7C | 2.5 | - | - | 45 | M25 | M25 | 20 | E | IRP (DCS) for P-2301A | -
48 | D01 | M-11SWGA-C2101-A | 11 | GCS-11-SWG-001A | C-2101A | 1250 | 3×95 | 3C | 95 | - | - | 270 | M90 | M90 EX | 87.7 | F | First & Second Stage Gas Compressor C-2101A | 01/04/05/07/09/11/12
49 | D01 | L-11SWGA-SPH-A | 0.23 | GCS-11-SWG-001A | Space Heater | 0.3 | 2×4 | 2C | 4 | 4 | - | 270 | M25 | M25 EX | 21 | A | Space Heater for Gas Compressor C-2101A | 01/04/05/07/09/11/12
50 | D01 | C-11SWGA-IRP-A | 0.11DC | GCS-11-SWG-001A | IRP (UCP-A) | - | 12×2.5 | 12C | 2.5 | - | - | 40 | M25 | M25 | 24.4 | E | IRP (UCP-A) for Gas Compressor C-2101A | -
51 | D01 | C-11SWGA-IRP-A (ESD) | 0.11DC | GCS-11-SWG-001A | IRP (ESD) | - | 3×2.5 | 3C | 2.5 | - | - | 40 | M25 | M25 | 20.5 | E | IRP (ESD) for Gas Compressor C-2101A | -
52 | D01 | C-11SWGA-C2101-A | 0.11DC | GCS-11-SWG-001A | C-2101A | - | 3×4 | 3C | 4 | - | - | 270 | M25 | M25 EX | 22.6 | D | Ammeter for Gas Compressor C-2101A | 01/04/05/07/09/11/12
53 | D01 | C-11SWGA-RTD2101-A | - | UCP-A | C-2101A | - | 12×3×1.5 | 36C | 1.5 | - | - | 300 | M50 | M50 | 41 | R | RTD for Gas Compressor C-2101A (From Control Room) | 01/04/05/07/09/11/12
54 | D01 | C-11SWGA-2101-A | - | GCS-11-SWG-001A | C-2101A | - | 3×6 | 3C | 6 | - | - | 270 | M25 | M25 EX | 23.5 | D | Differential Protection of C-2101A | 01/04/05/07/09/11/12
55 | D01 | M-11SWGA-CAP-A | 11 | GCS-11-SWG-001A | Cap Bank A | 360 kvar | 3×95 | 3C | 95 | - | - | 30 | M90 | M90 | 79.1 | I | Capacitor Bank for Gas Compressor C-2101A | -
56 | D01 | C-11SWGA-CAP-A | 0.11DC | GCS-11-SWG-001A | Cap Bank A | - | 7×2.5 | 7C | 2.5 | - | - | 30 | M25 | M25 | 20 | E | Control for Capacitor Bank of C-2101A | -
57 | D01 | L-NSWGA-MCC2101A | 0.4 | GCS-400-NSWG-001A | MCC-2101A | 50 | 3×35+16 | 4C | 35 | 16 | - | 25 | M32 | M32 | 32.1 | B | Normal Panel for Gas Compressor C-2101A (Auxiliary) | -
58 | D01 | L-MCC2101A-OH | 0.23 | MCC-2101A | Oil Heater | 1.5 | 2×16 | 2C | 16 | 16 | - | 250 | M32 | M32 EX | 27.2 | A | Oil Heater for Gas Compressor C-2101A | 01/04/05/07/09/11/12
59 | D01 | C-MCC2101A-OH | 0.23 | MCC-2101A | IRP (UCP-A) | - | 12×2.5 | 12C | 2.5 | - | - | 10 | M25 | M25 | 24.4 | E | IRP (UCP-A) for Oil Heater C-2101A | -
60 | D01 | L-MCC2101A-BR | 0.4 | MCC-2101A | Barring Device Motor | 2.2 | 3×6 | 3C | 6 | - | - | 250 | M25 | M25 EX | 23.5 | A | Barring Device Motor for Gas Compressor C-2101A | 01/04/05/07/09/11/12
61 | D01 | C-MCC2101A-BR01 | 0.23 | MCC-2101A | IRP (UCP-A) | - | 12×2.5 | 12C | 2.5 | - | - | 10 | M25 | M25 | 24.4 | E | IRP (UCP-A) for Barring Device Motor C-2101A | -
62 | D01 | C-MCC2101A-BR02 | 0.23 | MCC-2101A | Barring Device Motor | - | 3×4 | 3C | 4 | - | - | 250 | M25 | M25 EX | 22.6 | D | Ammeter for Barring Device Motor C-2101A | 01/04/05/07/09/11/12
63 | D01 | L-MCC2101A-AP | 0.4 | MCC-2101A | Oil Pump | 7.5 | 3×16 | 3C | 16 | - | - | 250 | M32 | M32 EX | 28.2 | A | Oil Pump for Gas Compressor C-2101A (P-2101-AP A) | 01/04/05/07/09/11/12
64 | D01 | C-MCC2101A-AP1 | 0.23 | MCC-2101A | IRP (UCP-A) | - | 12×2.5 | 12C | 2.5 | - | - | 10 | M25 | M25 | 24.4 | E | IRP (UCP-A) for Oil Pump C-2101A | -
65 | D01 | C-MCC2101A-AP2 | 0.23 | MCC-2101A | Oil Pump | - | 3×4 | 3C | 4 | - | - | 250 | M25 | M25 EX | 22.6 | D | Ammeter for Oil Pump C-2101A | 01/04/05/07/09/11/12
66 | D01 | L-MCC2101A-OC | 0.4 | MCC-2101A | Oil Cooler | 5.5 | 3×10 | 3C | 10 | - | - | 250 | M32 | M32 EX | 26.7 | A | Lube Oil Cooler for Gas Compressor C-2101A (AE-2101-OC A) | 01/04/05/07/09/11/12
67 | D01 | C-MCC2101A-OC1 | 0.23 | MCC-2101A | IRP (UCP-A) | - | 12×2.5 | 12C | 2.5 | - | - | 10 | M25 | M25 | 24.4 | E | IRP (UCP-A) for Lube Oil Cooler C-2101A | -
68 | D01 | C-MCC2101A-OC2 | 0.23 | MCC-2101A | Oil Cooler | - | 3×4 | 3C | 4 | - | - | 250 | M25 | M25 EX | 22.6 | D | Ammeter for Lube Oil Cooler Motor C-2101A | 01/04/05/07/09/11/12
69 | D01 | L-MCC2101A-LP | 0.4 | MCC-2101A | Lubricator Pump | 0.55 | 3×4 | 3C | 4 | - | - | 250 | M25 | M25 EX | 22.6 | A | Cylinder Lubricator Pump for Gas Compressor C-2101A (M-2101-LP A) | 01/04/05/07/09/11/12
70 | D01 | C-MCC2101A-LP1 | 0.23 | MCC-2101A | IRP (UCP-A) | - | 12×2.5 | 12C | 2.5 | - | - | 10 | M25 | M25 | 24.4 | E | IRP (UCP-A) for Cylinder Lubricator Pump C-2101A | -
71 | D01 | C-MCC2101A-LP2 | 0.23 | MCC-2101A | Lubricator Pump | - | 3×4 | 3C | 4 | - | - | 250 | M25 | M25 EX | 22.6 | D | Ammeter for Cylinder Lubricator Pump C-2101A | 01/04/05/07/09/11/12
72 | D01 | L-MCC2101A-LH | 0.23 | MCC-2101A | Lubricator Heater | 0.4 | 2×4 | 2C | 4 | 4 | - | 250 | M25 | M25 EX | 21 | A | Cylinder Lubricator Oil Heater for Gas Compressor C-2101A | 01/04/05/07/09/11/12
73 | D01 | C-MCC2101A-LH | 0.23 | MCC-2101A | IRP (UCP-A) | - | 12×2.5 | 12C | 2.5 | - | - | 10 | M25 | M25 | 24.4 | E | IRP (UCP-A) for Cylinder Lubricator Oil Heater C-2101A | -
74 | D01 | L-MCC2101A-AX | 0.4 | MCC-2101A | Aux Pump Motor | 7.5 | 3×16 | 3C | 16 | - | - | 250 | M32 | M32 EX | 28.2 | A | Aux Pump Motor for Gas Compressor C-2101A (P-2101-AX A) | 01/04/05/07/09/11/12
75 | D01 | C-MCC2101A-AX1 | 0.23 | MCC-2101A | IRP (UCP-A) | - | 12×2.5 | 12C | 2.5 | - | - | 10 | M25 | M25 | 24.4 | E | IRP (UCP-A) for Aux Pump Motor C-2101A | -
76 | D01 | C-MCC2101A-AX2 | 0.23 | MCC-2101A | Aux Pump Motor | - | 3×4 | 3C | 4 | - | - | 250 | M25 | M25 EX | 22.6 | D | Ammeter for Aux Pump Motor C-2101A | 01/04/05/07/09/11/12
77 | D01 | L-MCC2101A-WP | 0.4 | MCC-2101A | Main Pump Motor | 7.5 | 3×16 | 3C | 16 | - | - | 250 | M32 | M32 EX | 28.2 | A | Main Pump Motor for Gas Compressor C-2101A (P-2101-WP A) | 01/04/05/07/09/11/12
78 | D01 | C-MCC2101A-WP1 | 0.23 | MCC-2101A | IRP (UCP-A) | - | 12×2.5 | 12C | 2.5 | - | - | 10 | M25 | M25 | 24.4 | E | IRP (UCP-A) for Main Pump Motor C-2101A | -
79 | D01 | C-MCC2101A-WP2 | 0.23 | MCC-2101A | Main Pump Motor | - | 3×4 | 3C | 4 | - | - | 250 | M25 | M25 EX | 22.6 | D | Ammeter for Main Pump Motor C-2101A | 01/04/05/07/09/11/12
80 | D01 | L-MCC2101A-WH | 0.4 | MCC-2101A | Electric Heater | 12 | 3×70+35 | 4C | 70 | 35 | - | 250 | M50 | M50 EX | 47.9 | A | Electric Heater for Gas Compressor C-2101A (P-2101-WH A) | 01/04/05/07/09/11/12
81 | D01 | C-MCC2101A-WH | 0.23 | MCC-2101A | IRP (UCP-A) | - | 12×2.5 | 12C | 2.5 | - | - | 10 | M25 | M25 | 24.4 | E | IRP (UCP-A) for Electric Heater C-2101A | -
82 | D01 | L-MCC2101A-WC | 0.4 | MCC-2101A | Water Console | 4 | 3×10 | 3C | 10 | - | - | 250 | M32 | M32 EX | 26.7 | A | Water Console Cooler Motor for Gas Compressor C-2101A (AE-2101-WC A) | 01/04/05/07/09/11/12
83 | D01 | C-MCC2101A-WC1 | 0.23 | MCC-2101A | IRP (UCP-A) | - | 12×2.5 | 12C | 2.5 | - | - | 10 | M25 | M25 | 24.4 | E | IRP (UCP-A) for Water Console Cooler Motor C-2101A | -
84 | D01 | C-MCC2101A-WC2 | 0.23 | MCC-2101A | Water Console | - | 3×4 | 3C | 4 | - | - | 250 | M25 | M25 EX | 22.6 | D | Ammeter for Water Console Cooler Motor for Gas Compressor C-2101A | 01/04/05/07/09/11/12
85 | D01 | M-11SWGB-C2101-B | 11 | GCS-11-SWG-001B | C-2101B | 1250 | 3×95 | 3C | 95 | - | - | 300 | M90 | M90 EX | 87.7 | F | First & Second Stage Gas Compressor C-2101B | 01/04/05/07/09/11/13/14
86 | D01 | L-11SWGB-SPH-B | 0.23 | GCS-11-SWG-001B | Space Heater | 0.3 | 2×4 | 2C | 4 | 4 | - | 300 | M25 | M25 EX | 21 | A | Space Heater for Gas Compressor C-2101B | 01/04/05/07/09/11/13/14
87 | D01 | C-11SWGB-IRP-B | 0.11DC | GCS-11-SWG-001B | IRP (UCP-B) | - | 12×2.5 | 12C | 2.5 | - | - | 40 | M25 | M25 | 24.4 | E | IRP (UCP-B) for Gas Compressor C-2101B | -
88 | D01 | C-11SWGB-IRP-B (ESD) | 0.11DC | GCS-11-SWG-001B | IRP (ESD) | - | 3×2.5 | 3C | 2.5 | - | - | 40 | M25 | M25 | 20.5 | E | IRP (ESD) for Gas Compressor C-2101B | -
89 | D01 | C-11SWGB-C2101-B | 0.11DC | GCS-11-SWG-001B | C-2101B | - | 3×4 | 3C | 4 | - | - | 300 | M25 | M25 EX | 22.6 | D | Ammeter for Gas Compressor C-2101B | 01/04/05/07/09/11/13/14
90 | D01 | C-11SWGB-RTD2101-B | - | UCP-B | C-2101B | - | 12×3×1.5 | 36C | 1.5 | - | - | 330 | M50 | M50 | 41 | R | RTD for Gas Compressor C-2101B (From Control Room) | 01/04/05/07/09/11/13/14
91 | D01 | C-11SWGB-2101-B | - | GCS-11-SWG-001B | C-2101B | - | 3×6 | 3C | 6 | - | - | 300 | M25 | M25 EX | 23.5 | D | Differential Protection of C-2101B | 01/04/05/07/09/11/13/14
92 | D01 | M-11SWGB-CAP-B | 11 | GCS-11-SWG-001B | Cap Bank B | 360 kvar | 3×95 | 3C | 95 | - | - | 30 | M90 | M90 | 79.1 | I | Capacitor Bank for Gas Compressor C-2101B | -
93 | D01 | C-11SWGB-CAP-B | 0.11DC | GCS-11-SWG-001B | Cap Bank B | - | 7×2.5 | 7C | 2.5 | - | - | 30 | M25 | M25 | 20 | E | Control for Capacitor Bank of C-2101B | -
94 | D01 | L-NSWGB-MCC2101B | 0.4 | GCS-400-NSWG-001B | MCC-2101B | 50 | 3×35+16 | 4C | 35 | 16 | - | 25 | M32 | M32 | 32.1 | B | Normal Panel for Gas Compressor C-2101B (Auxiliary) | -
95 | D01 | L-MCC2101B-OH | 0.23 | MCC-2101B | Oil Heater | 1.5 | 2×16 | 2C | 16 | 16 | - | 280 | M32 | M32 EX | 27.2 | A | Oil Heater for Gas Compressor C-2101A | 01/04/05/07/09/11/13/14
96 | D01 | C-MCC2101B-OH | 0.23 | MCC-2101B | IRP (UCP-B) | - | 12×2.5 | 12C | 2.5 | - | - | 10 | M25 | M25 | 24.4 | E | IRP (UCP-B) for Oil Heater C-2101B | -
97 | D01 | L-MCC2101B-BR | 0.4 | MCC-2101B | Barring Device Motor | 2.2 | 3×6 | 3C | 6 | - | - | 280 | M25 | M25 EX | 23.5 | A | Barring Device Motor for Gas Compressor C-2101B | 01/04/05/07/09/11/13/14
98 | D01 | C-MCC2101B-BR1 | 0.23 | MCC-2101B | IRP (UCP-B) | - | 12×2.5 | 12C | 2.5 | - | - | 10 | M25 | M25 | 24.4 | E | IRP (UCP-B) for Barring Device Motor C-2101B | -
99 | D01 | C-MCC2101B-BR2 | 0.23 | MCC-2101B | Barring Device Motor | - | 3×4 | 3C | 4 | - | - | 280 | M25 | M25 EX | 22.6 | D | Ammeter for Barring Device Motor for Gas Compressor C-2101B | 01/04/05/07/09/11/13/14
100 | D01 | L-MCC2101B-AP | 0.4 | MCC-2101B | Oil Pump | 7.5 | 3×16 | 3C | 16 | - | - | 280 | M32 | M32 EX | 28.2 | A | Oil Pump for Gas Compressor C-2101B (P-2101-AP B) | 01/04/05/07/09/11/13/14
101 | D01 | C-MCC2101B-AP1 | 0.23 | MCC-2101B | IRP (UCP-B) | - | 12×2.5 | 12C | 2.5 | - | - | 10 | M25 | M25 | 24.4 | E | IRP (UCP-B) for Oil Pump C-2101B | -
102 | D01 | C-MCC2101B-AP2 | 0.23 | MCC-2101B | Oil Pump | - | 3×4 | 3C | 4 | - | - | 280 | M25 | M25 EX | 22.6 | D | Ammeter for Oil Pump for Gas Compressor C-2101B | 01/04/05/07/09/11/13/14
103 | D01 | L-MCC2101B-OC | 0.4 | MCC-2101B | Oil Cooler | 5.5 | 3×10 | 3C | 10 | - | - | 280 | M32 | M32 EX | 26.7 | A | Lube Oil Cooler for Gas Compressor C-2101B (AE-2101-OC B) | 01/04/05/07/09/11/13/14
104 | D01 | C-MCC2101B-OC1 | 0.23 | MCC-2101B | IRP (UCP-B) | - | 12×2.5 | 12C | 2.5 | - | - | 10 | M25 | M25 | 24.4 | E | IRP (UCP-B) for Lube Oil Cooler C-2101B | -
105 | D01 | C-MCC2101B-OC2 | 0.23 | MCC-2101B | Oil Cooler | - | 3×4 | 3C | 4 | - | - | 280 | M25 | M25 EX | 22.6 | D | Ammeter for Lube Oil Cooler for Gas Compressor C-2101B | 01/04/05/07/09/11/13/14
106 | D01 | L-MCC2101B-LP | 0.4 | MCC-2101B | Lubricator Pump | 0.55 | 3×4 | 3C | 4 | - | - | 280 | M25 | M25 EX | 22.6 | A | Cylinder Lubricator Pump for Gas Compressor C-2101B (M-2101-LP B) | 01/04/05/07/09/11/13/14
107 | D01 | C-MCC2101B-LP1 | 0.23 | MCC-2101B | IRP (UCP-B) | - | 12×2.5 | 12C | 2.5 | - | - | 10 | M25 | M25 | 24.4 | E | IRP (UCP-B) for Cylinder Lubricator Pump C-2101B | -
108 | D01 | C-MCC2101B-LP2 | 0.23 | MCC-2101B | Lubricator Pump | - | 3×4 | 3C | 4 | - | - | 280 | M25 | M25 EX | 22.6 | D | Ammeter for Cylinder Lubricator Pump for Gas Compressor C-2101B | 01/04/05/07/09/11/13/14
109 | D01 | L-MCC2101B-LH | 0.23 | MCC-2101B | Lubricator Heater | 0.4 | 2×4 | 2C | 4 | 4 | - | 280 | M25 | M25 EX | 21 | A | Cylinder Lubricator Oil Heater for Gas Compressor C-2101B | 01/04/05/07/09/11/13/14
110 | D01 | C-MCC2101B-LH | 0.23 | MCC-2101B | IRP (UCP-B) | - | 12×2.5 | 12C | 2.5 | - | - | 10 | M25 | M25 | 24.4 | E | IRP (UCP-B) for Cylinder Lubricator Oil Heater C-2101B | -
111 | D01 | L-MCC2101B-AX | 0.4 | MCC-2101B | Aux Pump Motor | 7.5 | 3×16 | 3C | 16 | - | - | 280 | M32 | M32 EX | 28.2 | A | Aux Pump for Gas Compressor C-2101B (P-2101-AX B) | 01/04/05/07/09/11/13/14
112 | D01 | C-MCC2101B-AX1 | 0.23 | MCC-2101B | IRP (UCP-B) | - | 12×2.5 | 12C | 2.5 | - | - | 10 | M25 | M25 | 24.4 | E | IRP (UCP-B) for Aux Pump Motor C-2101B | -
113 | D01 | C-MCC2101B-AX2 | 0.23 | MCC-2101B | Aux Pump Motor | - | 3×4 | 3C | 4 | - | - | 280 | M25 | M25 EX | 22.6 | D | Ammeter for Aux Pump for Gas Compressor C-2101B | 01/04/05/07/09/11/13/14
114 | D01 | L-MCC2101B-WP | 0.4 | MCC-2101B | Main Pump Motor | 7.5 | 3×16 | 3C | 16 | - | - | 280 | M32 | M32 EX | 28.2 | A | Main Pump for Gas Compressor C-2101B (P-2101-WP B) | 01/04/05/07/09/11/13/14
115 | D01 | C-MCC2101B-WP1 | 0.23 | MCC-2101B | IRP (UCP-B) | - | 12×2.5 | 12C | 2.5 | - | - | 10 | M25 | M25 | 24.4 | E | IRP (UCP-B) for Main Pump Motor C-2101B | -
116 | D01 | C-MCC2101B-WP2 | 0.23 | MCC-2101B | Main Pump Motor | - | 3×4 | 3C | 4 | - | - | 280 | M25 | M25 EX | 22.6 | D | Ammeter for Main Pump for Gas Compressor C-2101B | 01/04/05/07/09/11/13/14
117 | D01 | L-MCC2101B-WH | 0.4 | MCC-2101B | Electric Heater | 12 | 3×70+35 | 4C | 70 | 35 | - | 280 | M50 | M50 EX | 47.9 | A | Electric Heater for Gas Compressor C-2101B (P-2101-WH B) | 01/04/05/07/09/11/13/14
118 | D01 | C-MCC2101B-WH | 0.23 | MCC-2101B | IRP (UCP-B) | - | 12×2.5 | 12C | 2.5 | - | - | 10 | M25 | M25 | 24.4 | E | IRP (UCP-B) for Electric Heater C-2101B | -
119 | D01 | L-MCC2101B-WC | 0.4 | MCC-2101B | Water Console | 4 | 3×10 | 3C | 10 | - | - | 280 | M32 | M32 EX | 26.7 | A | Water Console Cooler Motor for Gas Compressor C-2101B (AE-2101-WC B) | 01/04/05/07/09/11/13/14
120 | D01 | C-MCC2101B-WC1 | 0.23 | MCC-2101B | IRP (UCP-B) | - | 12×2.5 | 12C | 2.5 | - | - | 10 | M25 | M25 | 24.4 | E | IRP (UCP-B) forWater Console Cooler Motor C-2101B | -
121 | D01 | C-MCC2101B-WC2 | 0.23 | MCC-2101B | Water Console | - | 3×4 | 3C | 4 | - | - | 280 | M25 | M25 EX | 22.6 | D | Ammeter for Water Console Cooler Motor for Gas Compressor C-2101B | 01/04/05/07/09/11/13/14
122 | D01 | M-11SWGC-C2101-C | 11 | GCS-11-SWG-001C | C-2101C | 1250 | 3×95 | 3C | 95 | - | - | 330 | M90 | M90 EX | 87.7 | F | First & Second Stage Gas Compressor C-2101C | 01/04/05/07/09/11/13/15/16
123 | D01 | L-11SWGC-SPH-C | 0.23 | GCS-11-SWG-001C | Space Heater | 0.3 | 2×4 | 2C | 4 | 4 | - | 330 | M25 | M25 EX | 21 | A | Space Heater for Gas Compressor C-2101C | 01/04/05/07/09/11/13/15/16
124 | D01 | C-11SWGC-IRP-C | 0.11DC | GCS-11-SWG-001C | IRP (UCP-C) | - | 12×2.5 | 12C | 2.5 | - | - | 40 | M25 | M25 | 24.4 | E | IRP (UCP-C) for Gas Compressor C-2101C | -
125 | D01 | C-11SWGC-IRP-C (ESD) | 0.11DC | GCS-11-SWG-001C | IRP (ESD) | - | 3×2.5 | 3C | 2.5 | - | - | 40 | M25 | M25 | 20.5 | E | IRP (ESD) for Gas Compressor C-2101C | -
126 | D01 | C-11SWGC-C2101-C | 0.11DC | GCS-11-SWG-001C | C-2101C | - | 3×4 | 3C | 4 | - | - | 330 | M25 | M25 EX | 22.6 | D | Ammeter for Gas Compressor C-2101C | 01/04/05/07/09/11/13/15/16
127 | D01 | C-11SWGC-RTD2101-C | - | UCP-C | C-2101C | - | 12×3×1.5 | 36C | 1.5 | - | - | 360 | M50 | M50 | 41 | R | RTD for Gas Compressor C-2101C (From Control Room) | 01/04/05/07/09/11/13/15/16
128 | D01 | C-11SWGC-2101-C | - | GCS-11-SWG-001C | C-2101C | - | 3×6 | 3C | 6 | - | - | 330 | M25 | M25 EX | 23.5 | D | Differential Protection of C-2101C | 01/04/05/07/09/11/13/15/16
129 | D01 | M-11SWGC-CAP-C | 11 | GCS-11-SWG-001C | Cap Bank C | 360 kvar | 3×95 | 3C | 95 | - | - | 30 | M90 | M90 | 79.1 | I | Capacitor Bank for Gas Compressor C-2101C | -
130 | D01 | C-11SWGC-CAP-C | 0.11DC | GCS-11-SWG-001C | Cap Bank C | - | 7×2.5 | 7C | 2.5 | - | - | 30 | M25 | M25 | 20 | E | Control for Capacitor Bank of C-2101C | -
131 | D01 | L-NSWGC-mcc2101C | 0.4 | GCS-400-NSWG-001C | MCC-2101C | 50 | 3×35+16 | 4C | 35 | 16 | - | 25 | M32 | M32 | 32.1 | B | Normal Panel for Gas Compressor C-2101C (Auxiliary) | -
132 | D01 | L-MCC2101C-OH | 0.23 | MCC-2101C | Oil Heater | 1.5 | 2×16 | 2C | 16 | 16 | - | 310 | M32 | M32 EX | 27.2 | A | Oil Heater for Gas Compressor C-2101C | 01/04/05/07/09/11/13/15/16
133 | D01 | C-MCC2101C-OH | 0.23 | MCC-2101C | IRP (UCP-C) | - | 12×2.5 | 12C | 2.5 | - | - | 10 | M25 | M25 | 24.4 | E | IRP (UCP-C) for Oil Heater C-2101C | -
134 | D01 | L-MCC2101C-BR | 0.4 | MCC-2101C | Barring Device Motor | 2.2 | 3×6 | 3C | 6 | - | - | 310 | M25 | M25 EX | 23.5 | A | Barring Device Motor for Gas Compressor C-2101C | 01/04/05/07/09/11/13/15/16
135 | D01 | C-MCC2101C-BR1 | 0.23 | MCC-2101C | IRP (UCP-C) | - | 12×2.5 | 12C | 2.5 | - | - | 10 | M25 | M25 | 24.4 | E | IRP (UCP-C) for Barring Device Motor C-2101C | -
136 | D01 | C-MCC2101C-BR2 | 0.23 | MCC-2101C | Barring Device Motor | - | 3×4 | 3C | 4 | - | - | 310 | M25 | M25 EX | 22.6 | D | Ammeter for Barring Device Motor for Gas Compressor C-2101C | 01/04/05/07/09/11/13/15/16
137 | D01 | L-MCC2101C-AP | 0.4 | MCC-2101C | Oil Pump | 7.5 | 3×16 | 3C | 16 | - | - | 310 | M32 | M32 EX | 28.2 | A | Oil Pump for Gas Compressor C-2101C (P-2101-AP C) | 01/04/05/07/09/11/13/15/16
138 | D01 | C-MCC2101C-AP1 | 0.23 | MCC-2101C | IRP (UCP-C) | - | 12×2.5 | 12C | 2.5 | - | - | 10 | M25 | M25 | 24.4 | E | IRP (UCP-C) for Oil Pump C-2101C | -
139 | D01 | C-MCC2101C-AP2 | 0.23 | MCC-2101C | Oil Pump | - | 3×4 | 3C | 4 | - | - | 310 | M25 | M25 EX | 22.6 | D | Ammeter for Oil Pump for Gas Compressor C-2101C | 01/04/05/07/09/11/13/15/16
140 | D01 | L-MCC2101C-OC | 0.4 | MCC-2101C | Oil Cooler | 5.5 | 3×10 | 3C | 10 | - | - | 310 | M32 | M32 EX | 26.7 | A | Lube Oil Cooler for Gas Compressor C-2101C (AE-2101-OC C) | 01/04/05/07/09/11/13/15/16
141 | D01 | C-MCC2101C-OC1 | 0.23 | MCC-2101C | IRP (UCP-C) | - | 12×2.5 | 12C | 2.5 | - | - | 10 | M25 | M25 | 24.4 | E | IRP (UCP-B) for Lube Oil Cooler C-2101C | -
142 | D01 | C-MCC2101C-OC2 | 0.23 | MCC-2101C | Oil Cooler | - | 3×4 | 3C | 4 | - | - | 310 | M25 | M25 EX | 22.6 | D | Ammeter for Lube Oil Cooler for Gas Compressor C-2101C | 01/04/05/07/09/11/13/15/16
143 | D01 | L-MCC2101C-LP | 0.4 | MCC-2101C | Lubricator Pump | 0.55 | 3×4 | 3C | 4 | - | - | 310 | M25 | M25 EX | 22.6 | A | Cylinder Lubricator Pump for Gas Compressor C-2101C (M-2101-LP C) | 01/04/05/07/09/11/13/15/16
144 | D01 | C-MCC2101C-LP1 | 0.23 | MCC-2101C | IRP (UCP-C) | - | 12×2.5 | 12C | 2.5 | - | - | 10 | M25 | M25 | 24.4 | E | IRP (UCP-C) for Cylinder Lubricator Pump C-2101C | -
145 | D01 | C-MCC2101C-LP2 | 0.23 | MCC-2101C | Lubricator Pump | - | 3×4 | 3C | 4 | - | - | 310 | M25 | M25 EX | 22.6 | D | Ammeter for Cylinder Lubricator for Gas Compressor C-2101C | 01/04/05/07/09/11/13/15/16
146 | D01 | L-MCC2101C-LH | 0.23 | MCC-2101C | Lubricator Heater | 0.4 | 2×4 | 2C | 4 | 4 | - | 310 | M25 | M25 EX | 21 | A | Cylinder Lubricator Oil Heater for Gas Compressor C-2101C | 01/04/05/07/09/11/13/15/16
147 | D01 | C-MCC2101C-LH | 0.23 | MCC-2101C | IRP (UCP-C) | - | 12×2.5 | 12C | 2.5 | - | - | 10 | M25 | M25 | 24.4 | E | IRP (UCP-C) for Cylinder Lubricator Oil Heater C-2101C | -
148 | D01 | L-MCC2101C-AX | 0.4 | MCC-2101C | Aux Pump Motor | 7.5 | 3×16 | 3C | 16 | - | - | 310 | M32 | M32 EX | 28.2 | A | Aux Pump Motor for Gas Compressor C-2101B (P-2101-AX C) | 01/04/05/07/09/11/13/15/16
149 | D01 | C-MCC2101C-AX1 | 0.23 | MCC-2101C | IRP (UCP-C) | - | 12×2.5 | 12C | 2.5 | - | - | 10 | M25 | M25 | 24.4 | E | IRP (UCP-B) for Aux Pump Motor C-2101C | -
150 | D01 | C-MCC2101C-AX2 | 0.23 | MCC-2101C | Aux Pump Motor | - | 3×4 | 3C | 4 | - | - | 310 | M25 | M25 EX | 22.6 | D | Ammeter for Aux Pump Motor for Gas Compressor C-2101C | 01/04/05/07/09/11/13/15/16
151 | D01 | L-MCC2101C-WP | 0.4 | MCC-2101C | Main Pump Motor | 7.5 | 3×16 | 3C | 16 | - | - | 310 | M32 | M32 EX | 28.2 | A | Main Pump Motor for Gas Compressor C-2101C (P-2101-WP C) | 01/04/05/07/09/11/13/15/16
152 | D01 | C-MCC2101C-WP1 | 0.23 | MCC-2101C | IRP (UCP-C) | - | 12×2.5 | 12C | 2.5 | - | - | 10 | M25 | M25 | 24.4 | E | IRP (UCP-C) for Main Pump Motor C-2101C | -
153 | D01 | C-MCC2101C-WP2 | 0.23 | MCC-2101C | Main Pump Motor | - | 3×4 | 3C | 4 | - | - | 310 | M25 | M25 EX | 22.6 | D | Ammeter for Main Pump Motor for Gas Compressor C-2101C | 01/04/05/07/09/11/13/15/16
154 | D01 | L-MCC2101C-WH | 0.4 | MCC-2101C | Electric Heater | 12 | 3×70+35 | 4C | 70 | 35 | - | 310 | M50 | M50 EX | 47.9 | A | Electric Heater for Gas Compressor C-2101B (P-2101-WH C) | 01/04/05/07/09/11/13/15/16
155 | D01 | C-MCC2101C-WH | 0.23 | MCC-2101C | IRP (UCP-C) | - | 12×2.5 | 12C | 2.5 | - | - | 10 | M25 | M25 | 24.4 | E | IRP (UCP-C) for Electric Heater C-2101C | -
156 | D01 | L-MCC2101C-WC | 0.4 | MCC-2101C | Water Console | 4 | 3×10 | 3C | 10 | - | - | 310 | M32 | M32 EX | 26.7 | A | Water Console Cooler Motor for Gas Compressor C-2101C (AE-2101-WC C) | 01/04/05/07/09/11/13/15/16
157 | D01 | C-MCC2101C-WC1 | 0.23 | MCC-2101C | IRP (UCP-C) | - | 12×2.5 | 12C | 2.5 | - | - | 10 | M25 | M25 | 24.4 | E | IRP (UCP-C) for Water Console Cooler Motor C-2101C | -
158 | D01 | C-MCC2101C-WC2 | 0.23 | MCC-2101C | Water Console | - | 3×4 | 3C | 4 | - | - | 310 | M25 | M25 EX | 22.6 | D | Ammeter for Water Console Cooler Motor for Gas Compressor C-2101C | 01/04/05/07/09/11/13/15/16
159 | D01 | L-NSWGA-AC2121A | 0.4 | GCS-400-NSWG-001A | AC-2101A1 | 5.5 | 3×10 | 3C | 10 | - | - | 310 | M32 | M32 EX | 26.7 | A | First Stage Air Cooler 01A1 | 01/04/22/24/25/27/28
160 | D01 | C-NSWGA-AC2121A-02 | 0.23 | GCS-400-NSWG-001A | IRP-DCS & ESD | - | 16×2.5 | 15C | 2.5 | - | - | 25 | M32 | M32 | 27.1 | E | IRP-DCS & ESD for Air Cooler 01A1 | -
161 | D01 | C-NSWGA-AC2121A-03 | 0.23 | GCS-400-NSWG-001A | LCS | - | 10×2.5 | 10C | 2.5 | - | - | 310 | M32 | M32 EX | 29 | D | LCS for Air Cooler 01A1 | 01/04/22/24/25/27/28
162 | D01 | L-NSWGA-AC2122A | 0.4 | GCS-400-NSWG-001A | AC-2101A2 | 5.5 | 3×10 | 3C | 10 | - | - | 310 | M32 | M32 EX | 26.7 | A | First Stage Air Cooler 01A2 | 01/04/22/24/25/27/28
163 | D01 | C-NSWGA-AC2122A-02 | 0.23 | GCS-400-NSWG-001A | IRP-DCS & ESD | - | 16×2.5 | 15C | 2.5 | - | - | 25 | M32 | M32 | 27.1 | E | IRP-DCS & ESD for Air Cooler 01A2 | -
164 | D01 | C-NSWGA-AC2122A-03 | 0.23 | GCS-400-NSWG-001A | LCS | - | 10×2.5 | 10C | 2.5 | - | - | 310 | M32 | M32 EX | 29 | D | LCS for Air Cooler 01A2 | 01/04/22/24/25/27/28
165 | D01 | L-NSWGB-AC2121B | 0.4 | GCS-400-NSWG-001B | AC-2101B1 | 5.5 | 3×10 | 3C | 10 | - | - | 340 | M32 | M32 EX | 26.7 | A | First Stage Air Cooler 01B1 | 01/04/22/24/25/27/29/30
166 | D01 | C-NSWGB-AC2121B-02 | 0.23 | GCS-400-NSWG-001B | IRP-DCS & ESD | - | 16×2.5 | 15C | 2.5 | - | - | 25 | M32 | M32 | 27.1 | E | IRP-DCS & ESD for Air Cooler 01B1 | -
167 | D01 | C-NSWGB-AC2121B-03 | 0.23 | GCS-400-NSWG-001B | LCS | - | 10×2.5 | 10C | 2.5 | - | - | 340 | M32 | M32 EX | 29 | D | LCS for Air Cooler 01B1 | 01/04/22/24/25/27/29/30
168 | D01 | L-NSWGB-AC2122B | 0.4 | GCS-400-NSWG-001B | AC-2101B2 | 5.5 | 3×10 | 3C | 10 | - | - | 340 | M32 | M32 EX | 26.7 | A | First Stage Air Cooler 01B2 | 01/04/22/24/25/27/29/30
169 | D01 | C-NSWGB-AC2122B-02 | 0.23 | GCS-400-NSWG-001B | IRP-DCS & ESD | - | 16×2.5 | 15C | 2.5 | - | - | 25 | M32 | M32 | 27.1 | E | IRP-DCS & ESD for Air Cooler 01B2 | -
170 | D01 | C-NSWGB-AC2122B-03 | 0.23 | GCS-400-NSWG-001B | LCS | - | 10×2.5 | 10C | 2.5 | - | - | 340 | M32 | M32 EX | 29 | D | LCS for Air Cooler 01B2 | 01/04/22/24/25/27/29/30
171 | D01 | L-NSWGA-AC2121C | 0.4 | GCS-400-NSWG-001A | AC-2101C1 | 5.5 | 3×10 | 3C | 10 | - | - | 370 | M32 | M32 EX | 26.7 | A | First Stage Air Cooler 01C1 | 01/04/22/24/25/27/29/31/32
172 | D01 | C-NSWGA-AC2121C-02 | 0.23 | GCS-400-NSWG-001A | IRP-DCS & ESD | - | 16×2.5 | 15C | 2.5 | - | - | 25 | M32 | M32 | 27.1 | E | IRP-DCS & ESD for Air Cooler 01C1 | -
173 | D01 | C-NSWGA-AC2121C-03 | 0.23 | GCS-400-NSWG-001A | LCS | - | 10×2.5 | 10C | 2.5 | - | - | 370 | M32 | M32 EX | 29 | D | LCS for Air Cooler 01C1 | 01/04/22/24/25/27/29/31/32
174 | D01 | L-NSWGA-AC2122C | 0.4 | GCS-400-NSWG-001A | AC-2101C2 | 5.5 | 3×10 | 3C | 10 | - | - | 370 | M32 | M32 EX | 26.7 | A | First Stage Air Cooler 01C2 | 01/04/22/24/25/27/29/31/32
175 | D01 | C-NSWGA-AC2122C-02 | 0.23 | GCS-400-NSWG-001A | IRP-DCS & ESD | - | 16×2.5 | 15C | 2.5 | - | - | 25 | M32 | M32 | 27.1 | E | IRP-DCS & ESD for Air Cooler 01C2 | -
176 | D01 | C-NSWGA-AC2122C-03 | 0.23 | GCS-400-NSWG-001A | LCS | - | 10×2.5 | 10C | 2.5 | - | - | 370 | M32 | M32 EX | 29 | D | LCS for Air Cooler 01C2 | 01/04/22/24/25/27/29/31/32
177 | D01 | L-NSWGA-AC2131A | 0.4 | GCS-400-NSWG-001A | AC-2102A1 | 5.5 | 3×10 | 3C | 10 | - | - | 310 | M32 | M32 EX | 26.7 | A | Second Stage Air Cooler 02A1 | 01/04/22/24/25/27/28
178 | D01 | C-NSWGA-AC2131A-02 | 0.23 | GCS-400-NSWG-001A | IRP-DCS & ESD | - | 16×2.5 | 15C | 2.5 | - | - | 25 | M32 | M32 | 27.1 | E | IRP-DCS & ESD for Air Cooler 02A1 | -
179 | D01 | C-NSWGA-AC2131A-03 | 0.23 | GCS-400-NSWG-001A | LCS | - | 10×2.5 | 10C | 2.5 | - | - | 310 | M32 | M32 EX | 29 | D | LCS for Air Cooler 02A1 | 01/04/22/24/25/27/28
180 | D01 | L-NSWGA-AC2132A | 0.4 | GCS-400-NSWG-001A | AC-2102A2 | 5.5 | 3×10 | 3C | 10 | - | - | 310 | M32 | M32 EX | 26.7 | A | Second Stage Air Cooler 02A2 | 01/04/22/24/25/27/28
181 | D01 | C-NSWGA-AC2132A-02 | 0.23 | GCS-400-NSWG-001A | IRP-DCS & ESD | - | 16×2.5 | 15C | 2.5 | - | - | 25 | M32 | M32 | 27.1 | E | IRP-DCS & ESD for Air Cooler 02A2 | -
182 | D01 | C-NSWGA-AC2132A-03 | 0.23 | GCS-400-NSWG-001A | LCS | - | 10×2.5 | 10C | 2.5 | - | - | 310 | M32 | M32 EX | 29 | D | LCS for Air Cooler 02A2 | 01/04/22/24/25/27/28
183 | D01 | L-NSWGB-AC2131B | 0.4 | GCS-400-NSWG-001B | AC-2102B1 | 5.5 | 3×10 | 3C | 10 | - | - | 340 | M32 | M32 EX | 26.7 | A | Second Stage Air Cooler 02B1 | 01/04/22/24/25/27/29/30
184 | D01 | C-NSWGB-AC2131B-02 | 0.23 | GCS-400-NSWG-001B | IRP-DCS & ESD | - | 16×2.5 | 15C | 2.5 | - | - | 25 | M32 | M32 | 27.1 | E | IRP-DCS & ESD for Air Cooler 02B1 | -
185 | D01 | C-NSWGB-AC2131B-03 | 0.23 | GCS-400-NSWG-001B | LCS | - | 10×2.5 | 10C | 2.5 | - | - | 340 | M32 | M32 EX | 29 | D | LCS for Air Cooler 02B1 | 01/04/22/24/25/27/29/30
186 | D01 | L-NSWGB-AC2132B | 0.4 | GCS-400-NSWG-001B | AC-2102B2 | 5.5 | 3×10 | 3C | 10 | - | - | 340 | M32 | M32 EX | 26.7 | A | Second Stage Air Cooler 02B2 | 01/04/22/24/25/27/29/30
187 | D01 | C-NSWGB-AC2132B-02 | 0.23 | GCS-400-NSWG-001B | IRP-DCS & ESD | - | 16×2.5 | 15C | 2.5 | - | - | 25 | M20 A | M20 A | 17.7 | E | IRP--DCS & ESD for Air Cooler 02B2 | -
188 | D01 | C-NSWGB-AC2132B-03 | 0.23 | GCS-400-NSWG-001B | LCS | - | 10×2.5 | 10C | 2.5 | - | - | 340 | M32 | M32 EX | 29 | D | LCS for Air Cooler 02B2 | 01/04/22/24/25/27/29/30
189 | D01 | L-NSWGA-AC2131C | 0.4 | GCS-400-NSWG-001A | AC-2102C1 | 5.5 | 3×10 | 3C | 10 | - | - | 370 | M32 | M32 EX | 26.7 | A | Second Stage Air Cooler 02C1 | 01/04/22/24/25/27/29/31/32
190 | D01 | C-NSWGA-AC2131C-02 | 0.23 | GCS-400-NSWG-001A | IRP-DCS & ESD | - | 16×2.5 | 15C | 2.5 | - | - | 25 | M32 | M32 | 27.1 | E | IRP--DCS & ESD for Air Cooler 02C1 | -
191 | D01 | C-NSWGA-AC2131C-03 | 0.23 | GCS-400-NSWG-001A | LCS | - | 10×2.5 | 10C | 2.5 | - | - | 370 | M32 | M32 EX | 29 | D | LCS for Air Cooler 02C1 | 01/04/22/24/25/27/29/31/32
192 | D01 | L-NSWGA-AC2132C | 0.4 | GCS-400-NSWG-001A | AC-2102C2 | 5.5 | 3×10 | 3C | 10 | - | - | 370 | M32 | M32 EX | 26.7 | A | Second Stage Air Cooler 02C2 | 01/04/22/24/25/27/29/31/32
193 | D01 | C-NSWGA-AC2132C-02 | 0.23 | GCS-400-NSWG-001A | IRP-DCS & ESD | - | 16×2.5 | 12C | 2.5 | - | - | 25 | M25 | M25 | 24.4 | E | IRP-DCS & ESD for Air Cooler 02C2 | -
194 | D01 | C-NSWGA-AC2132C-03 | 0.23 | GCS-400-NSWG-001A | LCS | - | 10×2.5 | 10C | 2.5 | - | - | 370 | M32 | M32 EX | 29 | D | LCS for Air Cooler 02C2 | 01/04/22/24/25/27/29/31/32
195 | D01 | L-NSWGE-PKC2203A1 | 0.4 | GCS-400-NSWG-001E | PK-C-2203A | 80 | 3×120+70 | 4C | 120 | 70 | - | 270 | M63 | M63 EX | 59.3 | A | Instrument & Plant Air Package A | 36/40/44/45/46/47
196 | D01 | L-NSWGE-PKC2203A2 | 0.4 | GCS-400-NSWG-001E | PK-C-2203A | 80 | 3×120+70 | 4C | 120 | 70 | - | 270 | M63 | M63 EX | 59.3 | A | Instrument & Plant Air Package A | 36/40/44/45/46/47
197 | D01 | L-NSWGE-PKC2203B1 | 0.4 | GCS-400-NSWG-001E | PK-C-2203B | 80 | 3×120+70 | 4C | 120 | 70 | - | 270 | M63 | M63 EX | 59.3 | A | Instrument & Plant Air Package B | 36/40/44/45/46/47
198 | D01 | L-NSWGE-PKC2203B2 | 0.4 | GCS-400-NSWG-001E | PK-C-2203B | 80 | 3×120+70 | 4C | 120 | 70 | - | 270 | M63 | M63 EX | 59.3 | A | Instrument & Plant Air Package B | 36/40/44/45/46/47
199 | D01 | L-NSWGA-PK2204-1 | 0.4 | GCS-400-NSWG-001A | PK-2204 | 75 | 3×120+70 | 4C | 120 | 70 | - | 280 | M50 | M50 | 51.9 | B | Nitrogen Package | 36/40/44/45/46/48/49/50
200 | D01 | L-NSWGA-PK2204-2 | 0.4 | GCS-400-NSWG-001A | PK-2204 | 75 | 3×120+70 | 4C | 120 | 70 | - | 280 | M50 | M50 | 51.9 | B | Nitrogen Package | 36/40/44/45/46/48/49/50
201 | D01 | L-NSWGB-PK2201 | 0.4 | GCS-400-NSWG-001B | PK-2201 | 30 | 3×120+70 | 4C | 120 | 70 | - | 420 | M63 | M63 | 59.3 | Z | LP Flare Package | 36/40/44/45/46/48/52
202 | D01 | L-NSWGA-PK2207 | 0.4 | GCS-400-NSWG-001A | PK-2207 | 3 | 4×10 | 4C | 10 | 10 | - | 250 | M32 | M32 EX | 28.1 | A | Corrosion Inhibitor Package (Chemical Package) | 01/04/05/07/08
203 | D01 | L-NSWGB-PK2101 | 0.4 | GCS-400-NSWG-001B | PK-2101 | 60 | 3×95+50 | 4C | 95 | 50 | - | 25 | M63 | M63 EX | 53.8 | A | Dehydration Package | -
204 | D01 | L-PK2101-P100A | 0.4 | PK-2101 | P-100/A | 2.2 | 3×6 | 3C | 6 | - | - | 330 | M25 | M25 EX | 23.5 | A | Lean Teg Circulation Pump A | 01/04/05/07/09/11/13/15/17/18
205 | D01 | C-PK2101-P100A2 | 0.23 | PK-2101 | IRP-DCS & ESD | - | 16×2.5 | 15C | 2.5 | - | - | 25 | M32 | M32 | 27.1 | E | IRP--DCS & ESD for Lean Teg Circulation Pump A | -
206 | D01 | C-PK2101-P100A3 | 0.23 | PK-2101 | LCS | - | 10×2.5 | 10C | 2.5 | - | - | 330 | M32 | M32 EX | 29 | D | LCS for Lean Teg Circulation Pump A | 01/04/05/07/09/11/13/15/17/18
207 | D01 | L-PK2101-P100B | 0.4 | PK-2101 | P-100/B | 2.2 | 3×6 | 3C | 6 | - | - | 330 | M25 | M25 EX | 23.5 | A | Lean Teg Circulation Pump B | 01/04/05/07/09/11/13/15/17/18
208 | D01 | C-PK2101-P100B2 | 0.23 | PK-2101 | IRP-DCS & ESD | - | 16×2.5 | 15C | 2.5 | - | - | 25 | M32 | M32 | 27.1 | E | IRP--DCS & ESD for Lean Teg Circulation Pump B | -
209 | D01 | C-PK2101-P100B3 | 0.23 | PK-2101 | LCS | - | 10×2.5 | 10C | 2.5 | - | - | 330 | M32 | M32 EX | 29 | D | LCS for Lean Teg Circulation Pump B | 01/04/05/07/09/11/13/15/17/18
210 | D01 | L-NSWGA-P2203A | 0.4 | GCS-400-NSWG-001A | P-2203A | 2.2 | 3×10 | 3C | 10 | - | - | 400 | M32 | M32 EX | 26.7 | A | Sump Pump A | 01/04/22/24/25/27/29/31/33/34
211 | D01 | C-NSWGA-P2203A-02 | 0.23 | GCS-400-NSWG-001A | IRP-DCS & ESD | - | 16×2.5 | 15C | 2.5 | - | - | 25 | M32 | M32 | 27.1 | E | IRP--DCS & ESD for Sump Pump A | -
212 | D01 | C-NSWGA-P2203A-03 | 0.23 | GCS-400-NSWG-001A | LCS | - | 7×2.5 | 7C | 2.5 | - | - | 400 | M25 | M25 EX | 25.3 | D | LCS for Sump Pump A | 01/04/22/24/25/27/29/31/33/34
213 | D01 | L-NSWGB-P2203B | 0.4 | GCS-400-NSWG-001B | P-2203B | 2.2 | 3×10 | 3C | 10 | - | - | 400 | M32 | M32 EX | 26.7 | A | Sump Pump B | 01/04/22/24/25/27/29/31/33/34
214 | D01 | C-NSWGB-P2203B-02 | 0.23 | GCS-400-NSWG-001B | IRP-DCS & ESD | - | 16×2.5 | 15C | 2.5 | - | - | 25 | M32 | M32 | 27.1 | E | IRP--DCS & ESD for Sump Pump B | -
215 | D01 | C-NSWGB-P2203B-03 | 0.23 | GCS-400-NSWG-001B | LCS | - | 7×2.5 | 7C | 2.5 | - | - | 400 | M25 | M25 EX | 25.3 | D | LCS for Sump Pump B | 01/04/22/24/25/27/29/31/33/34
216 | D01 | L-NSWGA-P-2202A | 0.4 | GCS-400-NSWG-001A | P-2202A | 7.5 | 3×25 | 3C | 25 | - | - | 410 | M32 | M32 EX | 32.4 | A | Closed Drain Pump A | 01/04/22/24/25/27/29/31/33/34
217 | D01 | C-NSWGA-P-2202A-02 | 0.23 | GCS-400-NSWG-001A | IRP-DCS & ESD | - | 16×2.5 | 15C | 2.5 | - | - | 25 | M32 | M32 | 27.1 | E | IRP--DCS & ESD for Closed Drain Pump A | -
218 | D01 | C-NSWGA-P-2202A-03 | 0.23 | GCS-400-NSWG-001A | LCS | - | 10×2.5 | 10C | 2.5 | - | - | 410 | M32 | M32 EX | 29 | D | LCS for Closed Drain Pump A | 01/04/22/24/25/27/29/31/33/34
219 | D01 | L-NSWGB-P-2202B | 0.4 | GCS-400-NSWG-001B | P-2202B | 7.5 | 3×25 | 3C | 25 | - | - | 410 | M32 | M32 EX | 32.4 | A | Closed Drain Pump B | 01/04/22/24/25/27/29/31/33/34
220 | D01 | C-NSWGB-P-2202B-02 | 0.23 | GCS-400-NSWG-001B | IRP-DCS & ESD | - | 16×2.5 | 15C | 2.5 | - | - | 25 | M32 | M32 | 27.1 | E | IRP--DCS & ESD for Closed Drain Pump B | -
221 | D01 | C-NSWGB-P-2202B-03 | 0.23 | GCS-400-NSWG-001B | LCS | - | 10×2.5 | 10C | 2.5 | - | - | 410 | M32 | M32 EX | 29 | D | LCS for Closed Drain Pump B | 01/04/22/24/25/27/29/31/33/34
222 | D01 | L-NSWGA-P-2101A | 0.4 | GCS-400-NSWG-001A | P-2101A | 11 | 3×16 | 3C | 16 | - | - | 210 | M32 | M32 EX | 28.2 | A | Slug Pump A | 01/04/05/06
223 | D01 | C-NSWGA-P-2101A-02 | 0.23 | GCS-400-NSWG-001A | IRP-DCS & ESD | - | 16×2.5 | 15C | 2.5 | - | - | 25 | M32 | M32 | 27.1 | E | IRP--DCS & ESD for Slug Pump A | -
224 | D01 | C-NSWGA-P-2101A-03 | 0.23 | GCS-400-NSWG-001A | LCS | - | 10×2.5 | 10C | 2.5 | - | - | 210 | M32 | M32 EX | 29 | D | LCS for Slug Pump A | 01/04/05/06
225 | D01 | L-NSWGB-P-2101B | 0.4 | GCS-400-NSWG-001B | P-2101B | 11 | 3×16 | 3C | 16 | - | - | 210 | M32 | M32 EX | 28.2 | A | Slug Pump B | 01/04/05/06
226 | D01 | C-NSWGB-P-2101B-02 | 0.23 | GCS-400-NSWG-001B | IRP-DCS & ESD | - | 16×2.5 | 12C | 2.5 | - | - | 25 | M25 | M25 | 24.4 | E | IRP--DCS & ESD for Slug Pump B | -
227 | D01 | C-NSWGB-P-2101B-03 | 0.23 | GCS-400-NSWG-001B | LCS | - | 10×2.5 | 10C | 2.5 | - | - | 210 | M32 | M32 EX | 29 | D | LCS for Slug Pump B | 01/04/05/06
228 | D01 | L-NSWGA-P-2302A | 0.4 | GCS-400-NSWG-001A | P-2302A | 22 | 3×35 | 3C | 35 | - | - | 215 | M32 | M32 | 28.6 | B | Fire Water Jockey Pump A | 36/40/41/42/43
229 | D01 | C-NSWGA-P-2302A | 0.23 | GCS-400-NSWG-001A | LCS | - | 3×4 | 3C | 4 | - | - | 215 | M20 A | M20 A | 16.6 | B | Ammeter for Fire Water Jockey Pump A | 36/40/41/42/43
230 | D01 | L-NSWGB-P-2302B | 0.4 | GCS-400-NSWG-001B | P-2302B | 22 | 3×35 | 3C | 35 | - | - | 215 | M32 | M32 | 28.6 | B | Fire Water Jockey Pump B | 36/40/41/42/43
231 | D01 | C-NSWGB-P-2302B | 0.23 | GCS-400-NSWG-001B | LCS | - | 3×4 | 3C | 4 | - | - | 215 | M20 A | M20 A | 16.6 | B | LCS for Fire Water Jockey Pump B | 36/40/41/42/43
232 | D01 | L-NSWGA-P-2209 | 0.4 | GCS-400-NSWG-001A | P-2209 | 2.2 | 3×4 | 3C | 4 | - | - | 90 | M20 A | M20 A | 16.6 | B | Potable Water Pump | 01/03
233 | D01 | C-NSWGA-P-2209-02 | 0.23 | GCS-400-NSWG-001A | IRP-DCS & ESD | - | 12×2.5 | 12C | 2.5 | - | - | 25 | M25 | M25 | 24.4 | E | IRP--DCS & ESD for Potable Water Pump | -
234 | D01 | C-NSWGA-P-2209-03 | 0.23 | GCS-400-NSWG-001A | LCS | - | 7×2.5 | 7C | 2.5 | - | - | 90 | M25 | M25 | 20 | E | LCS for Potable Water Pump | 01/03
235 | D01 | L-NSWGA-P-2206 | 0.4 | GCS-400-NSWG-001A | P-2206 | 1.1 | 3×4 | 3C | 4 | - | - | 215 | M20 A | M20 A | 16.6 | B | Diesel Oil Pump | 36/40/41/54
236 | D01 | L-NSWGE-P-2201A | 0.4 | GCS-400-NSWG-001E | P-2201A | 4 | 3×16 | 3C | 16 | - | - | 420 | M32 | M32 EX | 28.2 | A | LP Flare K.O. Drum Pump A | 01/04/22/24/25/27/29/31/33/34
237 | D01 | C-NSWGE-P-2201A-02 | 0.23 | GCS-400-NSWG-001E | IRP-DCS & ESD | - | 16×2.5 | 15C | 2.5 | - | - | 25 | M32 | M32 | 27.1 | E | IRP--DCS & ESD for LP Flare K.O. Drum Pump A | -
238 | D01 | C-NSWGE-P-2201A-03 | 0.23 | GCS-400-NSWG-001E | LCS | - | 10×2.5 | 7C | 2.5 | - | - | 420 | M32 | M32 EX | 29 | D | LCS for LP Flare K.O. Drum Pump A | 01/04/22/24/25/27/29/31/33/34
239 | D01 | L-NSWGE-P-2201B | 0.4 | GCS-400-NSWG-001E | P-2201B | 4 | 3×16 | 3C | 16 | - | - | 420 | M32 | M32 EX | 28.2 | A | LP Flare K.O. Drum Pump B | 01/04/22/24/25/27/29/31/33/34
240 | D01 | C-NSWGE-P-2201B-02 | 0.23 | GCS-400-NSWG-001E | IRP-DCS & ESD | - | 16×2.5 | 15C | 2.5 | - | - | 25 | M32 | M32 | 27.1 | E | IRP--DCS & ESD for LP Flare K.O. Drum Pump B | -
241 | D01 | C-NSWGE-P-2201B-03 | 0.23 | GCS-400-NSWG-001E | LCS | - | 10×2.5 | 10C | 2.5 | - | - | 420 | M32 | M32 EX | 29 | D | LCS for LP Flare K.O. Drum Pump B | 01/04/22/24/25/27/29/31/33/34
242 | D01 | L-NSWGA-P-2103A | 0.4 | GCS-400-NSWG-001A | P-2103A | 1.5 | 3×4 | 3C | 4 | - | - | 370 | M25 | M25 EX | 22.6 | A | Glycol Transfer Pump A | 01/04/05/07/09/11/13/15/17/19/21
243 | D01 | C-NSWGA-P-2103A-02 | 0.23 | GCS-400-NSWG-001A | IRP-DCS & ESD | - | 16×2.5 | 15C | 2.5 | - | - | 25 | M32 | M32 | 27.1 | E | IRP--DCS & ESD for Glycol Transfer Pump A | -
244 | D01 | C-NSWGA-P-2103A-03 | 0.23 | GCS-400-NSWG-001A | LCS | - | 7×2.5 | 7C | 2.5 | - | - | 370 | M25 | M25 EX | 25.3 | D | LCS for Glycol Transfer Pump A | 01/04/05/07/09/11/13/15/17/19/21
245 | D01 | L-NSWGB-P-2103B | 0.4 | GCS-400-NSWG-001B | P-2103B | 1.5 | 3×4 | 3C | 4 | - | - | 370 | M25 | M25 EX | 22.6 | A | Glycol Transfer Pump B | 01/04/05/07/09/11/13/15/17/19/21
246 | D01 | C-NSWGB-P-2103B-02 | 0.23 | GCS-400-NSWG-001B | IRP (DCS) | - | 16×2.5 | 15C | 2.5 | - | - | 25 | M32 | M32 | 27.1 | E | IRP--DCS for Glycol Transfer Pump B | -
247 | D01 | C-NSWGB-P-2103B-03 | 0.23 | GCS-400-NSWG-001B | LCS | - | 7×2.5 | 7C | 2.5 | - | - | 370 | M25 | M25 EX | 25.3 | D | LCS for Glycol Transfer Pump B | 01/04/05/07/09/11/13/15/17/19/21
248 | D01 | L-NSWGB-P-2104 | 0.4 | GCS-400-NSWG-001B | P-2104 | 1.1 | 3×4 | 3C | 4 | - | - | 400 | M25 | M25 EX | 22.6 | A | Glycol Drain Pump | 01/04/22/24/25/27/29/31/33/34
249 | D01 | C-NSWGB-P-2104-02 | 0.23 | GCS-400-NSWG-001B | IRP (DCS) | - | 16×2.5 | 17C | 2.5 | - | - | 25 | M32 | M32 | 27.1 | E | IRP--DCS & ESD for Glycol Drain Pump | -
250 | D01 | C-NSWGB-P-2104-03 | 0.23 | GCS-400-NSWG-001B | LCS | - | 7×2.5 | 7C | 2.5 | - | - | 400 | M25 | M25 EX | 25.3 | D | LCS for Glycol Drain Pump | 01/04/22/24/25/27/29/31/33/34
251 | D01 | L-NSWGB-CR-01 | 0.4 | GCS-400-NSWG-001B | GCS-400-CR-01 | 10 | 3×25+16 | 4C | 25 | 16 | - | 260 | M40 | M40 EX | 34.4 | A | Main Compressor Crane | 01/04/05/07/09/11/12
252 | D01 | L-NSWGA-CR-02 | 0.4 | GCS-400-NSWG-001A | GCS-400-CR-02 | 5 | 4×10 | 4C | 10 | 10 | - | 200 | M25 | M25 | 22.1 | B | Fire Water Pumps Crane | 36/40/41/42
253 | D01 | L-NSWGA-MCC-01 | 0.4 | GCS-400-NSWG-001A | GCS-400-MCC-01 | 20 | 4×50 | 4C | 50 | 50 | - | 250 | M50 | M50 EX | 42.2 | A | Process Area Normal Lighting Panel | 01/04/05/07/09/10
254 | D01 | L-NSWGE-EDP-01 | 0.4 | GCS-400-NSWG-001E | GCS-400-EDP-01 | 10 | 4×25 | 4C | 25 | 25 | - | 250 | M40 | M40 EX | 34.4 | A | Process Area Emergency Lighting Panel | 01/04/05/07/09/10
255 | D01 | L-NSWGB-MCC-02 | 0.4 | GCS-400-NSWG-001B | GCS-400-MCC-02 | 10 | 4×25 | 4C | 25 | 25 | - | 220 | M32 | M32 | 28.4 | B | Utility Area Normal Lighting Panel | 36/40/41/42/43
256 | D01 | L-NSWGE-EDP-02 | 0.4 | GCS-400-NSWG-001E | GCS-400-EDP-02 | 5 | 4×10 | 4C | 10 | 10 | - | 220 | M25 | M25 | 22.1 | B | Utility Area Emergency Lighting Panel | 36/40/41/42/43
257 | D01 | L-NSWGA-WS-PR-01 | 0.4 | GCS-400-NSWG-001A | WS-PR-01 | 35 | 3×50+25 | 4C | 50 | 25 | - | 250 | M50 | M50 EX | 42.2 | A | First Welding Receptacle (Process Area) | 01/04/05/07/09/11/12
258 | D01 | L-WS-PR-01-WS-PR-02 | 0.4 | WS-PR-01 | WS-PR-02 | 35 | 3×50+25 | 4C | 50 | 25 | - | 75 | M50 | M50 EX | 42.2 | A | to Junction Box for Second Welding Receptacle (Process Area) | Site Run
259 | D01 | L-WS-PR-01-SC-PR-01 | 0.23 | WS-PR-01 | SC-PR-01 | 3 | 3×4 | 3C | 4 | 4 | - | 2 | M25 | M25 EX | 22.6 | A | to Junction Box for Fisrt Outlet Socket (Process Area) | -
260 | D01 | L-WS-PR-02-SC-PR-02 | 0.23 | WS-PR-02 | SC-PR-02 | 3 | 3×4 | 3C | 4 | 4 | - | 2 | M25 | M25 EX | 22.6 | A | to Junction Box for Second Outlet Socket (Process Area) | -
261 | D01 | L-NSWGB-WS-PR-03 | 0.4 | GCS-400-NSWG-001B | WS-PR-03 | 35 | 3×50+25 | 4C | 50 | 25 | - | 310 | M50 | M50 EX | 42.2 | A | Third Welding Receptacle (Process Area) | 01/04/22/24/25/27/28
262 | D01 | L-WS-PR-03-WS-PR-04 | 0.4 | WS-PR-03 | WS-PR-04 | 35 | 3×50+25 | 4C | 50 | 25 | - | 50 | M50 | M50 EX | 42.2 | A | to Junction Box for Fourth Welding Receptacle (Process Area) | Site Run
263 | D01 | L-WS-PR-03-SC-PR-03 | 0.23 | WS-PR-03 | SC-PR-03 | 3 | 3×4 | 3C | 4 | 4 | - | 2 | M25 | M25 EX | 22.6 | A | to Junction Box for Third Welding Receptacle (Process Area) | -
264 | D01 | L-WS-PR-04-WS-PR-05 | 0.4 | WS-PR-04 | WS-PR-05 | 35 | 3×50+25 | 4C | 50 | 25 |  | 60 | M50 | M50 EX | 42.2 | A | to Junction Box for Fifth Welding Receptacle (Process Area) | Site Run
265 | D01 | L-WS-PR-04-SC-PR-04 | 0.23 | WS-PR-04 | SC-PR-04 | 3 | 3×4 | 3C | 4 | 4 | - | 2 | M25 | M25 EX | 22.6 | A | to Junction Box for Fourth Outlet Socket (Process Area) | -
266 | D01 | L-WS-PR-05-WS-SC-05 | 0.23 | WS-PR-05 | SC-PR-05 | 3 | 3×4 | 3C | 4 | 4 | - | 2 | M25 | M25 EX | 22.6 | A | to Junction Box for Fitfth Outlet Socket (Process Area) | -
267 | D01 | L-NSWGA-WS-UT-01 | 0.4 | GCS-400-NSWG-001A | WS-UT-01 | 35 | 3×50+25 | 4C | 50 | 25 | - | 225 | M40 | M40 | 36.3 | B | First Welding Receptacle (Utility Area) | 36/40/41/42/43
268 | D01 | L-WS-UT-01-SC-UT-01 | 0.23 | WS-UT-01 | SC-UT-01 | 3 | 3×4 | 3C | 4 | 4 | - | 2 | M20 A | M20 A | 16.6 | B | to Junction Box for First Outlet Socket (Utility Area) | -
269 | D01 | L-NSWGB-WS-UT-02 | 0.4 | GCS-400-NSWG-001B | WS-UT-02 | 35 | 3×50+25 | 4C | 50 | 25 | - | 275 | M40 | M40 | 36.3 | B | Second Welding Receptacle (Utility Area) | 36/40/44/45/46/47
270 | D01 | L-WS-UT-02-SC-UT-02 | 0.23 | WS-UT-02 | SC-UT-02 | 3 | 3×4 | 3C | 4 | 4 | - | 2 | M20 A | M20 A | 16.6 | B | to Junction Box for Second Outlet Socket (Utility Area) | -
271 | D01 | L-NSWGA-CP01 | 0.4 | GCS-400-NSWG-001A | GCS-400-CP01 | 5 | 4×10 | 4C | 10 | 10 | - | 425 | M32 | M32 EX | 28.1 | A | Cathodic Protection Transformer Rectifier1 | 01/04/22/24/25/27/29/31/33/35
272 | D01 | L-NSWGA-110-CHG001 | 0.4 | GCS-400-NSWG-001A | GCS-110-CHG-001 | 20 | 4×16 | 4C | 16 | 16 | - | 25 | M25 | M25 | 24.5 | B | 110VDC Charger 1 | -
273 | D01 | L-110-CHG001-FB1 | 0.11DC | GCS-110-CHG-001 | 110-Fuse Box 1 | 7.5 | 2×50 | 2C | 50 | - | - | 20 | M32 | M32 | 30.2 | B | DC Charger Fuse Box 1 | -
274 | D01 | L-110CH-FB1-BAT1 | 0.11DC | 110-Fuse Box 1 | 110-Battery Bank 1 | 7.5 | 2×50 | 2C | 50 | - | - | 20 | M32 | M32 | 30.2 | B | DC Charger Battery Bank 1 | -
275 | D01 | L-NSWGE-110-CHG002 | 0.4 | GCS-400-NSWG-001E | GCS-110-CHG-002 | 20 | 4×16 | 4C | 16 | 16 | - | 30 | M25 | M25 | 24.5 | B | 110VDC Charger 2 | -
276 | D01 | L-110-CHG002-FB2 | 0.11DC | GCS-110-CHG-002 | 110-Fuse Box 2 | 7.5 | 2×50 | 2C | 50 | - | - | 20 | M32 | M32 | 30.2 | B | DC Charger Fuse Box 2 | -
277 | D01 | L-110CH-FB2-BAT2 | 0.11DC | 110-Fuse Box 2 | 110-Battery Bank 2 | 7.5 | 2×50 | 2C | 50 | - | - | 20 | M32 | M32 | 30.2 | B | DC Charger Battery Bank 2 | -
278 | D01 | L-110CH-F05 | 0.11DC | GCS-110-CHG-F05 | 3.3 KV New Switchgear | 0.7 | 2×6 | 2C | 6 | - | - | 15 | M20 A | M20 A | 16.8 | B | To 3.3 KV New Switchgear | -
279 | D01 | L-110CH-F09 | 0.11DC | GCS-110-CHG-F09 | 0.4 KV New Switchgear A | 0.75 | 2×6 | 2C | 6 | - | - | 25 | M20 A | M20 A | 16.8 | B | To 0.4 KV New Switchgear A & Coupler | -
280 | D01 | L-110CH-F10 | 0.11DC | GCS-110-CHG-F10 | 0.4 KV New Switchgear B | 0.75 | 2×6 | 2C | 6 | - | - | 30 | M20 A | M20 A | 16.8 | B | To 0.4 KV New Switchgear B | -
281 | D01 | L-110CH-F11 | 0.11DC | GCS-110-CHG-F11 | 0.4 KV New Switchgear E | 0.7 | 2×6 | 2C | 6 | - | - | 35 | M20 A | M20 A | 16.8 | B | To 0.4 KV New Switchgear E | -
282 | D01 | L-110CH-F12 | 0.11DC | GCS-110-CHG-F12 | RCP | 0.1 | 2×6 | 2C | 6 | - | - | 40 | M20 A | M20 A | 16.8 | B | To RCP | -
283 | D01 | L-NSWGA-24-CHG001 | 0.4 | GCS-400-NSWG-001A | GCS-24-CHG-001 | 18.5 | 4×16 | 4C | 16 | 16 | - | 50 | M25 | M25 | 24.5 | B | 24VDC Charger 1 | -
284 | D01 | L-24-CHG001-FB1 | 0.024DC | GCS-24-CHG-001 | 24-Fuse Box 1 | 5.55 | 2×185 | 2C | 10 | - | - | 20 | M50 | M50 | 50.5 | B | DC Charger Fuse Box 1 | -
285 | D01 | L-24-FB1-BAT1 | 0.024DC | 24-Fuse Box 1 | 24-Battery Bank 1 | 5.55 | 2×185 | 2C | 10 | - | - | 15 | M50 | M50 | 50.5 | B | DC Charger Battery Bank 1 | -
286 | D01 | L-NSWGE-24-CHG002 | 0.4 | GCS-400-NSWG-001E | GCS-24-CHG-002 | 18.5 | 4×16 | 4C | 16 | 16 | - | 60 | M25 | M25 | 24.5 | B | 24VDC Charger 2 | -
287 | D01 | L-24-CHG002-FB2 | 0.024DC | GCS-24-CHG-002 | 24-Fuse Box 2 | 5.55 | 2×185 | 2C | 10 | - | - | 20 | M50 | M50 | 50.5 | B | DC Charger Fuse Box 2 | -
288 | D01 | L-24-FB2-BAT2 | 0.024DC | 24-Fuse Box 2 | 24-Battery Bank 2 | 5.55 | 2×185 | 2C | 10 | - | - | 15 | M50 | M50 | 50.5 | B | DC Charger Battery Bank 2 | -
289 | D01 | L-24CH-F03 | 0.024DC | GCS-24-CHG-F03 | F&G System Panel | 2.7 | 2×95 | 2C | 95 | - | - | 20 | M40 | M40 | 37.8 | B | F&G System Panel | -
290 | D01 | L-24CH-F04 | 0.024DC | GCS-24-CHG-F04 | F&G System Panel | 2.7 | 2×95 | 2C | 95 | - | - | 20 | M40 | M40 | 37.8 | B | F&G System Panel (Redundant) | -
291 | D01 | L-24CH-F05 | 0.024DC | GCS-24-CHG-F05 | F&G Marshaling Panel 1 | 2.7 | 2×95 | 2C | 95 | - | - | 20 | M40 | M40 | 37.8 | B | F&G Marshaling Panel 1 | -
292 | D01 | L-24CH-F06 | 0.024DC | GCS-24-CHG-F06 | F&G Marshaling Panel 1 | 2.7 | 2×95 | 2C | 95 | - | - | 20 | M40 | M40 | 37.8 | B | F&G System Panel 1 (Redundant) | -
293 | D01 | L-24CH-F07 | 0.024DC | GCS-24-CHG-F07 | F&G Marshaling Panel 2 | 2.7 | 2×95 | 2C | 95 | - | - | 20 | M40 | M40 | 37.8 | B | F&G Marshaling Panel 2 | -
294 | D01 | L-24CH-F08 | 0.024DC | GCS-24-CHG-F08 | F&G Marshaling Panel 2 | 2.7 | 2×95 | 2C | 95 | - | - | 20 | M40 | M40 | 37.8 | B | F&G System Panel 2 (Redundant) | -
295 | D01 | L-24CH-F09 | 0.024DC | GCS-24-CHG-F09 | FACP | 0.9 | 2×50 | 2C | 50 | - | - | 30 | M32 | M32 | 30.2 | B | FACP | -
296 | D01 | L-24CH-F10 | 0.024DC | GCS-24-CHG-F10 | FACP | 0.9 | 2×50 | 2C | 50 | - | - | 30 | M32 | M32 | 30.2 | B | FACP (Redundant) | -
297 | D01 | L-24CH-F11 | 0.024DC | GCS-24-CHG-F11 | Fire Protection | 0.8 | 2×120 | 2C | 120 | - | - | 80 | M50 | M50 | 41 | B | Fire Protection & Total Flooding System UCP | -
298 | D01 | L-24CH-F12 | 0.024DC | GCS-24-CHG-F12 | Fire Protection | 0.8 | 2×120 | 2C | 120 | - | - | 80 | M50 | M50 | 41 | B | Fire Protection & Total Flooding System UCP (Redundant) | -
299 | D01 | L-NSWGA-110-UPS001 | 0.4 | GCS-400-NSWG-001A | GCS-110-UPS-001 | 36 | 3×35+16 | 4C | 35 | 16 | - | 45 | M32 | M32 | 32.1 | B | 110VAC UPS 1 | -
300 | D01 | L-110-UPS001-FB1 | 0.11DC | GCS-110-UPS-001 | 110-Fuse Box 1 | 25 | 2×150 | 2C | 150 | - | - | 15 | M50 | M50 | 44.7 | B | UPS Fuse Box 1 | -
301 | D01 | L-110UPS-FB1-BAT1 | 0.11DC | 110-Fuse Box 1 | 110-Battery Bank 1 | 25 | 2×150 | 2C | 150 | - | - | 15 | M50 | M50 | 44.7 | B | UPS Battery Bank 1 | -
302 | D01 | L-NSWGA-110-UPS002 | 0.4 | GCS-400-NSWG-001E | GCS-110-UPS-001 | 36 | 3×35+16 | 4C | 35 | 16 | - | 55 | M32 | M32 | 32.1 | B | 110VAC UPS 2 | -
303 | D01 | L-110-UPS002-FB2 | 0.11DC | GCS-110-UPS-001 | 110-Fuse Box 2 | 25 | 2×150 | 2C | 150 | - | - | 15 | M50 | M50 | 44.7 | B | UPS Fuse Box 2 | -
304 | D01 | L-110UPS-FB2-BAT2 | 0.11DC | 110-Fuse Box 2 | 110-Battery Bank 2 | 25 | 2×150 | 2C | 150 | - | - | 15 | M50 | M50 | 44.7 | B | UPS Battery Bank 2 | -
305 | D01 | L-NSWGE-UPS-Bypass | 0.4 | GCS-400-NSWG-001E | GCS-110-UPS-Bypass | 20 | 3×25+16 | 4C | 25 | 16 | - | 55 | M32 | M32 | 28.4 | B | 110VAC UPS By Pass | -
306 | D01 | L-110UPS-F03 | 0.11AC | GCS-110-UPS-F03 | DCS System Panel | 0.7 | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 12 | M20 A | M20 A | 15.3 | B | To Power Supply for CPUs | -
307 | D01 | L-110UPS-F04 | 0.11AC | GCS-110-UPS-F04 | DCS System Panel | 0.7 | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 12 | M20 A | M20 A | 15.3 | B | To Power Supply for CPUs (Redundant) | -
308 | D01 | L-110UPS-F05 | 0.11AC | GCS-110-UPS-F05 | DCS System Panel | 0.6 | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 12 | M20 A | M20 A | 15.3 | B | To 110/24 VDC Power Supply | -
309 | D01 | L-110UPS-F06 | 0.11AC | GCS-110-UPS-F06 | DCS System Panel | 0.6 | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 12 | M20 A | M20 A | 15.3 | B | To 110/24 VDC Power Supply (Redundant) | -
310 | D01 | L-110UPS-F07 | 0.11AC | GCS-110-UPS-F07 | DCS Marshaling Panel | 0.9 | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 12 | M20 A | M20 A | 15.3 | B | To 110/24 VDC Power Supply | -
311 | D01 | L-110UPS-F08 | 0.11AC | GCS-110-UPS-F08 | DCS Marshaling Panel | 0.9 | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 12 | M20 A | M20 A | 15.3 | B | To 110/24 VDC Power Supply (Redundant) | -
312 | D01 | L-110UPS-F09 | 0.11AC | GCS-110-UPS-F09 | ESD System Panel | 0.7 | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 15 | M20 A | M20 A | 15.3 | B | To Power Supply for CPUs | -
313 | D01 | L-110UPS-F10 | 0.11AC | GCS-110-UPS-F10 | ESD System Panel | 0.7 | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 15 | M20 A | M20 A | 15.3 | B | To Power Supply for CPUs (Redundant) | -
314 | D01 | L-110UPS-F11 | 0.11AC | GCS-110-UPS-F11 | ESD System Panel | 0.78 | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 15 | M20 A | M20 A | 15.3 | B | To 110/24 VDC Power Supply | -
315 | D01 | L-110UPS-F12 | 0.11AC | GCS-110-UPS-F12 | ESD System Panel | 0.78 | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 15 | M20 A | M20 A | 15.3 | B | To 110/24 VDC Power Supply (Redundant) | -
316 | D01 | L-110UPS-F13 | 0.11AC | GCS-110-UPS-F13 | ESD Marshaling Panel | 0.58 | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 15 | M20 A | M20 A | 15.3 | B | To 110/24 VDC Power Supply | -
317 | D01 | L-110UPS-F14 | 0.11AC | GCS-110-UPS-F14 | ESD Marshaling Panel | 0.58 | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 15 | M20 A | M20 A | 15.3 | B | To 110/24 VDC Power Supply (Redundant) | -
318 | D01 | L-110UPS-F15 | 0.11AC | GCS-110-UPS-F15 | Elecro Gas Compressor UCP A | 1.5 | 3×4 | 3C | 4 | 4 | 4 | 30 | M20 A | M20 A | 16.6 | B | Elecro Gas Compressor UCP A Ssystem & Marshaling | -
319 | D01 | L-110UPS-F16 | 0.11AC | GCS-110-UPS-F16 | Elecro Gas Compressor UCP A | 1.5 | 3×4 | 3C | 4 | 4 | 4 | 30 | M20 A | M20 A | 16.6 | B | Elecro Gas Compressor UCP A Ssystem & Marshaling (Redundant) | -
320 | D01 | L-110UPS-F17 | 0.11AC | GCS-110-UPS-F17 | Elecro Gas Compressor UCP B | 1.5 | 3×4 | 3C | 4 | 4 | 4 | 30 | M20 A | M20 A | 16.6 | B | Elecro Gas Compressor UCP B Ssystem & Marshaling | -
321 | D01 | L-110UPS-F18 | 0.11AC | GCS-110-UPS-F18 | Elecro Gas Compressor UCP B | 1.5 | 3×4 | 3C | 4 | 4 | 4 | 30 | M20 A | M20 A | 16.6 | B | Elecro Gas Compressor UCP B Ssystem & Marshaling (Redundant) | -
322 | D01 | L-110UPS-F19 | 0.11AC | GCS-110-UPS-F19 | Elecro Gas Compressor UCP C | 1.5 | 3×4 | 3C | 4 | 4 | 4 | 30 | M20 A | M20 A | 16.6 | B | Elecro Gas Compressor UCP C Ssystem & Marshaling | -
323 | D01 | L-110UPS-F20 | 0.11AC | GCS-110-UPS-F20 | Elecro Gas Compressor UCP C | 1.5 | 3×4 | 3C | 4 | 4 | 4 | 30 | M20 A | M20 A | 16.6 | B | Elecro Gas Compressor UCP C Ssystem & Marshaling (Redundant) | -
324 | D01 | L-110UPS-F21 | 0.11AC | GCS-110-UPS-F21 | Dehydration Package A (UCP/BMS) | 3 | 3×10 | 3C | 10 | 10 | 10 | 35 | M25 | M25 | 20.7 | B | Dehydration Package A LCP/Analyzer/BMS | -
325 | D01 | L-110UPS-F22 | 0.11AC | GCS-110-UPS-F22 | Dehydration Package A (UCP/BMS) | 3 | 3×10 | 3C | 10 | 10 | 10 | 35 | M25 | M25 | 20.7 | B | Dehydration Package A LCP/Analyzer/BMS (Redundant) | -
326 | D01 | L-110UPS-F23 | 0.11AC | GCS-110-UPS-F23 | Dehydration Package B (UCP/BMS) | 3 | 3×10 | 3C | 10 | 10 | 10 | 35 | M25 | M25 | 20.7 | B | Dehydration Package B LCP/Analyzer/BMS | -
327 | D01 | L-110UPS-F24 | 0.11AC | GCS-110-UPS-F24 | Dehydration Package B (UCP/BMS) | 3 | 3×10 | 3C | 10 | 10 | 10 | 35 | M25 | M25 | 20.7 | B | Dehydration Package B LCP/Analyzer/BMS (Redundant) | -
328 | D01 | L-110UPS-F25 | 0.11AC | GCS-110-UPS-F25 | Paging System | 1 | 3×4 | 3C | 4 | 4 | 4 | 35 | M20 A | M20 A | 16.6 | B | To Paging System | -
329 | D01 | L-110UPS-F26 | 0.11AC | GCS-110-UPS-F26 | Paging System | 1 | 3×4 | 3C | 4 | 4 | 4 | 35 | M20 A | M20 A | 16.6 | B | To Paging System (Redundant) | -
330 | D01 | L-110UPS-F27 | 0.11AC | GCS-110-UPS-F27 | Air Compressor A | 2 | 3×4 | 3C | 4 | 4 | 4 | 15 | M20 A | M20 A | 16.6 | B | Air Compressor Local UCP A | -
331 | D01 | L-110UPS-F28 | 0.11AC | GCS-110-UPS-F28 | Air Compressor A | 2 | 3×4 | 3C | 4 | 4 | 4 | 15 | M20 A | M20 A | 16.6 | B | Air Compressor Local UCP A (Redundant) | -
332 | D01 | L-110UPS-F29 | 0.11AC | GCS-110-UPS-F29 | Air Compressor B | 2 | 3×4 | 3C | 4 | 4 | 4 | 15 | M20 A | M20 A | 16.6 | B | Air Compressor Local UCP B | -
333 | D01 | L-110UPS-F30 | 0.11AC | GCS-110-UPS-F30 | Air Compressor B | 2 | 3×4 | 3C | 4 | 4 | 4 | 15 | M20 A | M20 A | 16.6 | B | Air Compressor Local UCP B (Redundant) | -
334 | D01 | L-110UPS-F31 | 0.11AC | GCS-110-UPS-F31 | Air Drayer A | 1.6 | 3×50 | 3C | 50 | 50 | 50 | 300 | M40 | M40 | 33.3 | B | Air Drayer A Local LCP | 36/40/44/45/46/47
335 | D01 | L-110UPS-F32 | 0.11AC | GCS-110-UPS-F32 | Air Drayer A | 1.6 | 3×50 | 3C | 50 | 50 | 50 | 300 | M40 | M40 | 33.3 | B | Air Drayer A Local LCP (Redundant) | 36/40/44/45/46/47
336 | D01 | L-110UPS-F33 | 0.11AC | GCS-110-UPS-F33 | Air Drayer B | 1.6 | 3×50 | 3C | 50 | 50 | 50 | 300 | M40 | M40 | 33.3 | B | Air Drayer B Local LCP | 36/40/44/45/46/47
337 | D01 | L-110UPS-F34 | 0.11AC | GCS-110-UPS-F34 | Air Drayer B | 1.6 | 3×50 | 3C | 50 | 50 | 50 | 300 | M40 | M40 | 33.3 | B | Air Drayer B Local LCP (Redundant) | 36/40/44/45/46/47
338 | D01 | L-110UPS-F35 | 0.11AC | GCS-110-UPS-F35 | Nitrogen Package | 1 | 3×4 | 3C | 4 | 4 | 4 | 15 | M20 A | M20 A | 16.6 | B | Nitrogen Package Local UCP A/B | -
339 | D01 | L-110UPS-F36 | 0.11AC | GCS-110-UPS-F36 | Nitrogen Package | 1 | 3×4 | 3C | 4 | 4 | 4 | 15 | M20 A | M20 A | 16.6 | B | Nitrogen Package Local UCP A/B (Redundant) | -
340 | D01 | L-110UPS-F37 | 0.11AC | GCS-110-UPS-F37 | Operator WorkStation | 2.964 | 3×10 | 3C | 10 | 10 | 10 | 35 | M25 | M25 | 20.7 | B | Operator WorkStation (Including DCS, ESD, Package) | -
341 | D01 | L-110UPS-F38 | 0.11AC | GCS-110-UPS-F38 | DCS Engineering Workstation | 0.713 | 3×4 | 3C | 4 | 4 | 4 | 20 | M20 A | M20 A | 16.6 | B | To DCS Engineering Workstation | -
342 | D01 | L-110UPS-F39 | 0.11AC | GCS-110-UPS-F39 | ESD Engineering Workstation | 0.713 | 3×4 | 3C | 4 | 4 | 4 | 20 | M20 A | M20 A | 16.6 | B | To ESD Engineering Workstation | -
343 | D01 | L-110UPS-F40 | 0.11AC | GCS-110-UPS-F40 | F&G Operator / Engineering | 0.713 | 3×4 | 3C | 4 | 4 | 4 | 20 | M20 A | M20 A | 16.6 | B | To F&G Operator / Engineering | -
344 | D01 | L-110UPS-F41 | 0.11AC | GCS-110-UPS-F41 | Printer A | 1.8 | 3×6 | 3C | 6 | 6 | 6 | 35 | M20 A | M20 A | 17.5 | B | To Operator / Engineering Printer A | -
345 | D01 | L-110UPS-F42 | 0.11AC | GCS-110-UPS-F42 | Printer B | 1.8 | 3×6 | 3C | 6 | 6 | 6 | 35 | M20 A | M20 A | 17.5 | B | To Operator / Engineering Printer B | -
346 | D01 | L-110UPS-F43 | 0.11AC | GCS-110-UPS-F43 | Printer C | 1.8 | 3×6 | 3C | 6 | 6 | 6 | 35 | M20 A | M20 A | 17.5 | B | To Operator / Engineering Printer C | -
347 | D01 | L-NSWGE-Non UPS | 0.4 | GCS-400-NSWG-001E | GCS-400-Non UPS | 8 | 4×10 | 4C | 10 | 10 | - | 60 | M25 | M25 | 22.1 | B | Non-UPS Load for Instrument | -
348 | D01 | L-Non UPS-F01 | 0.23 | GCS-400-Non UPS-F01 | F01 | 0.7 | 3×4 | 3C | 4 | 4 | - | 30 | M20 A | M20 A | 16.6 | B | Cabinet Utilities For DCS A (Heater, Fan, Light) | -
349 | D01 | L-Non UPS-F02 | 0.23 | GCS-400-Non UPS-F02 | F02 | 0.7 | 3×4 | 3C | 4 | 4 | - | 30 | M20 A | M20 A | 16.6 | B | Cabinet Utilities For DCS B (Heater, Fan, Light) | -
350 | D01 | L-Non UPS-F03 | 0.23 | GCS-400-Non UPS-F03 | F03 | 0.7 | 3×4 | 3C | 4 | 4 | - | 30 | M20 A | M20 A | 16.6 | B | Cabinet Utilities For DCS C (Heater, Fan, Light) | -
351 | D01 | L-Non UPS-F04 | 0.23 | GCS-400-Non UPS-F04 | F04 | 0.7 | 3×4 | 3C | 4 | 4 | - | 30 | M20 A | M20 A | 16.6 | B | Cabinet Utilities For DCS D (Heater, Fan, Light) | -
352 | D01 | L-Non UPS-F05 | 0.23 | GCS-400-Non UPS-F05 | F05 | 0.7 | 3×4 | 3C | 4 | 4 | - | 30 | M20 A | M20 A | 16.6 | B | Cabinet Utilities For ESD A (Heater, Fan, Light) | -
353 | D01 | L-Non UPS-F06 | 0.23 | GCS-400-Non UPS-F06 | F06 | 0.7 | 3×4 | 3C | 4 | 4 | - | 30 | M20 A | M20 A | 16.6 | B | Cabinet Utilities For ESD B (Heater, Fan, Light) | -
354 | D01 | L-Non UPS-F07 | 0.23 | GCS-400-Non UPS-F07 | F07 | 0.7 | 3×4 | 3C | 4 | 4 | - | 30 | M20 A | M20 A | 16.6 | B | Cabinet Utilities For ESD C (Heater, Fan, Light) | -
355 | D01 | L-Non UPS-F08 | 0.23 | GCS-400-Non UPS-F08 | F08 | 0.7 | 3×4 | 3C | 4 | 4 | - | 25 | M20 A | M20 A | 16.6 | B | Cabinet Utilities For F&G A (Heater, Fan, Light) | -
356 | D01 | L-Non UPS-F09 | 0.23 | GCS-400-Non UPS-F08 | F09 | 0.7 | 3×4 | 3C | 4 | 4 | - | 25 | M20 A | M20 A | 16.6 | B | Cabinet Utilities For F&G B (Heater, Fan, Light) | -
357 | D01 | L-Non UPS-F10 | 0.23 | GCS-400-Non UPS-F08 | F10 | 0.7 | 3×4 | 3C | 4 | 4 | - | 25 | M20 A | M20 A | 16.6 | B | Cabinet Utilities For F&G C (Heater, Fan, Light) | -
358 | D01 | L-Non UPS-F11 | 0.23 | GCS-400-Non UPS-F09 | F11 | 0.7 | 3×4 | 3C | 4 | 4 | - | 10 | M20 A | M20 A | 16.6 | B | Cabinet Utilities For Gas Compressor UCP A (Heater, Fan, Light) | -
359 | D01 | L-Non UPS-F12 | 0.23 | GCS-400-Non UPS-F09 | F12 | 0.7 | 3×4 | 3C | 4 | 4 | - | 10 | M20 A | M20 A | 16.6 | B | Cabinet Utilities For Gas Compressor UCP B (Heater, Fan, Light) | -
360 | D01 | L-Non UPS-F13 | 0.23 | GCS-400-Non UPS-F09 | F13 | 0.7 | 3×4 | 3C | 4 | 4 | - | 10 | M20 A | M20 A | 16.6 | B | Cabinet Utilities For Gas Compressor UCP C (Heater, Fan, Light) | -
361 | D01 | L-Non UPS-F14 | 0.23 | GCS-400-Non UPS-F10 | F14 | 0.7 | 3×4 | 3C | 4 | 4 | - | 10 | M20 A | M20 A | 16.6 | B | Cabinet Utilities For Dehydration BMS A ( if any) (Heater, Socket, Fan, Light) | -
362 | D01 | L-Non UPS-F15 | 0.23 | GCS-400-Non UPS-F10 | F15 | 0.7 | 3×4 | 3C | 4 | 4 | - | 10 | M20 A | M20 A | 16.6 | B | Cabinet Utilities For Dehydration BMS B ( if any) (Heater, Socket, Fan, Light) | -
363 | D01 | L-Non UPS-F16 | 0.23 | GCS-400-Non UPS-F11 | F16 | 0.7 | 3×4 | 3C | 4 | 4 | - | 75 | M20 A | M20 A | 16.6 | B | Cabinet Utilities For Total Flooding UCP(Heater, Socket, Fan, Light) | -
364 | D01 | L-Non UPS-F17 | 0.23 | GCS-400-Non UPS-F12 | F17 | 0.7 | 3×4 | 3C | 4 | 4 | - | 30 | M20 A | M20 A | 16.6 | B | Cabinet Utilities For Paging Cabinet (Heater, Socket, Fan, Light) | -
365 | D01 | L-Non UPS-F18 | 0.23 | GCS-400-Non UPS-F13 | F18 | 0.7 | 3×4 | 3C | 4 | 4 | - | 20 | M20 A | M20 A | 16.6 | B | Cabinet Utilities For Air Compressor UCP A (Heater, Socket, Fan, Light) | -
366 | D01 | L-Non UPS-F19 | 0.23 | GCS-400-Non UPS-F13 | F19 | 0.7 | 3×4 | 3C | 4 | 4 | - | 20 | M20 A | M20 A | 16.6 | B | Cabinet Utilities For Air Compressor UCP B (Heater, Socket, Fan, Light) | -
367 | D01 | L-Non UPS-F20 | 0.23 | GCS-400-Non UPS-F14 | F20 | 0.7 | 3×4 | 3C | 4 | 4 | - | 25 | M20 A | M20 A | 16.6 | B | Cabinet Utilities For Nitrogen package UCP(Heater, Socket, Fan, Light) | -
368 | D01 | L-Non UPS-F21 | 0.23 | GCS-400-Non UPS-F15 | F21 | 3.5 | 3×10 | 3C | 10 | 10 | - | 30 | M25 | M25 | 20.7 | B | Control Desk Sockets | -
369 | D01 | L-NSWGE-FDP 01 | 0.4 | GCS-400-NSWG-001E | GCS-230-FDP 01 | 1 | 4×4 | 4C | 4 | 4 | - | 210 | M20 A | M20 A | 17.7 | B | Fire Diesel Panel | 36/40/41/55
370 | D01 | L-NSWGE-SPH-01 | 0.4 | GCS-400-NSWG-001E | SPH-01 | 2 | 4×4 | 4C | 4 | 4 | - | 20 | M20 A | M20 A | 17.7 | B | Space Heater & Lighting for New LV Switchgear | -
371 | D01 | L-NSWGE-SPH-02 | 0.4 | GCS-400-NSWG-001E | SPH-02 | 2 | 4×4 | 4C | 4 | 4 | - | 30 | M20 A | M20 A | 17.7 | B | Space Heater & Lighting for MV Switchgear | -
372 | D01 | L-NSWGE-EDP-CRM | 0.4 | GCS-400-NSWG-001E | GCS-400-EDP-CRM | 23 | 4×25 | 4C | 25 | 16 | - | 75 | M32 | M32 | 28.4 | B | Emergency Lighting Panel for Extention of Control Room | 37
373 | D01 | L-NSWGE-EHTC |  | GCS-400-NSWG-001E | EHTC | [11 empty] | Electrical Heat Tracing | 01/04/05/07/09/11/12
374 | D01 | L-NSWGA-CAP-A-01 | 0.4 | GCS-400-NSWG-001A | CAP-01 | 120 | 3×185 | 3C | 185 | - | - | 35 | M63 | M63 | 56.9 | B | Cable 1 of LV Switchgear A Capacitor Bank | -
375 | D01 | L-NSWGA-CAP-A-02 | 0.4 | GCS-400-NSWG-001A | CAP-01 | 120 | 3×185 | 3C | 185 | - | - | 35 | M63 | M63 | 56.9 | B | Cable 2 of LV Switchgear A Capacitor Bank | -
376 | D01 | C-NSWGA-CAP-A |  | GCS-400-NSWG-001A | CAP-01 | - | 7×2.5 | 7C | 2.5 | - | - | 35 | M25 | M25 | 20 | E | Control Cable of LV Switchgear A Capacitor Bank | -
377 | D01 | L-NSWGA-CAP-B-01 | 0.4 | GCS-400-NSWG-001B | CAP-02 | 120 | 3×185 | 3C | 185 | - | - | 25 | M63 | M63 | 56.9 | B | Capacitor Bank 2 of LV Switchgear B | -
378 | D01 | L-NSWGA-CAP-B-02 | 0.4 | GCS-400-NSWG-001B | CAP-02 | 120 | 3×185 | 3C | 185 | - | - | 25 | M63 | M63 | 56.9 | B | Capacitor Bank 2 of LV Switchgear B | -
379 | D01 | C-NSWGA-CAP-B |  | GCS-400-NSWG-001B | CAP-02 | - | 7×2.5 | 7C | 2.5 | - | - | 25 | M25 | M25 | 20 | E | Control Cable of LV Switchgear A Capacitor Bank | -
380 | D01 | L-NSWGA-DG-001A1 | 0.4 | GCS-400-NSWG-001A | GCS-DG-001 | 400 | 1×300 | 1C | 300 | - | - | 30 | M40 | M40 | 34.2 | C | to Generator Control Panel | -
381 | D01 | L-NSWGA-DG-001A2 | 0.4 | GCS-400-NSWG-001A | GCS-DG-001 | 400 | 1×300 | 1C | 300 | - | - | 30 | M40 | M40 | 34.2 | C | to Generator Control Panel | -
382 | D01 | L-NSWGA-DG-001B1 | 0.4 | GCS-400-NSWG-001A | GCS-DG-001 | 400 | 1×300 | 1C | 300 | - | - | 30 | M40 | M40 | 34.2 | C | to Generator Control Panel | -
383 | D01 | L-NSWGA-DG-001B2 | 0.4 | GCS-400-NSWG-001A | GCS-DG-001 | 400 | 1×300 | 1C | 300 | - | - | 30 | M40 | M40 | 34.2 | C | to Generator Control Panel | -
384 | D01 | L-NSWGA-DG-001C1 | 0.4 | GCS-400-NSWG-001A | GCS-DG-001 | 400 | 1×300 | 1C | 300 | - | - | 30 | M40 | M40 | 34.2 | C | to Generator Control Panel | -
385 | D01 | L-NSWGA-DG-001C2 | 0.4 | GCS-400-NSWG-001A | GCS-DG-001 | 400 | 1×300 | 1C | 300 | - | - | 30 | M40 | M40 | 34.2 | C | to Generator Control Panel | -
386 | D01 | L-NSWGA-DG-001N1 | 0.4 | GCS-400-NSWG-001A | GCS-DG-001 | 400 | 1×300 | 1C | - | 300 | - | 30 | M40 | M40 | 34.2 | C | to Generator Control Panel | -
387 | D01 | M-11SWGA-CAP-1 | 11 | GCS-11-SWG-001A | Existing MV Capacitor Bank 1 | 350 kvar | 3×95 | 3C | 95 | - | - | 35 | M90 | M90 | 79.1 | I | From New Location of Existing Capacitor Bank1 to Existing MV Cell | -
388 | D01 | M-11SWGB-CAP-2 | 11 | GCS-11-SWG-001B | Existing MV Capacitor Bank 2 | 350 kvar | 3×95 | 3C | 95 | - | - | 35 | M90 | M90 | 79.1 | I | From New Location of Existing Capacitor Bank2 to Existing MV Cell | -
389 | D01 | M-11SWGB-CAP-3 | 11 | GCS-11-SWG-001B | Existing MV Capacitor Bank 3 | 350 kvar | 3×95 | 3C | 95 | - | - | 35 | M90 | M90 | 79.1 | I | From New Location of Existing Capacitor Bank3 to Existing MV Cell | -
390 | D01 | L-NSWGE-CCTV | 0.4 | GCS-11-SWG-001E | CCTV Control Building | 10 | 3×35+16 | 4C | 35 | 16 | - | 200 | M32 | M32 | 32.1 | B |  | 36/38/39

## Lighting
Item | Rev | Cable Tag No. | Service Voltage (KV) | Equipment Tag |  | Rating (KW) | Size | Cable Size (SQMM) |  |  |  | Length (m) |  | Cable Gland Size |  | O.D (mm) | Cable Type | Description | ROUT
|  |  |  | From | To |  |  | Core | Phase | N | E |  |  | Source | Field
1 | D01 | L-NDP01F01-FLTJB34 | 0.4 | GCS-400-NDP-01/F01 | NEW FLT-34RST-JB | 8 | 5×10 | 5C | 10 | 10 | 10 | 340 |  | M25 | M25 | 28.3 | A | To Latest Flood Lighting Tower in The Line | 21S/20S/16S/15S/14S/13S/12S/01S
2 | D01 | - | 0.23 | FLT-JB | Floodlight Fixtures |  | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 100 |  | M20 A | M20 A | 15.3 | B | From Tower JB to Terminal Box & Floodlight Fixtures | 21S/20S/16S/15S/14S/13S/12S/01S
3 | D01 | L-NDP01F02-FLTJB5 | 0.4 | GCS-400-NDP-01/F02 | EXISTING FLT-5RST | 3.5 | 5×10 | 5C | 10 | 10 | 10 | 190 |  | M25 | M25 | 28.3 | A | To Latest Flood Lighting Tower in The Line
4 | D01 | - | 0.23 | FLT-JB | Floodlight Fixtures |  | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 80 |  | M20 A | M20 A | 15.3 | B | From Tower JB to Terminal Box & Floodlight Fixtures
5 | D01 | L-NDP02F01-FLTJB35 | 0.4 | GCS-400-NDP-02/F01 | NEW FLT-35RST | 4.5 | 5×10 | 5C | 10 | 10 | 10 | 210 |  | M25 | M25 | 22.3 | B | To Latest Flood Lighting Tower in The Line | 02S/08S
6 | D01 | - | 0.23 | FLT-JB | Floodlight Fixtures |  | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 70 |  | M20 A | M20 A | 15.3 | B | From Tower JB to Terminal Box & Floodlight Fixtures | 02S/08S
7 | D01 | L-EDP02F01-JB | 0.23 | GCS-400-EDP-02/F01 | FLT-UT-F01-JB | 0.036 | 3×6 | 3C | 6 | 6 | 6 | 65 |  | M20 A | M20 A | 17.5 | B | To First Fluorescent Lighting JB in The Line | 02S/08S
8 | D01 | - | 0.23 | FLT-UT-F01-JB | Fluorescent Lighting Fixtures |  | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 15 |  | M20 A | M20 A | 15.3 | B | From Fluorescent Lighting JB to Fluorescent Lightings | 02S/08S
9 | D01 | L-EDP02F02-JB | 0.23 | GCS-400-EDP-02 | FLT-UT-F02-JB | 0.018 | 3×6 | 3C | 6 | 6 | 6 | 170 |  | M20 A | M20 A | 17.5 | B | To First Fluorescent Lighting JB in The Line | 02S/08S
10 | D01 | - | 0.23 | FLT-UT-F02-JB | Fluorescent Lighting Fixtures |  | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 5 |  | M20 A | M20 A | 15.3 | B | From Fluorescent Lighting JB to Fluorescent Lightings | 02S/08S
11 | D01 | L-EDP02F03-JB | 0.23 | GCS-400-EDP-02 | FLT-UT-F03-JB | 0.018 | 3×6 | 3C | 6 | 6 | 6 | 180 |  | M20 A | M20 A | 17.5 | B | To First Fluorescent Lighting JB in The Line | 02S/08S
12 | D01 | - | 0.23 | FLT-UT-F03-JB | Fluorescent Lighting Fixtures |  | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 5 |  | M20 A | M20 A | 15.3 | B | From Fluorescent Lighting JB to Fluorescent Lightings | 02S/08S
13 | D01 | L-EDP02F04-JB | 0.23 | GCS-400-EDP-02 | FLT-UT-F04-JB | 0.126 | 3×6 | 3C | 6 | 6 | 6 | 30 |  | M20 A | M20 A | 17.5 | B | To First Fluorescent Lighting JB in The Line | 02S/08S
14 | D01 | - | 0.23 | FLT-UT-F04-JB | Fluorescent Lighting Fixtures |  | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 80 |  | M20 A | M20 A | 15.3 | B | From Fluorescent Lighting JB to Fluorescent Lightings | 02S/08S
15 | D01 | L-EDP02F05-JB | 0.23 | GCS-400-EDP-02 | FLT-UT-F05-JB | 0.126 | 3×6 | 3C | 6 | 6 | 6 | 60 |  | M20 A | M20 A | 17.5 | B | To First Fluorescent Lighting JB in The Line | 02S/08S
16 | D01 | - | 0.23 | FLT-UT-F05-JB | Fluorescent Lighting Fixtures |  | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 80 |  | M20 A | M20 A | 15.3 | B | From Fluorescent Lighting JB to Fluorescent Lightings | 02S/08S
17 | D01 | L-EDP01F01-JB | 0.23 | GCS-400-EDP-01 | FLC-PR-F01-JB | 0.108 | 3×6 | 3C | 6 | 6 | 6 | 220 | EX | M25 | M25 | 23.5 | A | To First Fluorescent Lighting JB in The Line
18 | D01 | - | 0.23 | FLC-PR-F01-JB | Fluorescent Lighting Fixtures |  | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 55 | EX | M20 A | M20 A | 15.3 | B | From Fluorescent Lighting JB to Fluorescent Lightings
19 | D01 | L-EDP01F02-JB | 0.23 | GCS-400-EDP-01 | FLC-PR-F02-JB | 0.108 | 3×6 | 3C | 6 | 6 | 6 | 260 | EX | M25 | M25 | 23.5 | A | To First Fluorescent Lighting JB in The Line
20 | D01 | - | 0.23 | FLC-PR-F02-JB | Fluorescent Lighting Fixtures |  | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 55 | EX | M20 A | M20 A | 15.3 | B | From Fluorescent Lighting JB to Fluorescent Lightings
21 | D01 | L-EDP01F03-JB | 0.23 | GCS-400-EDP-01 | FLC-PR-F03-JB | 0.108 | 3×6 | 3C | 6 | 6 | 6 | 290 | EX | M25 | M25 | 23.5 | A | To First Fluorescent Lighting JB in The Line
22 | D01 | - | 0.23 | FLC-PR-F03-JB | Fluorescent Lighting Fixtures |  | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 55 | EX | M20 A | M20 A | 15.3 | B | From Fluorescent Lighting JB to Fluorescent Lightings
23 | D01 | L-EDP01F04-JB | 0.23 | GCS-400-EDP-01 | FLC-PR-F04-JB | 0.108 | 3×6 | 3C | 6 | 6 | 6 | 320 | EX | M25 | M25 | 23.5 | A | To First Fluorescent Lighting JB in The Line
24 | D01 | - | 0.23 | FLC-PR-F04-JB | Fluorescent Lighting Fixtures |  | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 75 | EX | M20 A | M20 A | 15.3 | B | From Fluorescent Lighting JB to Fluorescent Lightings
25 | D01 | L-EDP01F05-JB | 0.23 | GCS-400-EDP-01 | FLC-PR-F05-JB | 0.144 | 3×6 | 3C | 6 | 6 | 6 | 230 | EX | M25 | M25 | 23.5 | A | To First Fluorescent Lighting JB in The Line
26 | D01 | - | 0.23 | FLC-PR-F05-JB | Fluorescent Lighting Fixtures |  | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 65 | EX | M20 A | M20 A | 15.3 | B | From Fluorescent Lighting JB to Fluorescent Lightings
27 | D01 | L-EDP01F06-JB | 0.23 | GCS-400-EDP-01 | FLC-PR-F06-JB | 0.144 | 3×6 | 3C | 6 | 6 | 6 | 270 | EX | M25 | M25 | 23.5 | A | To First Fluorescent Lighting JB in The Line | 02S/08S
28 | D01 | - | 0.23 | FLC-PR-F06-JB | Fluorescent Lighting Fixtures |  | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 65 | EX | M20 A | M20 A | 15.3 | B | From Fluorescent Lighting JB to Fluorescent Lightings
29 | D01 | L-EDP01F07-JB | 0.23 | GCS-400-EDP-01 | FLC-PR-F07-JB | 0.18 | 3×6 | 3C | 6 | 6 | 6 | 320 | EX | M25 | M25 | 23.5 | A | To First Fluorescent Lighting JB in The Line | 02S/08S
30 | D01 | - | 0.23 | FLC-PR-F07-JB | Fluorescent Lighting Fixtures |  | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 90 | EX | M20 A | M20 A | 15.3 | B | From Fluorescent Lighting JB to Fluorescent Lightings
31 | D01 | L-EDP01F08-JB | 0.23 | GCS-400-EDP-01 | FLC-PR-F08-JB | 0.126 | 3×6 | 3C | 6 | 6 | 6 | 260 | EX | M25 | M25 | 23.5 | A | To First Fluorescent Lighting JB in The Line | 02S/08S
32 | D01 | - | 0.23 | FLC-PR-F08-JB | Fluorescent Lighting Fixtures |  | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 130 | EX | M20 A | M20 A | 15.3 | B | From Fluorescent Lighting JB to Fluorescent Lightings
33 | D01 | L-EDP01F09-JB | 0.23 | GCS-400-EDP-01 | FLC-PR-F09-JB | 0.108 | 3×6 | 3C | 6 | 6 | 6 | 100 | EX | M25 | M25 | 23.5 | A | To First Fluorescent Lighting JB in The Line | 02S/08S
34 | D01 | - | 0.23 | FLC-PR-F09-JB | Fluorescent Lighting Fixtures |  | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 75 | EX | M20 A | M20 A | 15.3 | B | From Fluorescent Lighting JB to Fluorescent Lightings
35 | D01 | L-EDP01F10-JB | 0.23 | GCS-400-EDP-01 | FLC-PR-F10-JB | 0.036 | 3×6 | 3C | 6 | 6 | 6 | 160 | EX | M25 | M25 | 23.5 | A | To First Fluorescent Lighting JB in The Line | 02S/08S
36 | D01 | - | 0.23 | FLC-PR-F10-JB | Fluorescent Lighting Fixtures |  | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 15 | EX | M20 A | M20 A | 15.3 | B | From Fluorescent Lighting JB to Fluorescent Lightings