## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-EL-LI-0002_D00 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1082 |  |  | Transmital Date: 15-Jun-2022
Document Title: Electrical Power & Control Cable Schedule |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-EL-TR-1082 |  |  | Transmital Date: 15-Jun-2022
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-PEDCO-120-EL-LI-0002_D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | This document shall be revised and issued as AFC after finalizing or minor comments on below prerequisite documents: -Electrical Load List -Electrical Equipment Arrangement Layout For Building -Calculation Note For Cable Sizing -Area Electrical Cable Route & Section Layout -Electrical Cable Route & Section Layout For Building & Shelter -Area Lighting & Small Power Layout -Specification For Power & Control Cables -Electrical I/O Signal List |  | BK-SUR-ENG-ELE-01-04835 | 2022-06-22 | اعمال گردید.
2 | Control cables shall be considered in a separated sheet. |  | BK-SUR-ENG-ELE-01-04835 | 2022-06-22 | کابلهای مربوط به هر تجهیز اعم از قدرت و کنترل در کنار هم آورده شده است.
3 | According to our telephone conversation following cables shall be added to cable list: |  | BK-SUR-ENG-ELE-01-04835 | 2022-06-22 | اعمال گردید.
3-1 | The new power MV cable between existing MV capacitor bank and existing MV switchgear |  | BK-SUR-ENG-ELE-01-04835 | 2022-06-22 | اعمال گردید.
3-2 | The Power LV cable between generator and diesel generator control panel |  | BK-SUR-ENG-ELE-01-04835 | 2022-06-22 | با وندور ژنراتور می باشد.
3-3 | The Power LV cable between diesel generator control panel and LV switchgear |  | BK-SUR-ENG-ELE-01-04835 | 2022-06-22 | اضافه گردید.
3-4 | The Control cables between diesel generator and LV switchgear |  | BK-SUR-ENG-ELE-01-04835 | 2022-06-22 | اضافه گردید.
3-5 | The Power LV cable between LV switchgear and 230VAC UPS (For CCTV system) |  | BK-SUR-ENG-ELE-01-04835 | 2022-06-22 | اضافه گردید.
3-6 | The Power LV cable for 110VDC/24VDC/110VAC/230VAC UPS outgoing feeders |  | BK-SUR-ENG-ELE-01-04835 | 2022-06-22 | اضافه گردید.
3-7 | The Control cables between RCP and MV switchgear incomings, Coupling and outgoings |  | BK-SUR-ENG-ELE-01-04835 | 2022-06-22 | اضافه گردید.
3-8 | The Control cables between DCS (IRP) and MV/LV switchgears incomings, Coupling and outgoing feeders, AC/DC UPS, diesel generator, transformer, etc. |  | BK-SUR-ENG-ELE-01-04835 | 2022-06-22 | اضافه گردید.
3-9 | The Control cables for interlocks and intertrips |  | BK-SUR-ENG-ELE-01-04835 | 2022-06-22 | اضافه گردید.
3-10 | The Cables between LV switchgear and capacitor banks (Current sample). |  | BK-SUR-ENG-ELE-01-04835 | 2022-06-22 | اضافه گردید.
3-11 | The Cables for differential protection CT |  | BK-SUR-ENG-ELE-01-04835 | 2022-06-22 | اضافه گردید.
3-12 | Space heater cable for motor |  | BK-SUR-ENG-ELE-01-04835 | 2022-06-22 | اضافه گردید.
3-13 | Lighting cables (Especially outdoor area) |  | BK-SUR-ENG-ELE-01-04835 | 2022-06-22 | اضافه گردید.
4 | Cable type shall be completely mentioned in cable list such as conductor type, inner and outer insulation (XPLE or PVC), armour, Screen, etc. in legend sheet. |  | BK-SUR-ENG-ELE-01-04835 | 2022-06-22 | اضافه گردید.
5 | Considered cable type in "cable type" column shall be totally rechecked and modified base on scope of work and project requirement for example the primary side of transformer and LV capacitor bank shall be armour type and lead cover for MV capacitor bank not required. |  | BK-SUR-ENG-ELE-01-04835 | 2022-06-22 | به روزرسانی گردید.
6 | Cable type for compressor B, C and related capacitor bank have been mentioned "MAL3". This type has not been define in the legend |  | BK-SUR-ENG-ELE-01-04835 | 2022-06-22 | به روزرسانی گردید.
7 | According to telephone conversation, Control cables between MV/LV switchgear and IRP panel will be installed indoor (In cable gallery), so there is not need to lead cover and relevant cables type shall be modified in cable list (Only for process area shall be considered Lead Cover). |  | BK-SUR-ENG-ELE-01-04835 | 2022-06-22 | به روزرسانی گردید.
8 | Cables length shall be totally rechecked and modified for example according to latest revision of plot plan, fire water pump and jockey pump are near to each other but the cables length are different from each other or 110AC /24VDC will be installed in control room and it seems the related incoming cables shall be modified. |  | BK-SUR-ENG-ELE-01-04835 | 2022-06-22 | به روزرسانی گردید.
9 | According to telephone conversation, maximum cable length has not been checked in this document, so it is recommended to checked maximum cable length in cable sizing document for long distance cables. |  | BK-SUR-ENG-ELE-01-04835 | 2022-06-22 | به روزرسانی گردید.
10 | It shall be clarify lighting cable (For outgoing feeders of outdoor and indoor LP) will be considered in this document or not? |  | BK-SUR-ENG-ELE-01-04835 | 2022-06-22 | به روزرسانی گردید.
11 | Cable size of NGR shall be rechecked and modified. Meanwhile the size of RTD cable shall be added (10X3X1.5 or not?). |  | BK-SUR-ENG-ELE-01-04835 | 2022-06-22 | به روزرسانی گردید.
12 | According to cable list, all 11KV cables size (and without LC) except 800KVA transformer is 95mm². Therefore, in order to facilitate in purchasing process, it is recommended to change incoming cable size of 800KVA from 70mm² to 95mm². |  | BK-SUR-ENG-ELE-01-04835 | 2022-06-22 | به روزرسانی گردید.
13 | Incoming cable of LV capacitor banks shall be considered 4 core cable instead of 3 core cable. |  | BK-SUR-ENG-ELE-01-04835 | 2022-06-22 | به روزرسانی گردید.
14 | According to scope of work and endorsement, Fire resistance cable shall be used instead of MICC cable where required. (It is necessary to considered in hazardous area such as battery room, LP flare package, etc. base on hazardous area classification layout. ) |  | BK-SUR-ENG-ELE-01-04835 | 2022-06-22 | به روزرسانی گردید.
15 | According to our telephone conversation, two separate row shall be considered for HVAC system power cable like as LV capacitor bank . |  | BK-SUR-ENG-ELE-01-04835 | 2022-06-22 | به روزرسانی گردید.
16 | Type of gland (Ex or Non-Ex) shall be specified base on hazardous area classification layout. |  | BK-SUR-ENG-ELE-01-04835 | 2022-06-22 | به روزرسانی گردید.
17 | Reference document for OD cables and gland size shall be attached to document and submitted in next revision to check OD cables and gland size. |  | BK-SUR-ENG-ELE-01-04835 | 2022-06-22 | به روزرسانی گردید.
18 | Tag number for all cables shall be the same according to cable tag numbering procedure in legend sheet. |  | BK-SUR-ENG-ELE-01-04835 | 2022-06-22 | به روزرسانی گردید.
19 | Cable destination shall be rechecked and modified for example destination for cables to IRP shall be mentioned IRP instead of pump tag number. |  | BK-SUR-ENG-ELE-01-04835 | 2022-06-22 | به روزرسانی گردید.
20 | Complementary comments will be submitted after receive prerequisite and revised documents. |  | BK-SUR-ENG-ELE-01-04835 | 2022-06-22 | به روزرسانی گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 22-Jun-22 |  |  |  |  | Date: