## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-PPL-PEDCO-320-PR-PI-0001 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1731 |  |  | Transmital Date:12/28/2022
Document Title: P&ID - Gas Pipeline (to Siahmakan G.I. Station) |  |  |  |  | PEDCO Tr. No.:BK-PEDCO-NISOC-0005-PR-TR-1731 |  |  | Transmital Date:12/28/2022
[5 empty] | CRS No: NISOC-CRS-BK-PPL-PEDCO-320-PR-PI-0001_D04 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | سایز شیر ESDV-3202,3201 با مدرک سایزینگ PSV مطابقت ندارد. خروجی سایزینگ D میباشد ولی در PIDنشان E درج شده است. |  | 1401-2294-473531 | 1401/12/10 | مطابق آخرین نسخه مدرک PSV سایزینگ به روز رسانی شد.
2 | پاسخ ارائه شده توسط آن پیمانکار در خصوص نقطه نظر شماره 2 مورد قبول این امور نمیباشد. |  | 1401-2294-473531 | 1401/12/10 | با توجه به وجود PG-3201 بر روی تجهیز PL-3201 نیازی به در نظر گرفتن PG بر روی تجهیز مذکور نمی باشد. لازم به ذکر است مطابق اسناد پسمان و نقشه استاندارد مربوط به پیگ رسیور S4L-6516-Rev. B(NISOC STD.) یک کانکشن جهت اتصال PG کافی میباشد.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: |  |  |  |  | Date: 24/08/2021