## Cover
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بستههای کاری تحت الارض ساخت موقعیت چاه، تأسیسات سرچاهی، خطوط جرياني، تسهیلات برق‌رسانی مربوط به موقعیت W007S و توسعه چندراهه کلاستر بینک
DATA SHEETS FOR ORIFICE PLATE/RESTRICTION ORIFICE - EXTENSION OF BINAK B/C MANIFOLD
شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 6
9184 – 073 - 053 |  |  | BK |  | W007S | PEDCO | 110 |  | IN | DT | 0008 | D00
طرح نگهداشت و افزایش تولید 27 مخزن
DATA SHEETS FOR ORIFICE PLATE/RESTRICTION ORIFICE - EXTENSION OF BINAK B/C MANIFOLD نگهداشت و افزایش تولید میدان نفتی بینک
D00 |  | NOV.2023 |  | IFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | S.Faramarzpour
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
Class: 1 |  |  |  | CLIENT Doc. Number: 'F9Z-707978
status: | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved

## REVISION
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بستههای کاری تحت الارض ساخت موقعیت چاه، تأسیسات سرچاهی، خطوط جرياني، تسهیلات برق‌رسانی مربوط به موقعیت W007S و توسعه چندراهه کلاستر بینک
DATA SHEETS FOR ORIFICE PLATE/RESTRICTION ORIFICE - EXTENSION OF BINAK B/C MANIFOLD
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 6
9184 – 073 - 053 |  |  | BK | W007S |  | PEDCO | 110 | IN | DT | 0008 |  | D00
REVISION RECORD SHEET
Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D01 |  | D02 | D03 | D04
1 | X | [7 empty] | 65
2 | X | [7 empty] | 66
3 | X | [7 empty] | 67
4 | X | [7 empty] | 68
5 | X | [7 empty] | 69
6 | X | [7 empty] | 70
7 | [8 empty] | 71
8 | [8 empty] | 72
9 | [8 empty] | 73
10 | [8 empty] | 74
11 | [8 empty] | 75
12 | [8 empty] | 76
13 | [8 empty] | 77
14 | [8 empty] | 78
15 | [8 empty] | 79
16 | [8 empty] | 80
17 | [8 empty] | 81
18 | [8 empty] | 82
19 | [8 empty] | 83
20 | [8 empty] | 84
21 | [8 empty] | 85
22 | [8 empty] | 86
23 | [8 empty] | 87
24 | [8 empty] | 88
25 | [8 empty] | 89
26 | [8 empty] | 90
27 | [8 empty] | 91
28 | [8 empty] | 92
29 | [8 empty] | 93
30 | [8 empty] | 94
31 | [8 empty] | 95
32 | [8 empty] | 96
33 | [8 empty] | 97
34 | [8 empty] | 98
35 | [8 empty] | 99
36 | [8 empty] | 100
37 | [8 empty] | 101
38 | [8 empty] | 102
39 | [8 empty] | 103
40 | [8 empty] | 104
41 | [8 empty] | 105
42 | [8 empty] | 106
43 | [8 empty] | 107
44 | [8 empty] | 108
45 | [8 empty] | 109
46 | [8 empty] | 110
47 | [8 empty] | 111
48 | [8 empty] | 112
49 | [8 empty] | 113
50 | [8 empty] | 114
51 | [8 empty] | 115
52 | [8 empty] | 116
53 | [8 empty] | 117
54 | [8 empty] | 118
55 | [8 empty] | 119
56 | [8 empty] | 120
57 | [8 empty] | 121
58 | [8 empty] | 122
59 | [8 empty] | 123
60 | [8 empty] | 124
61 | [8 empty] | 125
62 | [8 empty] | 126
63 | [8 empty] | 127
64 | [8 empty] | 128

## REFERENCE
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بستههای کاری تحت الارض ساخت موقعیت چاه، تأسیسات سرچاهی، خطوط جرياني، تسهیلات برق‌رسانی مربوط به موقعیت W007S و توسعه چندراهه کلاستر بینک
DATA SHEETS FOR ORIFICE PLATE/RESTRICTION ORIFICE - EXTENSION OF BINAK B/C MANIFOLD
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 3 از 6
9184 – 073 - 053 |  |  | BK | W007S | PEDCO | 110 | IN | DT | 0008 | D00
REFERENCE DOCUMENTS :
|  | Specification For Instrumentation | [6 empty] | BK-GNRAL-PEDCO-000-IN-SP-0001
|  | Process Basis Of Design | [6 empty] | BK-GNRAL-PEDCO-000-PR-DB-0001
|  | Piping Material Specification | [6 empty] | BK-SSGRL-PEDCO-110-PI-SP-0001
|  | Symbol & Legend For PFD and P&ID | [6 empty] | BK-SSGRL-PEDCO-110-PR-PI-0001
|  | P&ID - Extention of Binak B/C Manifold | [6 empty] | BK-W007S-PEDCO-110-PR-PI-0001

## Notes
NISOC |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بستههای کاری تحت الارض ساخت موقعیت چاه، تأسیسات سرچاهی، خطوط جرياني، تسهیلات برق‌رسانی مربوط به موقعیت W007S و توسعه چندراهه کلاستر بینک
DATA SHEETS FOR ORIFICE PLATE/RESTRICTION ORIFICE - EXTENSION OF BINAK B/C MANIFOLD
شماره پیمان: |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 4 از 6
9184 – 073 - 053 |  | BK | W007S | PEDCO | 110 | IN | DT | 0008 | D00
General Note:
1. Orifice plate and restriction orifice plates shall be stamped with manufacturer's name, tag no., bore size, line size/rating, plate material , plate thickness and the word 'upstream' on the upstream side of the paddle.
2. Bore sizing shall be done as per the full scale flow rate.
3.The calculation for orifice plates shall be produced in accordance with ISO 5167.
4. Datasheets shall be submitted for approval by purchaser. The orifice bore diameter shall be as per vendor's approved calculations.
5. Vendor shall provide certificate of compliance to NACE MR-0175 requirement for the instrument supplied, wherever specified.
6. Beta ratio limits shall be 0.2 to 0.7 For some cases where there is constraint vendor can size for beta ratio of More than 0.7 but however the beta ratio shall not exceed 0.75 as per ISO 5167. The orifice plate thickness shall be As per manufacturer's standard, however as a minimum shall be to ISO 5167 requirements
7. Vendor shall supply the orifice plate assembly complete with flanges, gasket, bolt&nuts and jack screws. All orifice flanges shall be as per ANSI B16.5 and orifice plates shall be supplied suitable for the same. Wherever 'FF' flange facing is indicated, the orifice plates shall be suitable for mounting between the flat faced flanges.
8. Orifice bore shall not be beveled for the restriction orifice plates.
9. Drain hole for vapor service and vent hole for liquid service shall be provided for the orifices in horizontal runs.
10. IPS-D-IN-103 regarding Orifice Plate Fabrication to be followed by vendor.
11 . Environmental Condition For Field Instrumentation Of Mansouri Complex Shall Be Considered As Per The Following:
Temperature:
Maximum ambient temperature: 50 (°C)
Minimum ambient temperature: 5 (°C)
Maximum steel surface exposed to sun: 85 (°C)
Maximum summer dry bulb: 50 (°C)
Maximum Design relative humidity (%): 100
Minimum Design relative humidity (%): 0
Maximum Design relative humidity (%): 100
Minimum Design relative humidity (%): 0
12. Max acceptable noise level for orifice and restriction orifice plate is 85 dbA in 1m.

## FE
NISOC |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بستههای کاری تحت الارض ساخت موقعیت چاه، تأسیسات سرچاهی، خطوط جرياني، تسهیلات برق‌رسانی مربوط به موقعیت W007S و توسعه چندراهه کلاستر بینک
DATA SHEETS FOR ORIFICE PLATE/RESTRICTION ORIFICE - EXTENSION OF BINAK B/C MANIFOLD
شماره پیمان: |  | پروژه | بسته کاری | صادر کننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 5 از 6
9184 – 073 - 053 |  | BK | W007S | PEDCO | 110 | IN | DT | 0008 | D00
FLOW ELEMENT (ORIFICE PLATE)
GENERAL | 1 | Tag No. | [5 empty] | SEE PAGE 5
| 2 | P&ID No. |  |  | Service |  |  | SEE PAGE 5 |  |  | SEE PAGE 5
| 3 | Line Size |  |  | Schedule |  |  | SEE PAGE 5 |  |  | SEE PAGE 5
| 4 | Piping Class | [5 empty] | SEE PAGE 5
| 5 | Nace Requirements | [5 empty] | SEE PAGE 5
6
PROCESS CONDITION | 7 | Fluid |  |  | Phase |  |  | SEE PAGE 5 |  |  | SEE PAGE 5
| 8 | Design Temperature |  |  | Operating Temperature |  | (°C) | SEE PAGE 5 |  |  | SEE PAGE 5
| 9 | Design Pressure |  |  | Operating Pressure |  | (bar-g) | SEE PAGE 5 |  |  | SEE PAGE 5
| 10 | Minimum Flow Rate |  |  | Normal Flow Rate |  | (kg/h) | SEE PAGE 5 |  |  | SEE PAGE 5
| 11 | Maximum Flow Rate |  |  |  |  | (kg/h) | SEE PAGE 5
| 12 | Density |  | (kg/m3) | Molecular Weight |  |  | SEE PAGE 5 |  |  | SEE PAGE 5
| 13 | Viscosity |  |  | Gas Compressibility Factor |  |  | SEE PAGE 5 |  |  | SEE PAGE 5
| 14 | Limit On Pressure Drop Across Flowmeter |  |  |  |  | (bar) | SEE PAGE 5
| 15 | Cp / Cv |  |  | Allowable Press. Drop |  |  | SEE PAGE 5 |  |  | SEE PAGE 5
| 16 | Liquid Vapor Pressure |  |  |  |  | (bara) | SEE PAGE 5
ORIFICE PLATE | 17 | Type |  |  | Sub Type |  |  | Sharp Edge Orifice |  |  | Concentric with Flange Tappings
| 18 | Material | [5 empty] | 316L S.S
| 19 | Flow Full Scale |  |  | Diff. Pressure Range |  |  | SEE PAGE 5 |  |  | SEE PAGE 5
| 20 | Construction Standard | [5 empty] | EN ISO 5167
| 21 | Plate Thickness | [5 empty] | SEE PAGE 5
| 22 | Bore Diameter | [5 empty] | SEE PAGE 5
| 23 | Beta Ratio (d/D) | [5 empty] | SEE PAGE 5
| 24 | Drain / Vent Hole | [5 empty] | Note 9
25
ORIFICE FLANGE | 26 | Flange Type | [5 empty] | Weld Neck Flanged Tap
| 27 | Flange Size | [5 empty] | SEE PAGE 5
| 28 | Flange Rating | [5 empty] | SEE PAGE 5
| 29 | Flange Facing | [5 empty] | SEE PAGE 5
| 30 | FlangeTapping Size | [5 empty] | 1/2" NPT
| 31 | Flange Material | [5 empty] | SEE PAGE 5
| 32 | Gasket Material | [5 empty] | S.S 316 Winding /Graphite Filler, C.S. Outer& S.S 316L Inner Ring
PURCHASING DATA | 33 | Model |  |  | Manufacture |  |  | will be finalized later |  |  | will be finalized later
| 34 | Supplier |  |  | Order |  |  | will be finalized later |  |  | will be finalized later
35
NOTES : | VTA :Vendor To Advice |  |  |  |  | VTC: VENDOR TO CONFIRM

## FE List
نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بستههای کاری تحت الارض ساخت موقعیت چاه، تأسیسات سرچاهی، خطوط جرياني، تسهیلات برق‌رسانی مربوط به موقعیت W007S و توسعه چندراهه کلاستر بینک
DATA SHEETS FOR ORIFICE PLATE/RESTRICTION ORIFICE - EXTENSION OF BINAK B/C MANIFOLD
شماره پیمان: |  |  |  |  | پروژه |  |  |  | بسته کاری |  |  |  | صادرکننده |  |  | تسهیلات | رشته | نوع مدرک |  |  | سریال |  | نسخه
[5 empty] | BK |  |  |  | W007S |  |  |  | PEDCO |  |  | 110 | IN | DT |  |  | 0008 |  | D00 |  |  | شماره صفحه: 6 از 6
9184 – 073 - 053
FLOW ELEMENT (ORIFICE PLATE)
Rev. | Item No. | Tag No. | P&ID No. | Line Number | Line Size | Schedule | Piping Class | Nace | Fluid | Phase | Temperature (°C) |  | Pressure (barg) |  | Flow Rate (Kg/h) GAS-LIQUID |  |  | Density (Kg/m3) (Mix./Liq./Gas) | Specific Gravity (LIQUID/GAS) | Molecular Weight(Kg/Kgmol) LIQUID/GAS | Viscosity(CP) (Gas/Liquid) | Allowable Press. Drop (barg) | Gas Compressibility Factor | Cp / Cv | Liquid Vapor Pressure (bara) | Max. Diff. Pressure Range(mbar) | Plate Thickness(mm) | Bore Diameter(inch) | Beta Ratio (d/D) | Flange Size | Flange Rating/Facing | Flange Material | Remark
[11 empty] | Design | Operating | Design | Operating | Min. | Normal | Max.
| 1 | FE-1701A | MIAS-06-HE-120-PR-PI-0009 ( 1 OF 4) | CRD-110-171A-FN05-4"-PT | 4" | SCH.80 | FN05 | YES | HC | GAS/LIQUID | 5~85 | 36.31 | 93 | 12.78 | 59.3600 / 3722.9859 | 178.0761 / 11168.9579 | 195.9100 / 12285.8537 | 384.4/864.1/11.39 | 0.8641/0.8158 | 231.1/23.66 | 0.01158/8.899 | 0.25 | 0.947 | 1.004 | 12.779 | 1.5 | 3.2 mm | VTA | VTA | 4" | 600# | ASTM A105
| 2 | FE-1701B | MIAS-06-HE-120-PR-PI-0009 ( 2 OF 4) | CRD-110-171B-FN05-4"-PT | 4" | SCH.80 | FN05 | YES | HC | GAS/LIQUID | 5~85 | 31.6 | 93 | 12.78 | 431.6600 / 11182.9443 | 647.4920 / 16774.4165 | 712.2410 / 18451.8581 | 230.1/825.8/11.77 | 0.8258/0.8265 | 204.5/23.97 | 0.01137/6.250 | 0.25 | 0.942 | 1.007 | 12.779 | 1.5 | 3.2 mm | VTA | VTA | 4" | 600# | ASTM A105
| 3 | FE-1701C | MIAS-06-HE-120-PR-PI-0009 ( 3 OF 4) | CRD-110-171C-FN05-4"-PT | 4" | SCH.80 | FN05 | YES | HC | GAS/LIQUID | 5~86 | 46.19 | 93 | 12.78 | 66.3500 / 3715.9978 | 199.0406 / 11147.9935 | 218.9550 / 12262.7928 | 361.4/857.5/11.50 | 0.8575/0.85 | 233.7/24.67 | 0.01184/7.604 | 0.25 | 0.948 | 1.005 | 12.779 | 1.5 | 3.2 mm | VTA | VTA | 4" | 600# | ASTM A105
| 4 | FE-1701D | MIAS-06-HE-120-PR-PI-0009 ( 4 OF 4) | CRD-110-171D-FN05-4"-PT | 4" | SCH.80 | FN05 | YES | HC | GAS/LIQUID | 5~87 | 44.41 | 93 | 12.78 | 718.1500 / 16703.7589 | 1196.9170 / 27839.5981 | 1316.6080 / 30623.5579 | 212.5/818.5/11.78 | 0.8185/0.8634 | 210.4/25.04 | 0.0173/5.391 | 0.25 | 0.944 | 1.007 | 12.779 | 1.5 | 3.2 mm | VTA | VTA | 4" | 600# | ASTM A105
| 5 | FE-1701E | MIAS-06-HE-120-PR-PI-0012 ( 1 OF 4) | CRD-110-171E-FN05-4"-PT | 4" | SCH.80 | FN05 | YES | HC | GAS/LIQUID | 5~88 | 40.71 | 93 | 12.78 | 697.2000 / 16.724.7065 | 1162.0040 / 27874.5109 | 1278.2040 / 30661.9620 | 217.4/820.6/11.77 | 0.8206/0.8527 | 208.7/24.73 | 0.01163/5.606 | 0.25 | 0.943 | 1.007 | 12.779 | 1.5 | 3.2 mm | VTA | VTA | 4" | 600# | ASTM A105
| 6 | FE-1701F | MIAS-06-HE-120-PR-PI-0012 ( 2 OF 4) | CRD-110-171F-FN05-4"-PT | 4" | SCH.80 | FN05 | YES | HC | GAS/LIQUID | 5~89 | 41.77 | 93 | 12.78 | 234.3800 / 5572.9181 | 468.7690 / 11145.8363 | 515.6450 / 12260.4200 | 216.0/820.0/11.77 | 0.82/0.8558 | 209.2/24.82 | 0.01165/5.543 | 0.25 | 0.943 | 1.007 | 12.779 | 1.5 | 3.2 mm | VTA | VTA | 4" | 600# | ASTM A105
| Note: | (1) HC:HYDROCARBONE , L: LIQUID , G: GAS , M: MIXED
(2) Vendor shall calculate the bore size & beta for 2 phase orifice plates.
(3) BLANK PLATE to be supplied. The bore shall be drilled later by others.
(4) Flange with 1/2" NPT tapping, gasket, bolts & nuts shall be supplied by instr. Vendor.
(5) No of holes per flange for orifice plates to be specified by vendor.