## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No:BK-GCS-PEDCO-120-AR-DW-0002 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-2375 |  |  | Transmital Date: 9/20/2023
Document Title: Architectural Detail Drawing For Extension of Existing Elect. Building |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-AR-T-2375 |  |  | Transmital Date:9/20/2023
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-AR-DW-0002_D05 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | 1- عطف به بند 3 در خصوص جزئیات بام، مشخصات ایزوگام سقف ذکر نشده است، همچنین عایق حرارتی در wall section نشان داده نشده است. اصلاح گردد. |  | 1402/2294/310820 | 1402/08/07 | اعمال گردید.
2 | 2- عطف به بند 6 در خصوص paving ، مشخصات بتن بر اساس استاندارد paving اصلاح گردد، همچنین ارجاع paving به مدرک BK-GCS-PEDCO-120-CV-PY-0005 اشتباه می باشد، بازنگری و اصلاح گردد. |  | 1402/2294/310820 | 1402/08/07 | مقاومت مشخصه بتن اصلاح شد. با توجه به اطلاعات کامل کف سازی، ارجاع تذکر داده شده حذف شد.
3 | 3- در خصوص عایق کاری بازشو فن، عایق کاری تا لبه های داخلی آن امتداد یابد، اصلاح شود. |  | 1402/2294/310820 | 1402/08/07 | اعمال گردید.
4 | 4- به جدول نازک کاری ردیف بام هم اضافه گردد. در خصوص قرنیز پشت بام همانند کف آن موزائیک لحاظ گردد. |  | 1402/2294/310820 | 1402/08/07 | انجام گردید.
5 | 5- در شیت 15/15 دیتایل 13 دیوار به شکل عمودی نمایش داده شود. |  | 1402/2294/310820 | 1402/08/07 | انجام گردید.
6 | 6- در شیت 13/15 دیتایل مربوط به درب ضد انفجار جزئیات درب و پرفیل های چارچوب آن لحاظ گردد. |  | 1402/2294/310820 | 1402/08/07 | دیتیل درب ضد انفجار در تعهد سازنده می باشد. ورق های مورد نیاز در مدرک سازه ساختمان در نظر گرفته می شود و چارچوب در ضد انفجار به آن جوش می شود.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: | Signature
| Date: |  |  |  |  | Date: