## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-W007S-PEDCO-110-PR-DT-0001 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1760 |  |  | Transmital Date: 1/3/2023
Document Title: Process Data Sheets For Instrument Devices - W007S & Extension Manifold |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-PR-TR-1760 |  |  | Transmital Date: 1/3/2023
[5 empty] | CRS No: NISOC-CRS-BK-W007S-PEDCO-110-PR-DT-0001_D02 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | فشار طراحی PG-1702 و PRV-1702 مطابق با آخرین ویرایش مدرک PID برابر با 17.3 بار نسبی در نظر گرفته شود. |  | 1401-2294-471721 | 1401/12/09 | اصلاح گردید.
2 | فشار طراحی PG-1704 A~F مطابق با کلاس فشاری ANSI-300 در نظر گرفته شود. |  | 1401-2294-471721 | 1401/12/09 | فشار طراحی تجهیز فوق بر اساس CRITERIA پروژه اصلاح گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: |  |  |  |  | Date: 24/08/2021