## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-W007S-PEDCO-110-PR-DT-0001 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1760 |  |  | Transmital Date: 1/3/2023
Document Title: Process Data Sheets For Instrument Devices - W007S & Extension Manifold |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-PR-TR-1760 |  |  | Transmital Date: 1/3/2023
[5 empty] | CRS No:PEDCO-CRS-BK-W007S-PEDCO-110-PR-DT-0001_D02 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | همانطور که در CRS ویرایش پیشین اشاره گردید، نظرات بخش فرآیند بر روی داده برگ تجهیزات ابزار دقیق ارائه خواهد شد. در خصوص این مدرک صرفا لازم است نقطه نظرات ذینفع اصلی پروژه اعمال گردد. |  | BK-SUR-ENG-PCS-01-06611 | 2023-01-04 | مورد تایید است .
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: |  |  |  |  | Date: 24/08/2021

## Diesel Oil
Tank Sizing (Vertical)
Item | Value | Unit
Height (H) | 1.5 | m
Diameter (ID) | 3.2 | m
HLL | 1.3 | m
LLL | 0.15 | m
Nominal Capacity | 12.0576 | m3
Working Capacity | 9.2442 | m3 | 9.1168
Elevation | 3.5 | m
Diesel Consumption
Usage | 21.5 | gal/hr for 300 kW
Usage | 0.0814 | m3/hr
Usage Duration | 8 | hr
Daily Usage | 0.6512 | m3
Hold-Up | 14 | day
Total Vol. | 9.1168 | m3
Note on D14: Roshanak Haditalab: Based on vendor data.
Note on D15: Roshanak Haditalab: Coverter.