| # | Clarification Title | Clarification Description (Rev.00) | Conclusion (Rev.00) (VENDOR to Confirm & Consider in the Final Offers) | Clarification Description (Rev.01) | Conclusion (Rev.01) (VENDOR to Confirm & Consider in the Final Offers) |
| --- | --- | --- | --- | --- | --- |
| GENERAL |  |  |  |  |  |
|  | Project’ s documents | Vendor to confirm that in case of contradiction between this TCL and offer; vendor confirmation of compliance through this technical clarification is governed and shall be followed by vendor after order. In such case offer won’t be considered as basis of any claim after order. | CONFIRM | Noted and closed. |  |
|  | Scope of supply | The SUPPLIER shall include in the scope of supply all other equipment, not listed in Material Requisition (Doc. No. BK-GCS-PEDCO-120-ME-MR-0012, but necessary for good design and safe operation based on his experiences and good engineering practice, taking into account process data and installation conditions such as area classification and environmental conditions. | CONFIRM | Noted and closed. |  |
|  | Deviation List | Bidder shall confirm his full compliance to meet all purchaser documents listed and attached to MR, code / standards listed in MR with ref. No. "BK-GCS-PEDCO-120-ME-MR-0012" as well as MR requirements. All deviations shall be listed in project deviation form, attach to this TCL, signed and stamped. Notes: 1-Any exception and deviation from the requirements of MR and the related specifications including referenced codes & standards shall be clearly declared by vendor in writing for purchaser’s approval at bid stage by using of the format included in “Letter Of Conformity” attached to material requisition. Raising no deviation to any single requirement means full compliance of vendor quotation to that requirement. Purchaser has no responsibility to discover deviations or alternatives scattered over the proposal in addition to what proclaimed explicitly in deviation list; hence such deviation (if any) is disregarded and shall not be considered for vendor claim in future. (Vendor to confirm) 2- Bidder shall confirm that all MR attachments listed in MR are available for her for review at bid stage. 3-Considering items 1 & 2, please note that any deviation at detail stage will not be accepted by purchaser. | CONFIRM | Noted and closed. |  |
|  | Documents Priority | Bidder to confirm his compliance with documents priority stated in MR. Any conflict between the documents shall be notified by bidder to purchaser and resolved by his agreement. | CONFIRM | Noted and closed. |  |
|  | Design of Flare packages | Design of Flare packages shall be fully in accordance with Material Requisition Doc. BK-GCS-PEDCO-120-ME-MR-0012, and all documents attached to the requisition and latest edition of the project applicable standards. Any deviation to applicable standards, the material requisition and project specifications will not be acceptable other than those mentioned clearly in bidders’ deviation list and confirmed by the purchaser. | CONFIRM | Noted and closed. |  |
|  | Sub-supplier | Please submit your Sub-supplier list. Sub-suppliers shall be selected based on the project approved vendor list, otherwise is subject to the Purchaser approval. | CONFIRM | Noted and closed. |  |
|  | Spare parts | Vendor shall supply spare parts for commissioning and start-up (included in base price) and spare parts for 2 years operation & capital spars (as optional price) in accordance with the requisition and project Spare Part Procedure as per E&C-QC-SP-1. | CONFIRM | Noted and closed. |  |
|  | Emission Ground Level | Vendor shall calculate and guarantee Emission Ground Level Concentration based on Project specifications and Iranian environmental laws, regulations and standards. | CONFIRM | Noted and closed. |  |
|  | Calculations | Bidder shall perform all calculations required as part of the design. The calculations will require approval by the Purchaser. Calculations shall be collected, catalogued and furnished as part of the equipment data books. | CONFIRM | Noted and closed. |  |
|  | Guarantee | Bidder shall clarify the performance guarantee, mechanical guarantee and guarantee period in his proposal based on Project’s M.R. and Specification. | CONFIRM | Noted and closed. |  |
|  | Environment Aspects | Bidder shall consider any legal regulation regarding environment aspects such as emissions monitoring which is define by Iran DOE (Department of Environment) and requested by Purchaser. | CONFIRM | Noted and closed. |  |
|  | Documentation | Documentation based on relevant procedures and VPIS according to material requisition scope of supply to be followed. | CONFIRM | Noted and closed. |  |
|  | Guarantee points | Refer to duty specification for lp flare packages (FST-2201) and (IG-2201) section 4.2, Guarantee points such as performance guarantee, capacity including smokeless capacity, pressure drop. Noise level and heat intensity to be defined. | CONFIRM | Noted and closed. |  |
|  | Document Requirement | Bidder to submit all required documents with tender as per “RFD Form” in the MR. For example below documents: 1-Marked up and Filled out MR scope of supply and works (It shall be signed and stamped) 2-GA DWG with outline dimensions and weights related to this project 3- A complete Equipment List 4-Noise Data 5-Utility Consumption and load List 7-Spare Part List | CONFIRM | Noted and closed. |  |
|  | Iranian environmental laws | Vendor shall calculate and guarantee Emission Ground Level Concentration based on Project specifications and Iranian environmental laws, regulations and standards. | CONFIRM | Noted and closed. |  |
|  | Approved Vendor List | Bidder shall consider PURCHASER Approved Vendor List (AVL) and in case of any deviation or contradiction, PURCHASER approval is mandatory. | CONFIRM | Noted and closed. |  |
|  | Project documents | Bidder to be considered below documents in his revised offer, which are referred in 2nd Purchaser comments: 1- Spare parts procedure (E&C-QC-SP-1) 2- Project approval vendor list (AVL). 4-Standard drawings for Pressure Vessel. 5-Seismic Design Code as per ASCE 7-5 6- PID DWG - BK-GCS-PEDCO-120-PR-PI-0020 01-Piping Comments | CONFIRM | Seismic Design Code is modified to ASCE 7-5. Please confirm. |  |
|  | Vendor’s Scope | Access ladder and platforms, stairway shall be studied, designed and supplied by vendor. Relevant detail drawings shall be submitted for approval in detail design stage. Gratings shall be hot dip galvanized. Please confirm. | CONFIRM | Noted and closed. |  |
|  | Document Requirement | Bidder to submit all required documents with tender as per “RFD Form” in the MR. For example below documents: 1-Marked up and Filled out MR scope of supply and works (It shall be signed and stamped) 2-P&ID 3-GA DWG with outline dimensions and weights related to this project 4-Blower Datasheet and DWG 5-Utility Consumption List 6- Reference List 7- Deviation List | Requested items will be provided after signing the contract |  |  |
|  | Applied Standards | Applied Standards for equipment design, fabrication and test shall be listed. | CONFIRM | Noted and closed. |  |
|  | Mechanical Comments on Proposal | For Mechanical comments on proposal please refer to Attachment #1 of this TCL. | CONFIRM | Noted and closed. |  |
|  | NEW ITEM |  |  | LPG bottles shall be considered according for 24 hour backup. |  |
|  | NEW ITEM |  |  | Bidder’ s to be considered new revision of Specification for flare via attachment. |  |
| Fired Equipment |  |  |  |  |  |
|  | Corrosion Allowance | Bidder shall define corrosion allowance in his design for main equipment. Based on Corrosion Study & Material (BK-GCS-PEDCO-120-PI-RT-0001.corrosion allowance for CS is 3.2 mm and for SS is 0 mm. | CONFIRM | Noted and closed. |  |
|  | Discharge Velocity | The pilots shall be suitable for lighting the flare gas at the maximum discharge velocity of Mach 0.5. | CONFIRM | Noted and closed. |  |
|  | Performance Test | Pilots shall remain lit and capable of being relit at wind speeds up to 120 km/h. This performance shall be verified by type testing in accordance with a documented test protocol and documented Results. (API 537, Section 4.7.2) | CONFIRM | Noted and closed. |  |
|  | Flare Radiation | Pilot heat release shall be specified Based on Flare Radiation & Dispersion Study Report. | CONFIRM | Noted and closed. |  |
|  | Smoke Opacity | Bidder shall confirm that smoke opacity is considered based on Ringelmann #1. | CONFIRM | Noted and closed. |  |
|  | FFG | FFG dimension shall be specified. | CONFIRM | Noted and closed. |  |
|  | Internal lining | Bidder shall define flare burner internal lining specification if required. | CONFIRM | Noted and closed. |  |
|  | Flares sizes | Bidder shall finalize Flares sizes in Bid Stage and environmental issues as well as guarantee points according to technical specification for flare packages shall be considered. | CONFIRM | Noted and closed. |  |
|  | Ignition panel | Ignition panel shall be included: - High Energy Generator - Remote ignition system - Flame Detector - Internal combustion Detector - Automatic Re-ignition system - Smokeless Operation (Min Smoke free flaring for 25% of design relief flow) - LPG Bottles for pilot gas Backup (for 12hours) - Aircraft warning lights | CONFIRM | Noted and closed. |  |
| PROCESS |  |  |  |  |  |
|  | Process Design | Bidder's process design shall be according to -PROCESS DESIGN CRITERIA "BK-GNRAL-PEDCO-000-PR-DC-0001_D02", -Process Basis of Design and "BK-GNRAL-PEDCO-000-PR-DB-0001_D08" -Flare Radiation & Dispersion Study Report "BK-GCS-PEDCO-120-PR-RT-0002-D04" -Flare, Blow Down And Relief Philosophy "BK-GCS-PEDCO-120-PR-PH-0003_D02" -Duty Specification for LP Flare Package "BK-GCS-PEDCO-120-PR-SP-0003_D04" Any possible deviations to be inform to PURCHASER for his acceptance or rejection. | CONFIRM | Noted and closed. |  |
|  | Site Condition | Site Condition Shall be corrected based on Process Basis of Design"BK-GNRAL-PEDCO-000-PR-DB-0001_D08" | THIS IS OUT OF VENDOR’S SCOPE OF WORK |  |  |
|  | Utility Consumption | utility consumption shall be provided | THIS IS OUT OF VENDOR’S SCOPE OF WORK |  |  |
|  | calculation | Flare radiation calculation shall be provided | CONFIRM | Noted and closed. |  |
|  | P&ID | Vendor shall be provided P&ID and INPUT/OUTPUT signals (at least) and any other required signal or facility which are shown on purchaser PID. | CONFIRM | Noted and closed. |  |
| INSTRUMENT |  |  |  |  |  |
|  | Control System Requirements | VENDOR shall follow BK-GNRAL-PEDCO-000-IN-SP-0004 and provide the requirement of type A package as mentioned in this document. VENDOR shall comply with all the requirements and mentioned any mismatch in deviation list which is attached to the PMR. Signal details and communications shall be followed as per project P&ID. | CONFIRM | Noted and closed. |  |
|  | Panel Requirements | VENDOR shall follow BK-GNRAL-PEDCO-000-IN-SP- 004 for panels mounted field panels and all other details mentioned in this document. VENDOR shall comply with all the requirements and mentioned any mismatch in deviation list which is attached to the PMR. | CONFIRM | Noted and closed. |  |
|  | Instrumentation | Regarding supplying instrument on datasheet, bidder is requested to consider all instruments/Signals mentioned on project datasheet and Project P&ID. High temperature condition shall considered for flare trips devices if any. VENDOR shall follow BK-GNRAL-PEDCO-000-IN-SP-0001 for instrumentation devices and all other details mentioned in this document. VENDOR shall comply with all the requirements and mentioned any mismatch in deviation list which is attached to the PMR. | CONFIRM | Noted and closed. |  |
|  | Instrumentation Valves | VENDOR shall follow below documents for valves ( if any)and other documents as mentioned in these documents. - BK-GNRAL-PEDCO-000-IN-SP-0005 - BK-GNRAL-PEDCO-000-IN-SP-0006 - BK-GNRAL-PEDCO-000-IN-SP-0007 VENDOR shall comply with all the requirements and mentioned any mismatch in deviation list which is attached to the PMR. | CONFIRM | Noted and closed. |  |
|  | Connection with MCC | If MCC is supplied by VENDOR all interfaces shall be supplied by VENDOR. Below signals are typically defined in this project to be provided for electrical interfaces: - Start command (2 sec high pulse) - Stop command (2 sec high pulse) - Trip command (low signal for trip) - Run/Stop Status (high signal for run status) - Local/Remote status (high signal for local status) - Tripped on Fault (high signal for fault status) - Available for remote control (high signal for available status) Detail signal requirements as per P&ID shall be followed. | CONFIRM | Noted and closed. |  |
|  | Cable | VENDOR shall follow BK-GNRAL-PEDCO-000-IN-SP-0010 for cables and all other details mentioned in this document. Special cable such as thermocouple cables shall be provided by vendor. VENDOR shall comply with all the requirements and mentioned any mismatch in deviation list which is attached to the PMR. | CONFIRM | Noted and closed. |  |
|  | Terminals | All terminals shall be screw type. VENDOR shall note that each core/pair/etc. of cable shall be wired to dedicated terminal | CONFIRM | Noted and closed. |  |
|  | Local Panel Dimension | VENDOR shall specify the estimated dimension of panels. | CONFIRM | Noted and closed. |  |
|  | Required Power | VENDOR shall specify the estimated power required (non-UPS and UPS) if any. Normally 400 VAC non UPS power will be submitted in package battery limit and all other required voltage shall be prepared by vendor. | CONFIRM | Noted and closed. |  |
|  | Special Tools | VENDOR shall supply all special tools for compressor and axillary devices. This is included the special cables (not mentioned in BK-GNRAL-PEDCO-000-IN-SP-0010), MODBUS sockets, software and etc. The list shall be provided separately. | CONFIRM | Noted and closed. |  |
|  | Protection Instruments | The protection rating of instruments shall be EEXD/e/ia and IP 65. VENDOR shall comply with all the requirements and mentioned any mismatch in deviation list which is attached to the PMR. | CONFIRM | Noted and closed. |  |
|  | Start-up | VENDOR shall clearly state the start-up sequence. It shall be mentioned if any additional instrument or valve is required. Also, the interface signals shall be mentioned (if any) | CONFIRM | Noted and closed. |  |
|  | Spare part | VENDOR shall supply all commissioning/ 2 years spare part as per NISOC procedure, attached to PMR for instrumentation and LCP. | CONFIRM | Noted and closed. |  |
|  | Project AVL | Project AVL shall be followed by vendor for instrument/ control item selection. Any deviation shall be specified in deviation list. | CONFIRM | Noted and closed. |  |
| ELECTRICAL |  |  |  |  |  |
|  | Specification | All electrical equipment shall comply with electrical references & standard that mentioned on material requisition. IPS-E-EL-100 (1). IPS-M-El-271 (2), IPS-M-El-161 (2), IPS-M-EL-131 (2) | CONFIRM | Noted and closed. |  |
|  | Vendor Scope of Work & Supply | All documents related to electrical equipment shall be submitted by vendor such as preliminary load list, electrical equipment list, cable list & . . . | CONFIRM | Noted and closed. |  |
|  | Specification | The rated voltage of project is 3pahse, 400/230 V, 50 Hz. Please consider them for detail design. | CONFIRM | Noted and closed. |  |
|  | Specification | If there is outdoor control panel IP shall be 65. | CONFIRM | Noted and closed. |  |
|  | Vendor Scope of Work | Vendor list & sub vendor list of manufacture shall be according to project AVL. | CONFIRM | Noted and closed. |  |
|  | Specification | Motor/ blower shall be manufactured & tested in accordance with the latest applicable sections of the IEC standards. Project specification shall be applied as well. | CONFIRM | Noted and closed. |  |
|  | Specification | Environmental criteria for design of electrical systems, shall be considered by vendor (According to Electrical System Design Criteria) | CONFIRM | Noted and closed. |  |
|  | Vendor Scope of Work | - Vendor shall issue required cable list. - Cables shall be according to “BK-GNRAL-PEDCO-000-EL-SP-0014”. | CONFIRM | Noted and closed. |  |
|  | Vendor Scope of Work | If AC UPS or DC UPS & batteries are required, vendor shall provide all necessary document & equipment (such as calculation, list etc.) & supply required equipment according to purchaser standards. | CONFIRM | Noted and closed. |  |
|  | Vendor Scope of Work | Required Electrical specifications have been attached. Vendor shall follow them. | CONFIRM | Noted and closed. |  |
|  | Vendor Scope of Work | According to manufacturer detail design, there are 2 below loads: - LP Flare Package (PK-2201( - LP Flare Ignition Package (IG-2201) Supply power is by client. Interconnection between vendor & client is JB of panel in which the power supply. Vendor shall consider, cables, rout, tray/ladder, lighting & other in the skid. | CONFIRM | Noted and closed. |  |
|  | Vendor Scope of Work | The cable for flare shall be MICC type. | CONFIRM | Noted and closed. |  |
|  | Spare Part | A complete set of spare parts for commissioning shall be supplied for each electrical equipment | CONFIRM | Noted and closed. |  |
| CIVIL |  |  |  |  |  |
|  | Earthquake load | Also according to ASCE 7 (2010) Seismic factor to be considered: Fa=1 FV=1.8 S1=0.313 Ss=1.125 I=1.25 Site Class=D Site Coefficient=1.2 | CIVIL IS NOT IN THE VENDOR’S SCOPE OF WORK | Also according to ASCE 7 (2010) Seismic factor to be considered: Fa=1 FV=1.8 S1=0.313 Ss=1.125 I=1.25 Site Class=D Site Coefficient=1.2 |  |
|  | Design criteria | Design criteria shall be confirmed and considered by VENDOR for any structural design (BK-GNRAL-PEDCO-000-ST-DC-0001-D02). | CIVIL IS NOT IN THE VENDOR’S SCOPE OF WORK | Design criteria shall be confirmed and considered by VENDOR for any structural design (BK-GNRAL-PEDCO-000-ST-DC-0001-D02). |  |
|  | Wind | According to project spec. mean hourly with 50Yr return period speed shall be considered 120 Km/hr. | CIVIL IS NOT IN THE VENDOR’S SCOPE OF WORK | According to project spec. mean hourly with 50Yr return period speed shall be considered 120 Km/hr. |  |
|  | Anchor bolt | The type & location of the anchor bolts shall be provided by VENDOR. | CIVIL IS NOT IN THE VENDOR’S SCOPE OF WORK | The type & location of the anchor bolts shall be provided by VENDOR. |  |
|  | Calculation book | Flare structure calculation book shall be provided by VENDOR, Structural analysis for flare stack shall be done by SAP software. | CIVIL IS NOT IN THE VENDOR’S SCOPE OF WORK | Flare structure calculation book shall be provided by VENDOR, Structural analysis for flare stack shall be done by SAP software. |  |
|  | Native files | All native files (such as software files and drawings) shall be submitted to the client. | CIVIL IS NOT IN THE VENDOR’S SCOPE OF WORK | All native files (such as software files and drawings) shall be submitted to the client. |  |
|  | Calculation | In the case of any platforms not covered by standard drawing structural calculation note shall be prepared and submitted. | CIVIL IS NOT IN THE VENDOR’S SCOPE OF WORK | In the case of any platforms not covered by standard drawing structural calculation note shall be prepared and submitted. |  |
|  | Material | For material of structural plates and profiles A36 or ST37 with Fy more than 2400Kg/cm2 shall be used unless stronger material is specified in data sheets or MR attachments. | CIVIL IS NOT IN THE VENDOR’S SCOPE OF WORK | For material of structural plates and profiles A36 or ST37 with Fy more than 2400Kg/cm2 shall be used unless stronger material is specified in data sheets or MR attachments. |  |
|  | Platforms | Minimum clear width for platforms shall be 800 mm. Of course finally the geometry and distance between platforms shall be approved by client during design (in case of order) | CIVIL IS NOT IN THE VENDOR’S SCOPE OF WORK | Minimum clear width for platforms shall be 800 mm. Of course finally the geometry and distance between platforms shall be approved by client during design (in case of order) |  |
|  | Bolts | A325 shall be used for structural bolts. | CIVIL IS NOT IN THE VENDOR’S SCOPE OF WORK | A325 shall be used for structural bolts. |  |
|  | Connections | All structural connections shall be bolted connection in site. ( for shop connections , weld connection could be used ) | CIVIL IS NOT IN THE VENDOR’S SCOPE OF WORK | All structural connections shall be bolted connection in site. ( for shop connections , weld connection could be used ) |  |
|  | Erection and transportation | Erection and transportation procedure and relevant supporting documents shall be provided and submitted to client for approval. | CIVIL IS NOT IN THE VENDOR’S SCOPE OF WORK | Erection and transportation procedure and relevant supporting documents shall be provided and submitted to client for approval. |  |
|  | References | The below specifications shall be considered in the construction of steel structures: - Specification for Fabrication of Steel Structures (BK-GNRAL-PEDCO-000-ST-SP-0003) - Specification for Erection of Steel Structures (BK-GNRAL-PEDCO-000-ST-SP-0005) | CIVIL IS NOT IN THE VENDOR’S SCOPE OF WORK | The below specifications shall be considered in the construction of steel structures: - Specification for Fabrication of Steel Structures (BK-GNRAL-PEDCO-000-ST-SP-0003) Specification for Erection of Steel Structures (BK-GNRAL-PEDCO-000-ST-SP-0005) |  |
|  | Loads and center mass | The static & dynamic loads of the equipment shall be presented at the foundation level. The elevation and location of the equipment center of mass shall be determined. | CIVIL IS NOT IN THE VENDOR’S SCOPE OF WORK | The static & dynamic loads of the equipment shall be presented at the foundation level. The elevation and location of the equipment center of mass shall be determined. |  |
|  | Foot print | The detail of base plates and arrangement of them shall be provided in a separate document. | CIVIL IS NOT IN THE VENDOR’S SCOPE OF WORK | The detail of base plates and arrangement of them shall be provided in a separate document. |  |
| SAFETY |  |  |  |  |  |
|  | Reference | API 521 and API 537 shall be added in standard section. | CONFIRM | Noted and closed. |  |
|  | Area Classification | Bidder shall check and confirm hazardous area of the equipment and also all requirement for this matter shall be considered and mentioned in offer and also hazardous area classification layout for ignition package to be issued for ignition package. Project hazardous area shall be followed and also for package, vendor shall issue hazardous area and source list. | CONFIRM | Noted and closed. |  |
|  | Radiation calculation | Bidder shall check and confirm radiation calculation. Bidder shall ensure and guaranty the height of stack meet all requirement of project specification and standard. | CONFIRM | Noted and closed. |  |
|  | Project specification | Study for radiation, gas dispersion and noise, shall be submitted for client approval base on project specification, standard & limitation on plot plan. | CONFIRM | Noted and closed. |  |
|  | Mach number | Specify Mach number. PLEASE FOLLOW IPS-E-PR-460 | CONFIRM | Noted and closed. |  |
|  | Wind Speed | Maximum wind speed for Binak is 120_ Km/hr. | CONFIRM | Noted and closed. |  |
|  | Flare stack | Final Minimum flare stack height will be specified later and to be checked and confirmed by Bidder. | CONFIRM | Noted and closed. |  |
|  | Solar radiation | Solar radiation and dispersion shall be considered in calculation. | CONFIRM | Noted and closed. |  |
|  | Emergency Noise Level | Flare Noise -max noise level at base of stack during emergency conditions: 115dB. | CONFIRM | Noted and closed. |  |
|  | Operating Noise Level | Flare Noise -max noise level at perimeter of restricted (sterile) area during normal operation: 85dB. | CONFIRM | Noted and closed. |  |
| PIPING AND MATERIAL |  |  |  |  |  |
|  | Material | Tip Material shall be SS310. | CONFIRM | Noted and closed. |  |
|  | Material | Material of Purge Gas Line shall be SS310 for upper section of Flare tip. | CONFIRM | Noted and closed. |  |
|  | Ignition Pipe Material | Ignition line shall be SS304 up to Flare Tip. SS310 shall be used for above than flare tip. | CONFIRM | Noted and closed. |  |
|  | Corrosion Allowance | Corrosion allowance of Flare Gas and Fuel gas shall be 6mm same as Flare Entrance. | CONFIRM | Noted and closed. |  |
|  | NACE Requirement | Requirement of NACE MR0175/ISO 15156 shall be met for wetted parts. | CONFIRM | In this regard “SPECIFICATION FOR MATERIAL REQUIREMENTS IN SOUR SERVICE” document No.: BK-GNRAL-PEDCO-000-PI-SP-0008 shall also be met. (A516 and A105 shall be normalized and HIC is required for plates and welded pipes and where required in this spec). |  |
| QC |  |  |  |  |  |
|  | Normalized | Material shall be normalized and meet requirement of NACE MR0175/ISO15156. | CONFIRM | Noted and closed. |  |
|  | PWHT | PWHT is required for NACE items. | CONFIRM | Noted and closed. |  |
|  | Corrosion allowance | Corrosion allowance shall be in accordance with latest data sheet. | CONFIRM | Noted and closed. |  |
|  | ITP | ITP Shall be submitted according to Procedure No. ICE-EID-MI-SP01-Rev01 & API 537-673 Requirement | CONFIRM | Noted and closed. |  |
|  | ITP | ITP Will be finalized in PIM & KOM | CONFIRM | Noted and closed. |  |
|  | INSPECTION | Inspection Shall be according to API 537 Paragraph 5.6 | CONFIRM | Noted and closed. |  |
|  | AIRCRAFT | Aircraft Warning Lighting shall be according to API 537 Paragraph 5.9 | CONFIRM | Noted and closed. |  |
|  | PAINTING | Painting shall be in accordance with “Specification for Painting”BK-GNRAL-PEDCO-000-PI-SP-0006” & API 537 Paragraph 5.7 | CONFIRM | Noted and closed. |  |
|  | NOISE CONTROL | IPS-G-SF-900 (General Standard for Noise Control and Vibration) shall be added in standard section. | CONFIRM | Noted and closed. |  |
|  | GUARANTEE | Vendor shall guarantee the all flares are smokeless. | CONFIRM | Noted and closed. |  |
|  | CABLING | The cables separation (instrument and power) shall be followed according to IPS-EN-IN-190. Please send your deviations if any. | CONFIRM | Noted and closed. |  |
|  | DOCUMENTATION | All attached documents of MR shall be read, signed and stamped by Bidder. | CONFIRM | Noted and closed. |  |
|  | DOCUMENTATION | TBE shall be filled, signed and stamped by Bidder complete | CONFIRM | Noted and closed. |  |
|  | SUB-BIDDER | All sub-Bidder lists shall be of Approved Bidder List (AVL) of MOP. | CONFIRM | Noted and closed. |  |
|  | RESPONSIBILITY | Bidder is fully responsible for proposal information compatibility with MR and Attachment Documents | CONFIRM | Noted and closed. |  |
|  | DEVIATION | Any alteration/deviation in the offer or part of it which has consultant approval shall be sufficiently highlighted and notified by bidder, Consultant reserve the right to ask for former or later offer to be supplied by bidder after purchase order. | CONFIRM | Noted and closed. |  |
|  | ITP | The technical proposal of the vineyard company is very incomplete, for example, it does not have ITP. | noted | Noted and closed. |  |