## Cover
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
TBE FOR FLARE PACKAGES
شماره پیمان: |  |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 9
9184 – 073 - 053 |  |  |  | BK |  | GCS | PEDCO | 120 |  | ME | TB | 0012 | D00
طرح نگهداشت و افزایش تولید 27 مخزن
TBE FOR FLARE PACKAGE نگهداشت و افزایش تولید میدان نفتی بینک
D00 |  |  | NOV.2023 |  | IFI |  |  |  | H.Ghadyani |  |  | M.Fakharian |  | S.Faramarzpour
Rev. |  |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
Class: 2 | 3 |  |  |  | CLIENT Doc. Number: |  |  |  | F0Z-709238
status: |  | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved

## REVISION
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
TBE FOR FLARE PACKAGES
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 1 از 9
9184 – 073 - 053 |  |  | BK | GCS |  | PEDCO | 120 | ME | TB | 0012 |  | D00
REVISION RECORD SHEET
Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D01 |  | D02 | D03 | D04
1 | X | [7 empty] | 65
2 | X | [7 empty] | 66
3 | X | [7 empty] | 67
4 | X | [7 empty] | 68
5 | X | [7 empty] | 69
6 | X | [7 empty] | 70
7 | X | [7 empty] | 71
8 | X | [7 empty] | 72
9 | X | [7 empty] | 73
10 | [8 empty] | 74
11 | [8 empty] | 75
12 | [8 empty] | 76
13 | [8 empty] | 77
14 | [8 empty] | 78
15 | [8 empty] | 79
16 | [8 empty] | 80
17 | [8 empty] | 81
18 | [8 empty] | 82
19 | [8 empty] | 83
20 | [8 empty] | 84
21 | [8 empty] | 85
22 | [8 empty] | 86
23 | [8 empty] | 87
24 | [8 empty] | 88
25 | [8 empty] | 89
26 | [8 empty] | 90
27 | [8 empty] | 91
28 | [8 empty] | 92
29 | [8 empty] | 93
30 | [8 empty] | 94
31 | [8 empty] | 95
32 | [8 empty] | 96
33 | [8 empty] | 97
34 | [8 empty] | 98
35 | [8 empty] | 99
36 | [8 empty] | 100
37 | [8 empty] | 101
38 | [8 empty] | 102
39 | [8 empty] | 103
40 | [8 empty] | 104
41 | [8 empty] | 105
42 | [8 empty] | 106
43 | [8 empty] | 107
44 | [8 empty] | 108
45 | [8 empty] | 109
46 | [8 empty] | 110
47 | [8 empty] | 111
48 | [8 empty] | 112
49 | [8 empty] | 113
50 | [8 empty] | 114
51 | [8 empty] | 115
52 | [8 empty] | 116
53 | [8 empty] | 117
54 | [8 empty] | 118
55 | [8 empty] | 119
56 | [8 empty] | 120
57 | [8 empty] | 121
58 | [8 empty] | 122
59 | [8 empty] | 123
60 | [8 empty] | 124
61 | [8 empty] | 125
62 | [8 empty] | 126
63 | [8 empty] | 127
64 | [8 empty] | 128

## FST-2201, IG-2201
NISOC |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
TBE FOR GAS FLARE PACKAGES
|  | پروژه | بسته کاری |  | صادرکننده |  | تسهیلات | رشته | نوع مدرک |  | سریال |  | نسخه
شماره پیمان: |  | BK | GCS |  | PEDCO |  | 120 | ME | TB |  | 0012 |  | D00 | شماره صفحه: 3 از 9
053 – 073 - 9184
REQ. NAME: Material Requisition for Flare packages | [5 empty] | BIDDER: |  |  |  | "A" |  |  | "B" |  | "C" |  | "D"
REF. REQ. NO. : BK-GCS-PEDCO-120-ME-MR-0012 | [5 empty] | NAME: |  |  |  | Machin Foulad Jonoub |  |  | Masnouat Felezi Sangin |  | Takestan |  | Tehranjavan
EQUIPMENT TYPE: Flare packages | [5 empty] | QUOTATION NO.: |  |  |  | T-02-255-TB-FB-FL-GEN-005 |  |  | 1402/03-MFS-TC01-BHE-1362 |  | Q1402-03 |  | TJFG/TO/485
NO OF ITEMS INCLUDED IN REQUISITION: FST-2201, IG-2201 | [5 empty] | QUOTATION DATE: |  |  |  | 23.SEP.2023 |  |  | 22.OCT.2023 |  | 20, Aug.2023 |  | 13.NOV.2023
NO. | DESCRIPTION |  |  | UNITS |  | TECHNICAL REQUIREMENTS |  |  |  | MEETS TECHNICAL REQUIREMENT
[10 empty] | DESCRIPTION |  | STATUS | DESCRIPTION | STATUS | DESCRIPTION | STATUS | DESCRIPTION | STATUS
1. GENERAL
1.1 | Scope of Supply and Work |  |  | NO. | NO. | Material Requisition |  |  |  | ok |  | N | Noted & Confirmed. | Y | Confirm | Y | Confirm | Y
1.2 | Codes and Standards |  |  | - |  | Material Requisition |  |  |  | ok |  | N | Noted & Confirmed. | Y | Confirm | Y | Confirm | Y
1.3 | Reference List |  |  | - |  | to be Supplied by Bidder |  |  |  | ok |  | N | Please find it as attached. | Y | Confirm | Y | Please find in part K of technical offer | Y
1.4 | Quality Assurance and Relevant Certificates |  |  | - |  | to be Supplied by Bidder |  |  |  | ok |  | N | Please find it as attached. | Y | Confirm | Y | Please find in part J of technical offer | Y
1.5 | Any Deviation List From MR and Its Attachments. |  |  | - |  | Material Requisition |  |  |  | ok |  | N | Please find it as attached. | Y | Confirm | N | As per attached | Y
1.6 | Warrant the engineering, materials and workmanship of the Package. |  |  | - |  | The guarantee period shall be eighteen (18) months from the date of delivery or twelve (12) months from the installation date of each equipment/packages at site. |  |  |  | Confirm |  | Y | Noted & Confirmed. | Y | Confirm | Y | Confirm | Y
1.7 | Design Life |  |  | - |  | 20 Years |  |  |  | Confirm |  | N | Noted & Confirmed. | Y | Confirm | Y | 20 Years | Y
1.8 | Vendor shall Guarantee the dispersion study for flaring gas composition |  |  | - |  | to be defined and guaranteed by Bidder |  |  |  | Confirm |  | N | Dispersion analysis will send after PO but dispersion guarantee is not in scope of MFS. | N | Confirm | Y | Confirm | Y
1.9 | Delivery Time and Time Schedule |  |  | - |  | to be Dfined by Bidder |  |  |  | see proposal |  | Y | Please find it as attached. | Y | Confirm | Y | Please find in parts M and N of technical offer | Y
1.10 | Delivery Condition and Place |  |  | - |  | to be Dfined by Bidder |  |  |  | Confirm |  | Y | EXW - MFS Shop | Y | Confirm | Y | Ex-work | Y
1.11 | Erection , Commissioning and 2 Years Spare |  |  | - |  | AS per Project specification NO. E&C-QC-SP-1 |  |  |  | Confirm |  | Y | Noted & Confirmed. | Y | Confirm | Y | Confirm | Y
1.12 | Performance Guarantee Based on Duty Specification and Mechanical Specification |  |  | - |  | Duty Specification and Mechanical Specification |  |  |  | Confirm |  | Y | Noted & Confirmed. | Y | Confirm | Y | Confirm | Y
2. MECHANIC
2.1 | Stack Support |  |  | - |  | To be Defined By Bidder |  |  |  | GUYED |  | Y | Guy Wire | Y | GUY WIRE | Y | Guy Wire | Y
2.2 | Stack Height (Iinclude Tip Height) |  |  | m |  | 22.5(Vendor to be verified) |  |  |  | Confirm |  | Y | 22.5 | Y | 15 M ACCORDING TO CALCULATIONS | Y | 22.2 | Y
2.3 | Stack Size(Diameter) |  |  | inch |  | 12" |  |  |  | Confirm |  | Y | 16" | Y | 12'' | Y | 12" | Y
2.4 | Flare Stack Material(as minimum) |  |  | - |  | C.S.+3mm(VTA) |  |  |  | Confirm |  | Y | Noted & Confirmed. | Y | C.S. +3mm | Y | API 5L Gr. B or Equal | Y
2.5 | Flare Tip Length |  |  | m |  | 3 |  |  |  | 3 m |  | Y | 3 | Y | 3 M | Y | 3.16 | Y
2.6 | Flare Tip Size |  |  | inch |  | 12" |  |  |  | Confirm |  | Y | 12" | Y | 12'' | Y | 12" | Y
2.7 | Flare Tip Material |  |  | - |  | S.S.310(VTC) |  |  |  | Confirm |  | Y | Noted & Confirmed. | Y | S.S.310 | Y | S.S.310 | Y
2.8 | Number of Pilot |  |  | - |  | Min. 3 Pilot |  |  |  | Confirm |  | Y | 3 | Y | CONFIRM | Y | 3 | Y
2.9 | Pilot Material |  |  | - |  | S.S.304(VTC) |  |  |  | Confirm |  | Y | Noted & Confirmed. | Y | S.S.304 | Y | S.S.310 | Y
2.10 | Ignition Type and System |  |  | - |  | High Energy Generator |  |  |  | Confirm |  | Y | Noted & Confirmed. | Y | CONFIRM | Y | High Energy Generator | Y
2.11 | Flare Burner Internal Lining |  |  | - |  | To be Defined By Bidder |  |  |  | Confirm |  | N | Not Applicable. | N | 2'' | Y | Not Applicable | Y
2.12 | Flare Gas Seal Type |  |  | - |  | Dynamic seal |  |  |  | Confirm |  | N | Noted & Confirmed. | Y | CONFIRM | Y | Dynamic seal | Y
2.13 | Flare Gas Seal Material |  |  | - |  | To be Defined By Bidder |  |  |  | Confirm |  | N | SS 304 | Y | stainless steel | Y | S.S.310 | Y
2.14 | Distance Between Ignition Panel and Pilot Burners |  |  | m |  | 100 m |  |  |  | Confirm |  | N | Noted & Confirmed. | Y | CONFIRM | Y | 100 m | Y
2.15 | Corrosion allowance |  |  | mm |  | CS pressure part: 3.2 mm No Corrosion allowance for SS Corrosion allowance of Flare Gas and Fuel gas shall be 6mm same as Flare Entrance |  |  |  | Confirm |  | Y | Noted & Confirmed. | Y | CONFIRM | Y | Confirm | Y
2.16 | Design Life for flare Tip |  |  | years |  | 25 years |  |  |  | Confirm |  | N | Noted & Confirmed. | Y | CONFIRM | Y | 25 years | Y
3. PROCESS
3.1 | F Factor Method |  |  | - |  | High Efficiency Method |  |  |  | Confirm |  | N | Generic Pipe | N | Generic Pipe | Y | User Specified | Y
3.2 | Transmissivity Factor |  |  | - |  | To be Defined By Bidder |  |  |  | Confirm |  | N | Wayne | Y | Calculated Min Value 1.000 Max Value 1.000 | Y | User Specified | Y
3.3 | Heat Release |  |  | - |  | To be Defined By Bidder |  |  |  | Confirm |  | N | 397271 kW | Y | 345416.3 Kw | Y | 397271 | Y
3.4 | Noise Level at Normal and Emergency Condition |  |  | dB |  | 85 / 115 |  |  |  | Confirm |  | Y | Noted & Confirmed. | Y | CONFIRM | Y | 77.73 (for 15% emergency flowrate @ 40 m from stack base) | Y
3.5 | Solar Radiation |  |  | kw/m2 |  | 1.01 |  |  |  | Confirm |  | N | 1.010 kW/m2 | Y | CONFIRM | Y | 1.01 | Y
3.6 | Wind Velocity for Radiation Calculations |  |  | m/s |  | 10 |  |  |  | Confirm |  | N | 10 m/s | Y | CONFIRM | Y | 10 | Y
3.7 | Allowable Pressure Drop |  |  | - |  | To be Defined By Bidder |  |  |  | Confirm |  | N | 0.1 bar | Y | Tip Pressure Drop 0.015 bar Tip Total Pressure Drop 0.013 bar Seal Pressure Drop 0.000 bar Seal Total Pressure Drop 0.000 bar Stack Pressure Drop 0.056 bar Stack Total Pressure Drop 0.051 bar | Y | 0.1 | Y
3.8 | Mach Number |  |  | - |  | 0.5 |  |  |  | Confirm |  | Y | 0.4122 | Y | Confirm | Y | 0.2642 | Y
3.9 | Design Temperature |  |  | - |  | As Per BK-GNRAL-PEDCO-000-PR-DC-0001 |  |  |  | Confirm |  | N | 297 C | Y | Confirm | Y | 297 | Y
3.1 | Design Pressure |  |  | bar(g) |  | 3.5 |  |  |  | Confirm |  | N | 3.5 barg | Y | Confirm | Y | 3.5 | Y
3.11 | Flow Rate |  |  | - |  | As Per BK-GCS-PEDCO-120-PR-RT-0002 |  |  |  | Confirm |  | N | 39824 kg/h | Y | Confirm | Y | 39824 | Y
3.12 | Smokeless Capacity |  |  | kg/hr |  | 9944 |  |  |  | Confirm |  | N | 25% | Y | Confirm | Y | 9844 | Y
3.13 | Flare GasTemperature |  |  | - |  | As Per BK-GCS-PEDCO-120-PR-RT-0002 BK-GCS-PEDCO-120-PR-SP-0003 |  |  |  | Confirm |  | N | 272 C | Y | Confirm | Y | 272 | Y
3.14 | Pilot Gas Flow Rate |  |  | Nm3/h |  | To be Defined By Bidder |  |  |  | Confirm |  | N | 7.5 Nm3/h | Y | - | N | 1.74×3=5.22 | Y
3.15 | Pilot Gas Pressure |  |  | - |  | To be Defined By Bidder |  |  |  | Confirm |  | N | 1.1 | Y | 1.1 Barg | Y | 1 | Y
3.16 | Pilot Gas Temperature |  |  | - |  | To be Defined By Bidder |  |  |  | Confirm |  | N | 36 | Y | 57 C | Y | 48 | Y
3.17 | Utility Consumptions: Fuel Gas LPG Instrument Air Nitrogen Power Steam |  |  | - |  | To be Defined By Bidder |  |  |  | Confirm |  | Y | please refer to our revised T.P, T.D. section 7 | N | Fuel Gas LPG Instrument Air Nitrogen Power Steam | Y | please refer to our revised T.P, T.D. section 7
3.18 | Air flow for Smokeless |  |  | kg/hr |  | Yes/ 9444 |  |  |  | Confirm |  | Y | 24019 kg/h | N | 3900 m3/hr | N | 24000 | Y
3.19 | Air pressure for Smokeless |  |  | PSI |  | To be Defined By Bidder |  |  |  | Confirm |  | N | Atmospheric | Y | - |  | 10 | Y
3.20 | Smokeless criteria |  |  | - |  | As Per BK-GCS-PEDCO-120-PR-RT-0002 BK-GCS-PEDCO-120-PR-SP-0003 |  |  |  | Confirm |  | Y | 25% smokless with air | Y | Confirm | Y | Ringelmann 1 | Y
3.21 | Maximum radiant intensities at ground level for cumulated flowrate |  |  | Kw/m² |  | AS PER BK-GCS-PEDCO-120-PR-RT-0024_D04 |  |  |  | Confirm |  | Y | Confirm | Y | Confirm | Y | 7.055 @ 10 m from stack base | Y
3.22 | Maximum radiant intensities at ground leve |  |  | Kw/m² |  | AS PER BK-GCS-PEDCO-120-PR-RT-0024_D04 |  |  |  | Confirm |  | N | Confirm | Y | Confirm | Y | 7.055 @ 10 m from stack base | Y
3.23 | Radius of sterile area from stack based on 4.73 Kw/m² radiation intensity. |  |  | m |  | AS PER BK-GCS-PEDCO-120-PR-RT-0024_D04 |  |  |  | Confirm |  | Y | 4.73 | Y | Confirm | Y | 40 | Y
3.24 | Flare Monitoring |  |  |  |  | Yes |  |  |  | Confirm |  | Y | Noted & Confirmed. Via Thermocouple. | Y | Confirm | Y | By Client | N
3.25 | Flare Restricted area affected zone by toxic gas dispersion (m) |  |  | m |  | Not Reached |  |  |  | Confirm |  | Y | Dispersion analysis will send after PO | Y | Confirm | Y | Not Reached | Y
3.26 | Gas Back Up (LPG Bottle for Pilot) |  |  | Hr |  | 24 |  |  |  | Confirm |  | Y | Noted & Confirmed. | Y | Confirm | Y | 12 | N
3.27 | Automatic Re-Ignation System |  |  | - |  | Yes |  |  |  | Confirm |  | Y | Noted & Confirmed. | Y | Confirm | Y | Yes | Y
3.28 | Internal Combustion Detector |  |  | - |  | Yes |  |  |  | Confirm |  | Y | Noted & Confirmed. Please refer to our revised P&ID | Y | Confirm | Y | Not Applicable | Y
4. Electrical Requirements
4.1 | Design electrical specification as per JOB SPECIFICATION FOR DESIGN ELECTRICAL INSTALLATION IN PACKAGES. |  |  | - |  | BK-GNRAL-PEDCO-000-EL-DC-0001 |  |  |  | Confirm |  | Y | Noted & Confirmed. | Y | Confirm | Y | Confirm | Y
4.2 | Design and supply of ACWL Local control panel and distribution board shall be in accordance withAnnex 14 of ICAO; JOB SPECIFICATION FOR SUPPLY DISTRIBUTION PANELS. |  |  | - |  | According to Annex 14 of ICAO (Manufacture Standard) |  |  |  | Confirm |  | Y | We don’t have Air Craft Warning Lighting, Because the flare stack is less than 30 meters. | Y | Confirm | Y | Confirm | Y
4.3 | Electrical voltage and phase |  |  | - |  | 400/230 V ±5 %, 50 Hz ±2 %, |  |  |  | Confirm |  | Y | Noted & Confirmed. | Y | Confirm | Y | Confirm | Y
4.4 | Degree of protection |  |  | - |  | Motor: IP 54 Terminal Box of Motor: IP 55 LCS/LCP: IP 65 |  |  |  | Confirm |  | Y | Noted & Confirmed. | Y | Confirm | Y | Confirm | Y
4.5 | Hazardous Area Classification |  |  | - |  | Safe Area |  |  |  | Confirm |  | Y | Noted & Confirmed. | Y | Confirm | Y | Fuel gas entering the ignition panel makes it a hazardous area. | Y
4.8 | Air Blower Power Rated & Quantity |  |  | KW/ No |  | to be Dfined by Bidder |  |  |  | Confirm |  | Y | 29KW/1QTY | Y | Confirm | Y | 30 / 1 | Y
4.9 | Air Blower VFD Quntity |  |  | - |  | if Required |  |  |  | Confirm |  | Y | No Required | Y | 1 | Y | Flow rate control by inlet guide vane damper | Y
4.10 | Electrical specification of VFD |  |  | - |  | if Required |  |  |  | Confirm |  | Y | No Required | Y | - | Y | Not Applicable | Y
4.11 | VFD Manufacturer |  |  | - |  | if Required |  |  |  | Confirm |  | Y | Not Applicable. | Y | - | Y | Not Applicable | Y
5. Instrument
5.1 | Remote control for flare ignition |  |  | - |  | Required as per Project P&ID |  |  |  | Confirm |  | Y | Noted & Confirmed. | Y | Confirm | Y | Confirm | Y
5.2 | control system type |  |  | - |  | TYPE A as per project Spec. BK-GNRAL-PEDCO-000-IN-SP-0004 |  |  |  | Confirm |  | Y | Noted & Confirmed. | Y | Confirm | Y | Confirm | Y
5.3 | Temprature indicators on ignition panels |  |  | - |  | Required as per Project P&ID |  |  |  | Confirm |  | Y | Noted & Confirmed. | Y | Confirm | Y | Not Required | N
5.4 | K type thermocouples dual type for each pilots |  |  | - |  | Required as per Project P&ID |  |  |  | Confirm |  | Y | Noted & Confirmed. | Y | Confirm | Y | Confirm | Y
5.5 | Number of thermocouple |  |  | - |  | 3 Nos. |  |  |  | Confirm |  | Y | Noted & Confirmed. | Y | Confirm | Y | 3 NO. | Y
5.6 | Area Clasification/IP rating |  |  | - |  | Zone 2 / IP65 |  |  |  | Confirm |  | Y | Noted & Confirmed. | Y | Confirm | Y | Confirm | Y
5.7 | Explosive Proof Grade |  |  | - |  | EEx requirments |  |  |  | Confirm |  | Y | Noted & Confirmed. | Y | Confirm | Y | Exde | Y
5.8 | Thermocouple cable ( from flare tip to IGP, Estimated length 250) |  |  | - |  | Required as per Project P&ID |  |  |  | Confirm |  | Y | Noted & Confirmed. | Y | Confirm | Y | Confirm | Y
5.9 | Flame detector for pilots |  |  | - |  | Required as per Project P&ID |  |  |  | Confirm |  | Y | Noted & Confirmed. Via Thermocouple. | Y | Confirm | Y | Thermocouple | Y
5.10 | Pilot status indication on ignition panel |  |  | - |  | Required as per Project P&ID |  |  |  | Confirm |  | Y | Noted & Confirmed. | Y | Confirm | Y | Confirm | Y
5.11 | on/off push button for pilots on ignition panel |  |  | - |  | Required as per Project P&ID |  |  |  | Confirm |  | Y | Noted & Confirmed. | Y | Confirm | Y | Confirm | Y
5.12 | All instrumentation, tube& fitting , Jb, Cable , earthing,… inside package skid |  |  | - |  | Required as per Project documents |  |  |  | Confirm |  | Y | Noted & Confirmed. | Y | Confirm | Y | Confirm | Y
5.13 | Spare part |  |  | - |  | Required as per Project PMR |  |  |  | Confirm |  | Y | Noted & Confirmed. Please refer to Art. 5 of our T.P. | Y | Confirm | Y | Confirm | Y
5.14 | Special tools |  |  | - |  | Required as per Project PMR |  |  |  | Confirm |  | Y | Not Applicable. | Y | Confirm | Y | Not Applicable | Y
5.15 | documentation |  |  | - |  | Required as per Project PMR |  |  |  | Confirm |  | Y | Noted & Confirmed. | Y | Confirm | Y | Confirm | Y
5.16 | Test and inspection |  |  | - |  | Required as per Project PMR |  |  |  | Confirm |  | Y | Noted & Confirmed. | Y | Confirm | Y | Confirm | Y
6. Piping Requirements
6.1 | Design Code |  |  | - |  | ASME B31.3 |  |  |  | Confirm |  | Y | Noted & Confirmed. | Y | Confirm | Y | Confirm | Y
6.2 | Tie in Points |  |  | - |  | to be Dfined by Bidder |  |  |  | Confirm |  | Y | Noted & Confirmed. | Y | ACC to P&ID | Y | As per submitted PID | Y
6.3 | Piping Material: |  |  | - |  | AS PER BK-GCS-PEDCO-120-PI-SP-0001_D02 |  |  |  | Confirm |  | Y | Noted & Confirmed. | Y | Confirm | Y | Confirm | Y
6.4 | Painting Equipment |  |  | - |  | AS PER BK-GNRAL-PEDCO-000-PI-SP-0006_D04 |  |  |  | Confirm |  | Y | Noted & Confirmed. | Y | Confirm | Y | Confirm | Y
6.5 | Stress Analysis Calculation |  |  | * |  | CAESAR II |  |  |  | Confirm |  | Y | Noted & Confirmed. Only for our B.L. | Y | Confirm | Y | Confirm | Y
6.6 | 3D Model of Whole Package in PDMS Format |  |  | - |  | PDMS 12.1 |  |  |  | Confirm |  | Y | Noted & Confirmed. Only for our B.L. | Y | Confirm | Y | STEP file will be submitted | Y
6.7 | Pipe and piping specification |  |  | - |  | PIPING MATERIAL SPECIFICATION |  |  |  | Confirm |  | Y | Noted & Confirmed. | Y | Confirm | Y | Confirm | Y
7. Structure
7.1 | Foundation load at base plate and gravity center location and anchor bolt arrangement shall be provided by Vendor. |  |  |  |  | Required |  |  |  | Confirm |  | Y | Noted & Confirmed. | Y | Confirm | Y | Confirm | Y
7.2 | Structural Steel Material is (ISIRI 14262-2 (S235JR). |  |  |  |  | According to ISIRI 14262-2 (S235JR) |  |  |  | Confirm |  | Y | Noted & Confirmed. | Y | Confirm | Y | Confirm | Y
7.3 | Structural bolts material is (Bolt Class 8.8 Grade B acc. to ISIRI 2874-1 Galvanized. Nut Class 8 Style 2 Grade B acc. to ISIRI 5654 and ISIRI 9737 Galvanized Washer 200 HV acc. to ISIRI 9742 Galvanized shall be considered for all bolts. |  |  |  |  | According to ISIRI 2874-1 , ISIRI 5654 and ISIRI 9737 , ISIRI 9742 |  |  |  | Confirm |  | Y | ST-37 | Y | Confirm | Y | Confirm | Y
7.4 | Loading and design of structure shall be done according to structurral design criteria "BK-GNRAL-PEDCO-000-ST-DC-0001". |  |  |  |  | According to "BK-GNRAL-PEDCO-000-ST-DC-0001". |  |  |  | Confirm |  | Y | A 325 | Y | Confirm | Y | Confirm | Y
7.5 | Canopy for motors which are exposed to sun light shall be considered |  |  |  |  | Required |  |  |  | Confirm |  | Y | Noted & Confirmed. | Y | Confirm | Y | Confirm | Y
7.6 | For all structural parts ASCE7-5 and AISC loading and design requirements shall be considered more than codes specified in datasheets. |  |  |  |  | Required |  |  |  | Confirm |  | Y | Noted . H.D.G will be used. | Y | Confirm | Y | Confirm | Y
8. SPARE PARTS
8.1 | Spare parts for pre commissioning and commissioning |  |  | - |  | As per E&C-QC-SP-1 |  |  |  | Confirm |  | Y | Noted & Confirmed. | Y | Confirm | Y | Confirm | Y
8.2 | Spare parts list for two (2) years operation {Option} |  |  | - |  | As per E&C-QC-SP-1 |  |  |  | Confirm |  | Y | Noted & Confirmed. | Y | Confirm | Y | Confirm | Y
8.3 | Capital spare parts {Option} |  |  | - |  | Bidder To Specify |  |  |  | Confirm |  | N | Not Applicable. | Y | Not Required | Y | Confirm | Y
9. EXCEPTION & DEVIATION
9.1 | Filled in and signed off deviation form |  |  | - |  | Y / N / N.A. |  |  |  | Confirm |  | N | Noted & Confirmed. | Y | Confirm | N | Confirm | Y
10. DELIVERY AND SHIPMENT
10.1 | Delivery term |  |  | - |  | Bidder To Specify |  |  |  | Confirm |  | A | EXW | Y | 6 Months and delivered form the factory | N | Ex-work | Y
10.2 | Delivery time |  |  | - |  | Bidder To Specify |  |  |  | Confirm |  | A | 12 months after receiving down payment and approving fabrication drawings | Y | 6 months | N | 9 months | Y
| FINAL CONCLUSION | [8 empty] | ACCEPTED |  |  | ACCEPTED |  | ACCEPTED |  | ACCEPTED
Notes: 1) ABBREVIATIONS: Y: ACCEPTED By Bidder, N: NOT ACCEPTED By Bidder, N.A.: NOT APPLICABLE