## Cover
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
I/O LIST FOR F&G SYSTEMS
شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 16
9184 – 073 - 053 |  |  | BK |  | GCS | PEDCO | 120 |  | IN | LI | 0004 | D03
طرح نگهداشت و افزایش تولید 27 مخزن
I/O LIST FOR F&G SYSTEMS نگهداشت و افزایش تولید میدان نفتی بینک
D03 |  | NOV.2022 |  | AFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | S.Faramarzpour
D02 |  | OCT.2022 |  | IFA |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
D01 |  | MAY.2022 |  | IFA |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
D00 |  | FEB.2022 |  | IFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
Class: 1 |  |  |  | CLIENT Doc. Number:F0Z-708970
status: | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved

## REVISION
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
I/O LIST FOR F&G SYSTEMS
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 16
9184 – 073 - 053 |  |  | BK | GCS |  | PEDCO | 120 | IN | LI | 0004 |  | D03
REVISION RECORD SHEET
Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D01 |  | D02 | D03 | D04
1 | X | X | X |  | X |  |  |  | 65
2 | X | X | X |  | X |  |  |  | 66
3 | X | X | [6 empty] | 67
4 | X | X | X |  | X |  |  |  | 68
5 | X | X | X |  | X |  |  |  | 69
6 | X | X | X |  | X |  |  |  | 70
7 | X | X | X |  | X |  |  |  | 71
8 | X | X | X |  | X |  |  |  | 72
9 |  | X | X |  | X |  |  |  | 73
10 |  | X | X |  | X |  |  |  | 74
11 |  | X | X |  | X |  |  |  | 75
12 |  | X | X |  | X |  |  |  | 76
13 |  | X | X |  | X |  |  |  | 77
14 |  | X | X |  | X |  |  |  | 78
15 |  |  | X |  | X |  |  |  | 79
16 |  |  | X |  | X |  |  |  | 80
17 |  |  | X |  | X |  |  |  | 81
18 |  |  | X |  | X |  |  |  | 82
19 | [8 empty] | 83
20 | [8 empty] | 84
21 | [8 empty] | 85
22 | [8 empty] | 86
23 | [8 empty] | 87
24 | [8 empty] | 88
25 | [8 empty] | 89
26 | [8 empty] | 90
27 | [8 empty] | 91
28 | [8 empty] | 92
29 | [8 empty] | 93
30 | [8 empty] | 94
31 | [8 empty] | 95
32 | [8 empty] | 96
33 | [8 empty] | 97
34 | [8 empty] | 98
35 | [8 empty] | 99
36 | [8 empty] | 100
37 | [8 empty] | 101
38 | [8 empty] | 102
39 | [8 empty] | 103
40 | [8 empty] | 104
41 | [8 empty] | 105
42 | [8 empty] | 106
43 | [8 empty] | 107
44 | [8 empty] | 108
45 | [8 empty] | 109
46 | [8 empty] | 110
47 | [8 empty] | 111
48 | [8 empty] | 112
49 | [8 empty] | 113
50 | [8 empty] | 114
51 | [8 empty] | 115
52 | [8 empty] | 116
53 | [8 empty] | 117
54 | [8 empty] | 118
55 | [8 empty] | 119
56 | [8 empty] | 120
57 | [8 empty] | 121
58 | [8 empty] | 122
59 | [8 empty] | 123
60 | [8 empty] | 124
61 | [8 empty] | 125
62 | [8 empty] | 126
63 | [8 empty] | 127
64 | [8 empty] | 128

## NOTE
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
I/O LIST FOR F&G SYSTEMS
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 3 از 16
9184 – 073 - 053 |  |  |  | BK | GCS | PEDCO | 120 | IN | LI | 0004 | D03
REFERENCES(NOTE 2):
|  | F&G LOCATION LAYOUT FOR PROCESS Area | [7 empty] | BK-GCS-PEDCO-120-IN-PY-0005
|  | F&G LOCATION LAYOUT FOR BUILDINGS | [7 empty] | BK-GCS-PEDCO-120-IN-PY-0006
|  | DATA SHEET FOR MATRIX PANEL | [7 empty] | BK-GCS-PEDCO-120-IN-DT-0017
|  | ESD LEVEL HIERARCHY | [7 empty] | BK-GCS-PEDCO-120-IN-DG-0003
|  | FIRE & GAS DETECTION DESIGN CRITERIA | [7 empty] | BK-GCS-PEDCO-120-IN-DC-0001
GENERAL NOTE
|  | 1 | ALL LISTED FACP'S SIGNALS SHALL BE MONITORED IN F&G SYSTEM BY MODBUS CONNECTION.
|  | 2 | REFER TO LATEST VERSION OF REFERENCE DOCUMENTS.
|  | 3 | ALL RELAYS & I.S. BARRIERS INSTALLED IN F&G PANEL SHALL BE SIL CERTIFIED. ALL RELAYS SHALL BE LINE-MONITORED
|  | 4 | GALVANIC ISOLATION BARRIER SHALL BE CONSIDERED FOR INTRINSICALLY SAFE (EEXia) LOOPS.
|  | 5 | I/O CARDS & ACCESSORIES SHALL BE SELECTED IN ACCORDANCE WITH '' SPECIFICATION FOR CONTROL SYSTEM".
Class: 1

## SUMMARY
NISOC | [5 empty] | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
I/O LIST FOR F&G SYSTEMS
شماره پیمان: | [5 empty] | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 4 از 16
9184 – 073 - 053 | [5 empty] | BK | GCS |  | PEDCO | 120 | IN | LI | 0004 | D03
F&G I/O SUMMERY COUNT
| ITEM |  | I/O TYPE |  | IS/NIS | R/NR |  | DESCRIPTION | [6 empty] | QTY OF SIGNALS |  | QTY (+20% SPARE) | REMARKS
| 1 |  | AI-IS-R |  | IS | R |  | ANALOGUE INPUT HARDWARE SIGNAL (INTRINSICALLY SAFE, REDUNDANT) | [6 empty] | 87 |  | 104 | NOTES 4,5 | 104.4
| 2 |  | DI-NIS-R |  | NIS | R |  | DIGITAL INPUT HARDWARE SIGNAL (NON INTRINSICALLY SAFE, NON-REDUNDANT) | [6 empty] | 60 |  | 72 |  | 72
| 3 |  | DO-NIS-R |  | NIS | R |  | DIGITAL OUTPUT HARDWARE SIGNAL (NON INTRINSICALLY SAFE, REDUNDANT) | [6 empty] | 121 |  | 146 |  | 145.2
ABBREVIATIONS:
|  | I/O |  | INPUT / OUTPUT | [7 empty] | DCS: | DISTRIBUTED CONTROL SYSTEM
|  | DI: |  | DIGITAL INPUT SIGNAL | [7 empty] | ESD: | EMERGENCY SHUT DOWN SYSTEM
|  | DO: |  | DIGITAL OUTPUT SIGNAL | [7 empty] | F&G | FIRE AND GAS CONTROL SYSTEM
|  | AI: |  | ANALOGUE INPUT SIGNAL | [7 empty] | MCC: | MOTOR CONTROL CENTER
|  | AO: |  | ANALOGUE OUTPUT SIGNAL | [7 empty] | IRP: | INTERPOSING RELAY PANEL
|  | IND: |  | INDICATION | [7 empty] | CH: | CHANNEL
|  | STA: |  | STATUS | [7 empty] | ADD: | ADDRESS
|  | COM: |  | COMMAND | [7 empty] | TB: | TERMINAL BLOCK
|  | IS: |  | INTRINSICALLY SAFE | [7 empty] | R: | REDUNDANT
|  | NIS: |  | NON INTRINSICALLY SAFE | [7 empty] | NR: | NON-REDUNDANT
|  | MAC: |  | MANUAL CALL POINT | [7 empty] | BR: | BLUE BEACON
|  | HN: |  | HORN | [7 empty] | BB: | RED BEACON
|  | LHD: |  | LINEAER HEAT DETECTOR | [7 empty] | FGD: | FLAMMABLE GAS DETECTOR
|  | SD: |  | SMOKE DETECTOR | [7 empty] | TGD: | TOXIC GAS DETECTOR
|  | BL: |  | BELL | [7 empty] | FD: | FLAME DETECTOR
|  | FACP: |  | FIRE ALARM CONTROL PANEL | [7 empty] | IRP: | INTERFACE RELAY PANEL
Class: 1
D03

## IO List for F&G System
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
I/O LIST FOR F&G SYSTEMS
شماره پیمان: |  |  |  | پروژه |  | بسته کاری |  | صادرکننده |  | تسهیلات |  |  | رشته |  | نوع مدرک | سریال |  |  | نسخه
9184 – 073 - 053 |  |  |  | BK |  | GCS |  | PEDCO |  | 120 |  |  | IN |  | LI | 0004 |  |  | D03
SIGNALS TO F&G SYSTEM
ITEM | TAG | DESCRIPTION | LOCATION |  | P&ID |  | SIGNAL TYPE/ Area CLASSIFICATION | I/O TYPE |  | FROM |  | TO |  | JB NO. | POWER SUPPLY | Cable Type | SYSTEM CABINET |  |  |  |  | Marshalling Cabinet |  |  | ALARM |  |  |  | I/O TYPE (ADDRE./CONV.) | REMARK | REV.
[17 empty] | CABINET NO. | RACK | SLOT | CH. | ADD. | CABINET NO. | TB NO. | ADD. | HH | H | L | LL
FOR PROCESS AREA
1 | MAC-1001 | Manual Call Point | Area 1 - Pig Receiver Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
2 | MAC-1002 | Manual Call Point | Area 1 - Pig Receiver Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
3 | HN-1001 | Horn | Area 1 - Pig Receiver Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | 2X DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 5 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
4 | BR-1001 | Beacon - Red | Area 1 - Pig Receiver Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
5 | BB-1001 | Beacon - Blue | Area 1 - Pig Receiver Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
6 | BY-1001 | Beacon - Yellow | Area 1 - Pig Receiver Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
7 | MAC-2001 | Manual Call Point | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
8 | MAC-2002 | Manual Call Point | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
9 | MAC-2003 | Manual Call Point | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
10 | HN-2001 | Horn | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | 2X DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 5 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
11 | BR-2001 | Beacon - Red | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
12 | BB-2001 | Beacon - Blue | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
13 | BY-2001 | Beacon - Yellow | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
14 | MAC-3001 | Manual Call Point | Area 3 - Chemical Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
15 | HN-3001 | Horn | Area 3 - Chemical Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | 2X DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 5 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
16 | BR-3001 | Beacon - Red | Area 3 - Chemical Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
17 | BB-3001 | Beacon - Blue | Area 3 - Chemical Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
18 | BY-3001 | Beacon - Yellow | Area 3 - Chemical Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
19 | MAC-4001 | Manual Call Point | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
20 | MAC-4002 | Manual Call Point | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
21 | HN-4001 | Horn | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 OF 12) |  | Eexd Zone2, IIB T4 | 2X DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 5 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
22 | BR-4001 | Beacon - Red | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
23 | BB-4001 | Beacon - Blue | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
24 | BY-4001 | Beacon - Yellow | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
25 | HN-4002 | Horn | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | 2X DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 5 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
26 | Class: 1 | Beacon - Red | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
27 | BB-4002 | Beacon - Blue | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
28 | BY-4002 | Beacon - Yellow | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
29 | MAC-5001 | Manual Call Point | Area 5 - 1St. & 2nd Stage Air Cooler Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
30 | MAC-5002 | Manual Call Point | Area 5 - 1St. & 2nd Stage Air Cooler Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
31 | HN-5001 | Horn | Area 5 - 1St. & 2nd Stage Air Cooler Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | 2X DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 5 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
32 | BR-5001 | Beacon - Red | Area 5 - 1St. & 2nd Stage Air Cooler Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
33 | BB-5001 | Beacon - Blue | Area 5 - 1St. & 2nd Stage Air Cooler Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
34 | BY-5001 | Beacon - Yellow | Area 5 - 1St. & 2nd Stage Air Cooler Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
35 | MAC-6001 | Manual Call Point | Area 6 - Sump & Pig Launcher Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
36 | MAC-6002 | Manual Call Point | Area 6 - Sump & Pig Launcher Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
37 | HN-6001 | Horn | Area 6 - Sump & Pig Launcher Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | 2X DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 5 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
38 | BR-6001 | Beacon - Red | Area 6 - Sump & Pig Launcher Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
39 | BB-6001 | Beacon - Blue | Area 6 - Sump & Pig Launcher Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
40 | BY-6001 | Beacon - Yellow | Area 6 - Sump & Pig Launcher Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
41 | MAC-7001 | Manual Call Point | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
42 | MAC-7002 | Manual Call Point | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
43 | HN-7002 | Horn | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | 2X DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 5 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
44 | BR-7002 | Beacon - Red | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
45 | BB-7002 | Beacon - Blue | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
46 | BY-7002 | Beacon - Yellow | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
47 | MAC-8001 | Manual Call Point | Area 8 - Diesel Generator Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
48 | MAC-8002 | Manual Call Point | Area 8 - Diesel Generator Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
49 | HN-8001 | Horn | Area 8 - Diesel Generator Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | 2X DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 5 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
50 | BR-8001 | Beacon - Red | Area 8 - Diesel Generator Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
51 | BB-8001 | Beacon - Blue | Area 8 - Diesel Generator Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
52 | BY-8001 | Beacon - Yellow | Area 8 - Diesel Generator Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
53 | MAC-9001 | Manual Call Point | Area 9 - Air Compressor /Air Dryer Packages Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
54 | MAC-9002 | Manual Call Point | Area 9 - Air Compressor /Air Dryer Packages Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
55 | HN-9001 | Horn | Area 9 - Air Compressor /Air Dryer Packages Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | 2X DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 5 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
56 | BR-9001 | Beacon - Red | Area 9 - Air Compressor /Air Dryer Packages Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
57 | BB-9001 | Beacon - Blue | Area 9 - Air Compressor /Air Dryer Packages Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
58 | BY-9001 | Beacon - Yellow | Area 9 - Air Compressor /Air Dryer Packages Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
59 | FGD-1001 | Flammable Gas Detector | Area 1 - Pig Receiver Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (4 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
60 | TGD-1001 | Toxic Gas Detector | Area 1 - Pig Receiver Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (4 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
61 | FD-2001 | Flame Detector | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (5 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
62 | FD-2002 | Flame Detector | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (5 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
63 | FD-2003 | Flame Detector | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (5 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
64 | FGD-2001 | Flammable Gas Detector | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (5 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
65 | FGD-2002 | Flammable Gas Detector | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (5 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
66 | FGD-2003 | Flammable Gas Detector | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (5 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
67 | FGD-2004 | Flammable Gas Detector | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (5 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
68 | TGD-2001 | Toxic Gas Detector | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (5 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
69 | TGD-2002 | Toxic Gas Detector | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (5 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
70 | TGD-2003 | Toxic Gas Detector | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (5 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
71 | TGD-2004 | Toxic Gas Detector | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (5 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
72 | FD-3001 | Flame Detector | Area 3 - Chemical Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (6 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
73 | FGD-3001 | Flammable Gas Detector | Area 3 - Chemical Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (6 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional | Deleted | D03
74 | TGD-3001 | Toxic Gas Detector | Area 3 - Chemical Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (6 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional | Deleted | D03
75 | FD-4001A | Flame Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
76 | FD-4002A | Flame Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
77 | FD-4003A | Flame Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
78 | FD-4004A | Flame Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
79 | FGD-4001A | Flammable Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
80 | FGD-4002A | Flammable Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
81 | FGD-4003A | Flammable Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
82 | FGD-4004A | Flammable Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
83 | TGD-4001A | Toxic Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
84 | TGD-4002A | Toxic Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
85 | TGD-4003A | Toxic Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
86 | TGD-4004A | Toxic Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
87 | FD-4001B | Flame Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
88 | FD-4002B | Flame Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
89 | FD-4003B | Flame Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
90 | FD-4004B | Flame Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
91 | FGD-4001B | Flammable Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
92 | FGD-4002B | Flammable Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
93 | FGD-4003B | Flammable Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
94 | FGD-4004B | Flammable Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
95 | TGD-4001B | Toxic Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
96 | TGD-4002B | Toxic Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
97 | TGD-4003B | Toxic Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
98 | TGD-4004B | Toxic Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
99 | FD-4001C | Flame Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
100 | FD-4002C | Flame Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
101 | FD-4003C | Flame Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
102 | FD-4004C | Flame Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
103 | FGD-4001C | Flammable Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
104 | FGD-4002C | Flammable Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
105 | FGD-4003C | Flammable Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
106 | FGD-4004C | Flammable Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
107 | TGD-4001C | Toxic Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
108 | TGD-4002C | Toxic Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
109 | TGD-4003C | Toxic Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
110 | TGD-4004C | Toxic Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
111 | FGD-5001A | Flammable Gas Detector | Area 5 - 1St. & 2nd Stage Air Cooler Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (8 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
112 | FGD-5001B | Flammable Gas Detector | Area 5 - 1St. & 2nd Stage Air Cooler Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (8 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
113 | FGD-5001C | Flammable Gas Detector | Area 5 - 1St. & 2nd Stage Air Cooler Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (8 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
114 | TGD-5001A | Toxic Gas Detector | Area 5 - 1St. & 2nd Stage Air Cooler Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (8 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
115 | TGD-5001B | Toxic Gas Detector | Area 5 - 1St. & 2nd Stage Air Cooler Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (8 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
116 | TGD-5001C | Toxic Gas Detector | Area 5 - 1St. & 2nd Stage Air Cooler Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (8 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
117 | FD-6001 | Flame Detector | Area 6 - Sump & Pig Launcher Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (9 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
118 | FD-6002 | Flame Detector | Area 6 - Sump & Pig Launcher Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (9 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
119 | FGD-6001 | Flammable Gas Detector | Area 6 - Sump & Pig Launcher Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (9 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
120 | FGD-6002 | Flammable Gas Detector | Area 6 - Sump & Pig Launcher Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (9 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
121 | FGD-6003 | Flammable Gas Detector | Area 6 - Sump & Pig Launcher Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (9 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
122 | TGD-6001 | Toxic Gas Detector | Area 6 - Sump & Pig Launcher Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (9 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
123 | TGD-6002 | Toxic Gas Detector | Area 6 - Sump & Pig Launcher Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (9 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
124 | TGD-6003 | Toxic Gas Detector | Area 6 - Sump & Pig Launcher Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (9 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
125 | LHD-7001 | Linear Heat Detector | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (10 OF 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
126 | LHD-7002 | Linear Heat Detector | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (10 OF 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
127 | LHD-7003 | Linear Heat Detector | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (10 OF 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional | Deleted | D03
128 | LHD-7004 | Linear Heat Detector | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (10 OF 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional | Deleted | D03
129 | FGD-7001 | Flammable Gas Detector | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (10 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
130 | FGD-7002 | Flammable Gas Detector | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (10 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
131 | FGD-7003 | Flammable Gas Detector | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (10 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
132 | TGD-7001 | Toxic Gas Detector | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (10 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
133 | TGD-7002 | Toxic Gas Detector | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (10 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
134 | TGD-7003 | Toxic Gas Detector | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (10 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
135 | FD-8001 | Flame Detector | Area 8 - Diesel Generator Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (11 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
136 | FD-8002 | Flame Detector | Area 9 - Air Compressor /Air Dryer Packages Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (12 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional | ADDED | D03
137 | PT-2301 | Pressure Transmitter | Fire Water Pressure |  | BK-GCS-PEDCO-120-SA-PI-0001(2/2) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 2Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional | ADDED | D03
138 | HN-1011 | Horn | Guard House |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | 2X DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 5 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional | ADDED | D03
139 | BR-1011 | Beacon - Red | Guard House |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional | ADDED | D03
140 | BB-1011 | Beacon - Blue | Guard House |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional | ADDED | D03
141 | BY-1011 | Beacon - Yellow | Guard House |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional | ADDED | D03
FOR BUILDING
1 | FGD-1101 | Flammable Gas Detector | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
2 | FGD-1102 | Flammable Gas Detector | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * | * | √ | √ |  | Conventional
3 | FGD-1103 | Flammable Gas Detector | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * | * | √ | √ |  | Conventional
4 | TGD-1101 | Toxic Gas Detector | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * | * | √ | √ |  | Conventional
5 | TGD-1102 | Toxic Gas Detector | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * | * | √ | √ |  | Conventional
6 | TGD-1103 | Toxic Gas Detector | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * | * | √ | √ |  | Conventional
7 | FGD-1201 | Flammable Gas Detector | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (3/6) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * | * | √ | √ |  | Conventional
8 | FGD-1202 | Flammable Gas Detector | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (3/6) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * | * | √ | √ |  | Conventional
9 | FGD-1203 | Flammable Gas Detector | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (3/6) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * | * | √ | √ |  | Conventional
10 | TGD-1201 | Toxic Gas Detector | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (3/6) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * | * | √ | √ |  | Conventional
11 | TGD-1202 | Toxic Gas Detector | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (3/6) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * | * | √ | √ |  | Conventional
12 | TGD-1203 | Toxic Gas Detector | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (3/6) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * | * | √ | √ |  | Conventional
13 | HGD-1101 | Hydrogen Gas Detector | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Eexd 'Zone1, IIC T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * | √ | √ |  | Conventional
14 | HGD-1102 | Hydrogen Gas Detector | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Eexd 'Zone1, IIC T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * | √ | √ |  | Conventional
15 | HGD-1103 | Hydrogen Gas Detector | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Eexd 'Zone1, IIC T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * | √ | √ |  | Conventional | Deleted | D03
16 | HD-1101 | Heat Detector | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Eexd 'Zone1, IIC T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional
17 | HD-1102 | Heat Detector | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Eexd 'Zone1, IIC T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional
18 | HD-1103 | Heat Detector | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Eexd 'Zone1, IIC T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional | Deleted | D03
18 | MAC-1101 | Manual Call Point | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Eexd 'Zone1, IIC T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional
SIGNALS BETWEEN F&G AND ESD SYSTEM & OTHER SYSTEMS
1 | ESD0-FG-1101 | ESD 0 Request | Control Building |  | BK-GCS-PEDCO-120-IN-DG-0003 |  | Unclassified | DO-NIS-R |  | FGS |  | ESD |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional
2 | ESD1A-FG-1101 | ESD 1A Request | Control Building |  | BK-GCS-PEDCO-120-IN-DG-0003 |  | Unclassified | DO-NIS-R |  | FGS |  | ESD |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional
3 | ESD1A-FD-1101 | ESD 1A Request | Control Building |  | BK-GCS-PEDCO-120-IN-DG-0003 |  | Unclassified | DO-NIS-R |  | FGS |  | ESD |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional | ADDED | D03
4 | ESD2A-FG-1101A | ESD 2A(Train A) Request | Control Building |  | BK-GCS-PEDCO-120-IN-DG-0003 |  | Unclassified | DO-NIS-R |  | FGS |  | ESD |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional | Deleted | D03
5 | ESD2A-FG-1101B | ESD 2A(Train B) Request | Control Building |  | BK-GCS-PEDCO-120-IN-DG-0003 |  | Unclassified | DO-NIS-R |  | FGS |  | ESD |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional | Deleted | D03
6 | ESD2A-FG-1101C | ESD 2A(Train C) Request | Control Building |  | BK-GCS-PEDCO-120-IN-DG-0003 |  | Unclassified | DO-NIS-R |  | FGS |  | ESD |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional | Deleted | D03
7 | FAN-FG-1101 | Battery Room Standby Fan Activation | Control Building |  | - |  | Unclassified | DO-NIS-R |  | FGS |  | IRP |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional
8 | INB-FG-1101 | Inhibit to Boost for UPS Charger | Control Building |  | - |  | Unclassified | DO-NIS-R |  | FGS |  | UPS |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional
9 | Ex-FG-G-1101 | F&G System confirmed Gas Alarm to Existing F&G | Control Building |  | - |  | Unclassified | DO-NIS-R |  | FGS |  | Existing F&G |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional | to be finalized based on existing f&g system | D03
10 | Ex-FG-F-1101 | F&G System confirmed Fire Alarm to Existing F&G System | Control Building |  | - |  | Unclassified | DO-NIS-R |  | FGS |  | Existing F&G |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D03
11 | Ex-FG-G-1102 | Existing F&G confirmed Gas Alarm to F&G System | Control Building |  | - |  | Unclassified | DI-NIS-R |  | Existing F&G |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D03
12 | Ex-FG-F-1102 | Existing F&G confirmed Fire Alarm to F&G System | Control Building |  | - |  | Unclassified | DI-NIS-R |  | Existing F&G |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D03
13 | HV-FG-1101 | HVAC confirmed damper closed to F&G System | Control Building |  | - |  | Unclassified | DI-NIS-R |  | HVAC |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional | ADDED | D03
14 | HV-FG-1102 | F&G System confirmed Gas Alarm to HVAC | Control Building |  | - |  | Unclassified | DO-NIS-R |  | FGS |  | HVAC |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional | ADDED | D03
15 | LSLL-2301 | Low Low Level Alarm | Control Building |  | BK-GCS-PEDCO-120-SA-PI-0001(2/1) |  | Eexd 'Zone1, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional
16 | LSLL-2302 | Low Low Level Alarm | Control Building |  | BK-GCS-PEDCO-120-SA-PI-0001(2/1) |  | Eexd 'Zone1, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional
17 | HSS-2301A | Pump Start Command | Control Building |  | BK-GCS-PEDCO-120-SA-PI-0001(2/2) |  | Eexd 'Zone1, IIB T4 | DO-NIS-R | DO-NIS-R | FGS | FGS | IRP | Battery Room Fan |  | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D03
18 | XL-2301A | Pump Local/ Remote Status | Control Building |  | BK-GCS-PEDCO-120-SA-PI-0001(2/2) |  | Eexd 'Zone1, IIB T4 | DI-NIS-R | DI-NIS-R | IRP | Battery Room Fan | FGS | FGS |  | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional | Deleted | D03
19 | XR-2301A | Pump Running/ Stopped Status | Control Building |  | BK-GCS-PEDCO-120-SA-PI-0001(2/2) |  | Eexd 'Zone1, IIB T4 | DI-NIS-R | DI-NIS-R | IRP | Battery Room Fan | FGS | FGS |  | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D03
20 | XF-2301A | Pump Fault Status | Control Building |  | BK-GCS-PEDCO-120-SA-PI-0001(2/2) |  | Eexd 'Zone1, IIB T4 | DI-NIS-R | DI-NIS-R | IRP | Battery Room Fan | FGS | FGS |  | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D03
21 | PAL-2301A | Low Pressure Alarm | Control Building |  | BK-GCS-PEDCO-120-SA-PI-0001(2/2) |  | Eexd 'Zone1, IIB T4 | DI-NIS-R | DI-NIS-R | P-2301A | Battery Room Fan | FGS | FGS |  | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional | Deleted | D03
22 | HSS-2301B | Pump Start Command | Control Building |  | BK-GCS-PEDCO-120-SA-PI-0001(2/2) |  | Eexd 'Zone1, IIB T4 | DO-NIS-R | DO-NIS-R | FGS | FGS | P-2301B | Battery Room Fan |  | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional
23 | XL-2301B | PumpAuto/ Manual Status | Control Building |  | BK-GCS-PEDCO-120-SA-PI-0001(2/2) |  | Eexd 'Zone1, IIB T4 | DI-NIS-R | DI-NIS-R | P-2301B | Battery Room Fan | FGS | FGS |  | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional
24 | XR-2301B | Pump Running/ Stopped Status | Control Building |  | BK-GCS-PEDCO-120-SA-PI-0001(2/2) |  | Eexd 'Zone1, IIB T4 | DI-NIS-R | DI-NIS-R | P-2301B | Battery Room Fan | FGS | FGS |  | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional
25 | XF-2301B | Pump Fault Status | Control Building |  | BK-GCS-PEDCO-120-SA-PI-0001(2/2) |  | Eexd 'Zone1, IIB T4 | DI-NIS-R | DI-NIS-R | P-2301B | Battery Room Fan | FGS | FGS |  | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional
26 | PAL-2301B | Low Pressure Alarm | Control Building |  | BK-GCS-PEDCO-120-SA-PI-0001(2/2) |  | Eexd 'Zone1, IIB T4 | DI-NIS-R | DI-NIS-R | P-2301B | Battery Room Fan | FGS | FGS |  | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional
27 | HSS-2302A | Pump Start Command | Control Building |  | BK-GCS-PEDCO-120-SA-PI-0001(2/2) |  | Eexd 'Zone1, IIB T4 | DO-NIS-R | DO-NIS-R | FGS | FGS | P-2302A | Battery Room Fan |  | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional
28 | XL-2302A | PumpAuto/ Manual Status | Control Building |  | BK-GCS-PEDCO-120-SA-PI-0001(2/2) |  | Eexd 'Zone1, IIB T4 | DI-NIS-R | DI-NIS-R | P-2302A | Battery Room Fan | FGS | FGS |  | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional
29 | XR-2302A | Pump Running/ Stopped Status | Control Building |  | BK-GCS-PEDCO-120-SA-PI-0001(2/2) |  | Eexd 'Zone1, IIB T4 | DI-NIS-R | DI-NIS-R | P-2302A | Battery Room Fan | FGS | FGS |  | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional
30 | XF-2302A | Pump Fault Status | Control Building |  | BK-GCS-PEDCO-120-SA-PI-0001(2/2) |  | Eexd 'Zone1, IIB T4 | DI-NIS-R | DI-NIS-R | P-2302A | Battery Room Fan | FGS | FGS |  | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional
31 | PAL-2302A | Low Pressure Alarm | Control Building |  | BK-GCS-PEDCO-120-SA-PI-0001(2/2) |  | Eexd 'Zone1, IIB T4 | DI-NIS-R | DI-NIS-R | P-2302A | Battery Room Fan | FGS | FGS |  | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional
32 | HSS-2302B | Pump Start Command | Control Building |  | BK-GCS-PEDCO-120-SA-PI-0001(2/2) |  | Eexd 'Zone1, IIB T4 | DO-NIS-R | DO-NIS-R | FGS | FGS | P-2302B | Battery Room Fan |  | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional
33 | XL-2302B | PumpAuto/ Manual Status | Control Building |  | BK-GCS-PEDCO-120-SA-PI-0001(2/2) |  | Eexd 'Zone1, IIB T4 | DI-NIS-R | DI-NIS-R | P-2302B | Battery Room Fan | FGS | FGS |  | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional
34 | XR-2302B | Pump Running/ Stopped Status | Control Building |  | BK-GCS-PEDCO-120-SA-PI-0001(2/2) |  | Eexd 'Zone1, IIB T4 | DI-NIS-R | DI-NIS-R | P-2302B | Battery Room Fan | FGS | FGS |  | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional
35 | XF-2302B | Pump Fault Status | Control Building |  | BK-GCS-PEDCO-120-SA-PI-0001(2/2) |  | Eexd 'Zone1, IIB T4 | DI-NIS-R | DI-NIS-R | P-2302B | Battery Room Fan | FGS | FGS |  | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional
36 | PAL-2302B | Low Pressure Alarm | Control Building |  | BK-GCS-PEDCO-120-SA-PI-0001(2/2) |  | Eexd 'Zone1, IIB T4 | DI-NIS-R | DI-NIS-R | P-2302B | Battery Room Fan | FGS | FGS |  | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional
37 | XA-CO2-1101 | MANUAL/AUTO SELECTOR SWITCH STATUS (FOR PROTECTED AREA) | Control Building |  | BK-GCS-PEDCO-120-SA-PI-0002 |  | - | DI-NIS-R |  | CO2 Control Panel |  | FGS | FGS |  | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional | Added | D03
38 | XRE-CO2-1101 | RELEASED STATUS (FOR PROTECTED AREA) | Control Building |  | BK-GCS-PEDCO-120-SA-PI-0002 |  | - | DI-NIS-R |  | CO2 Control Panel |  | FGS | FGS |  | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional | Added | D03
39 | XI-CO2-1101 | INHIBIT STATUS (FOR PROTECTED AREA) | Control Building |  | BK-GCS-PEDCO-120-SA-PI-0002 |  | - | DI-NIS-R |  | CO2 Control Panel |  | FGS | FGS |  | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional | Added | D03
40 | XF-CO2-1101 | GENERAL FAULT | Control Building |  | BK-GCS-PEDCO-120-SA-PI-0002 |  | - | DI-NIS-R |  | CO2 Control Panel |  | FGS | FGS |  | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional | Added | D03
41 | HS-CO2-1101 | AUTOMAT RELEASE COMMAND (FOR PROTECTED AREA) | Control Building |  | BK-GCS-PEDCO-120-SA-PI-0002 |  | - | DO-NIS-R |  | FGS | FGS | CO2 Control Panel |  |  | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional | Added | D03
42 | PSH-2302 | Valve Status | Control Building |  | BK-GCS-PEDCO-120-SA-PI-0001 |  | Eexd 'Zone1, IIB T4 | DI-NIS-R | DI-NIS-R | DV-2302 |  | FGS | FGS |  | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional | Added | D03
43 | DSOV-2302 | Valve Open Command | Control Building |  | BK-GCS-PEDCO-120-SA-PI-0001 |  | Eexd 'Zone1, IIB T4 | DO-NIS-R | DI-NIS-R | FGS | FGS | DV-2302 |  |  | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional | Added | D03
44 | PSH-2303 | Valve Status | Control Building |  | BK-GCS-PEDCO-120-SA-PI-0001 |  | Eexd 'Zone1, IIB T4 | DI-NIS-R | DI-NIS-R | DV-2303 |  | FGS | FGS |  | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional | Added | D03
45 | DSOV-2303 | Valve Open Command | Control Building |  | BK-GCS-PEDCO-120-SA-PI-0001 |  | Eexd 'Zone1, IIB T4 | DO-NIS-R | DI-NIS-R | FGS | FGS | DV-2303 |  |  | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional | Added | D03
46 | PSH-2304 | Valve Status | Control Building |  | BK-GCS-PEDCO-120-SA-PI-0001 |  | Eexd 'Zone1, IIB T4 | DI-NIS-R | DI-NIS-R | DV-2304 |  | FGS | FGS |  | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional | Added | D03
47 | DSOV-2304 | Valve Open Command | Control Building |  | BK-GCS-PEDCO-120-SA-PI-0001 |  | Eexd 'Zone1, IIB T4 | DO-NIS-R | DI-NIS-R | FGS | FGS | DV-2304 |  |  | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional | Added | D03
48 | PSH-2305 | Valve Status | Control Building |  | BK-GCS-PEDCO-120-SA-PI-0001 |  | Eexd 'Zone1, IIB T4 | DI-NIS-R | DI-NIS-R | DV-2305 |  | FGS | FGS |  | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional | Added | D03
49 | DSOV-2305 | Valve Open Command | Control Building |  | BK-GCS-PEDCO-120-SA-PI-0001 |  | Eexd 'Zone1, IIB T4 | DO-NIS-R | DI-NIS-R | FGS | FGS | DV-2305 |  |  | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional | Added | D03
SIGNALS TO F&G Matrix PANEL
1 | LP-AR1-FD | Fire Alarm For Area 1 | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional | low frequency pulse for prealarm and high frequency pulse for alarm | D03
2 | LP-AR1-FGD | Felemmable Gas Alarm For Area 1 | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D03
3 | LP-AR1-TGD | Toxic Gas Alarm For Area 1 | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D03
4 | LP-AR2-FD | Fire Alarm For Area 2 | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D03
5 | LP-AR2-FGD | Felemmable Gas Alarm For Area 2 | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D03
6 | LP-AR2-TGD | Toxic Gas Alarm For Area 2 | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D03
7 | LP-AR3-FD | Fire Alarm For Area 3 | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D03
8 | LP-AR4A-FD | Fire Alarm For Area 4A | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D03
9 | LP-AR4A-FGD | Felemmable Gas Alarm For Area 4 A | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D03
10 | LP-AR4A-TGD | Toxic Gas Alarm For Area 4A | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D03
11 | LP-AR4B-FD | Fire Alarm For Area 4B | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D03
12 | LP-AR4B-FGD | Felemmable Gas Alarm For Area 4 B | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D03
13 | LP-AR4B-TGD | Toxic Gas Alarm For Area 4B | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D03
14 | LP-AR4C-FD | Fire Alarm For Area 4C | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D03
15 | LP-AR4C-FGD | Felemmable Gas Alarm For Area 4C | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D03
16 | LP-AR4C-TGD | Toxic Gas Alarm For Area 4C | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D03
17 | LP-AR5-FD | Fire Alarm For Area 5 | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D03
18 | LP-AR5-FGD | Felemmable Gas Alarm For Area 5 | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D03
19 | LP-AR5-TGD | Toxic Gas Alarm For Area 5 | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D03
20 | LP-AR6-FD | Fire Alarm For Area 6 | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D03
21 | LP-AR6-FGD | Felemmable Gas Alarm For Area 6 | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D03
22 | LP-AR6-TGD | Toxic Gas Alarm For Area 6 | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D03
23 | LP-AR7-FD | Fire Alarm For Area 7 | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D03
24 | LP-AR7-FGD | Felemmable Gas Alarm For Area 7 | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D03
25 | LP-AR7-TGD | Toxic Gas Alarm For Area 7 | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D03
26 | LP-AR8-FD | Fire Alarm For Area 8 | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D03
27 | LP-AR9-FD | Fire Alarm For Area 9 | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D03
28 | LP-CB-FD | Fire Alarm For Control Building | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D03
29 | LP-CB-FGD | Felemmable Gas Alarm For Control Building | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D03
30 | LP-CB-TGD | Toxic Gas Alarm For Control Building | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D03
31 | LP-EB-FD | Fire Alarm For Electrical Building | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D03
32 | LP-EB-FGD | Felemmable Gas Alarm For Electrical Building | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D03
33 | LP-EB-TGD | Toxic Gas Alarm For Electrical Building | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D03
34 | LP-PSH-2302 | Deluge Valve 2302 Opened | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D03
35 | LP-PSH-2303 | Deluge Valve 2303 Opened | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D03
36 | LP-PSH-2304 | Deluge Valve 2304 Opened | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D03
37 | LP-PSH-2305 | Deluge Valve 2305 Opened | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D03
38 | LP-P-2301B | Diesel Pump Status | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D03
39 | LP-P-2301A | Electrical Pump Status | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D03
40 | LP-CO2-RE | CO2 Release Status | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D03
41 | PB-DV-2302 | Deluge Valve 2302 Open Command | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DI-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D03
42 | PB-DV-2303 | Deluge Valve 2302 Open Command | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DI-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D03
43 | PB-DV-2304 | Deluge Valve 2302 Open Command | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DI-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D03
44 | PB-DV-2305 | Deluge Valve 2302 Open Command | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DI-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D03
45 | PB-P-2301B | Diesel Pump Start Command | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DI-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D03
46 | PB-P-2301A | Electrical Pump Start Command | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DI-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D03
47 | PB-CO2-CO | CO2 Release Command | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DI-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D03
48 | PB-RST | RESET-PB | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DI-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D03
49 | PB-ACK-HO | ACK HORN-PB | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DI-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D03
50 | PB-ACK | ACK-PB | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DI-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D03
51 | HORN | Audible Alarm | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D03
D03

## IO List for FACP
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
I/O LIST FOR F&G SYSTEMS
شماره پیمان: |  |  |  | پروژه |  | بسته کاری |  | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه
9184 – 073 - 053 |  |  |  | BK |  | GCS |  | PEDCO | 120 |  | IN | LI | 0004 | D03
SIGNALS TO FACP
ITEM | TAG | DESCRIPTION | LOCATION |  | P&ID |  | SIGNAL TYPE/ Area CLASSIFICATION | I/O TYPE | FROM | TO |  | POWER SUPPLY | Cable Type | Marshalling Cabinet |  |  | ALARM |  |  |  | I/O TYPE (ADDRE./CONV.) | REMARK | REV.
[14 empty] | CABINET NO. | TB NO. | ADD. | HH | H | L | LL
FOR BUILDING
FACP LOOP 1
1 | FACP | Output Port of Loop 1 | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | FACP | MAC-1104 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
2 | MAC-1104 | Manual Call Point | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | MAC-1104 | SD-1101 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
3 | SD-1101 | Smoke Detector | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1101 | SD-1102 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE | deleted | D03
4 | SD-1102 | Smoke Detector | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1102 | SD-1103 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE | deleted | D03
5 | SD-1103 | Smoke Detector | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1103 | SD-1104 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
6 | SD-1104 | Smoke Detector | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1104 | SD-1105 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
7 | SD-1105 | Smoke Detector | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1105 | SD-1106 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
8 | SD-1106 | Smoke Detector | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1106 | SD-1107 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
9 | SD-1107 | Smoke Detector | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1107 | SD-1108 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
10 | SD-1108 | Smoke Detector | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1108 | MAC-1103 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
11 | MAC-1103 | Manual Call Point | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | MAC-1103 | HN-1102 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
12 | HN-1102 | Horn | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | HN-1102 | BR-1102 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE | deleted | D03
13 | BR-1102 | Beacon - Red | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | BR-1102 | BB-1102 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE | deleted | D03
14 | BB-1102 | Beacon - Blue | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | BB-1102 | BY-1102 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE | deleted | D03
15 | BY-1102 | Beacon - Yellow | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | BY-1102 | MAC-1102 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE | deleted | D03
16 | MAC-1102 | Manual Call Point | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | MAC-1102 | MAC-1106 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D03
17 | MAC-1106 | Manual Call Point | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | MAC-1106 | BR-1103 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE | deleted | D03
18 | BR-1103 | Beacon - Red | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | BR-1103 | BL-1101 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
19 | BL-1101 | Bell | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | BL-1101 | SD-1109 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
20 | SD-1109 | Smoke Detector | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1109 | BR-1104 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
21 | BR-1104 | Beacon - Red | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | BR-1104 | MAC-1105 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE | deleted | D03
22 | MAC-1105 | Manual Call Point | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | MAC-1105 | 0 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
23 |  | Bell | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | 0 | MAC-1109 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE | deleted | D03
24 | MAC-1109 | Manual Call Point | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | MAC-1109 | Class: 1 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE | deleted | D03
25 | Class: 1 | Horn | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | Class: 1 | BR-1101 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
26 | BR-1101 | Beacon - Red | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | BR-1101 | BB-1101 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
27 | BB-1101 | Beacon - Blue | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | BB-1101 | BY-1101 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
28 | BY-1101 | Beacon - Yellow | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | BY-1101 | SD-1116 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
29 | SD-1116 | Smoke Detector | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1116 | SD-1117 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
30 | SD-1117 | Smoke Detector | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1117 | MAC-1107 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
31 | MAC-1107 | Manual Call Point | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | MAC-1107 | SD-1120 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE | deleted | D03
32 | SD-1120 | Smoke Detector | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1120 | SD-1118 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
33 | SD-1118 | Smoke Detector | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1118 | SD-1119 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
34 | SD-1119 | Smoke Detector | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1119 | SD-1114 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
35 | SD-1114 | Smoke Detector | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1114 | SD-1113 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
36 | SD-1113 | Smoke Detector | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1113 | SD-1111 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
37 | SD-1111 | Smoke Detector | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1111 | SD-1110 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
38 | SD-1110 | Smoke Detector | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1110 | SD-1112 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
39 | SD-1112 | Smoke Detector | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1112 | SD-1115 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
40 | SD-1115 | Smoke Detector | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1115 | MAC-1108 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
41 | MAC-1108 | Manual Call Point | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | MAC-1108 | FACP |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE | deleted | D03
FACP LOOP 2
1 | FACP | Output Port of Loop 2 | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | FACP | SD-1181 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE | deleted | D03
2 | SD-1181 | Smoke Detector | Control Building-False Floor |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1181 | SD-1182 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE | deleted | D03
3 | SD-1182 | Smoke Detector | Control Building-False Floor |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1182 | SD-1183 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE | deleted | D03
4 | SD-1183 | Smoke Detector | Control Building-False Floor |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1183 | SD-1184 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE | deleted | D03
5 | SD-1184 | Smoke Detector | Control Building-False Floor |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1184 | SD-1185 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE | deleted | D03
6 | SD-1185 | Smoke Detector | Control Building-False Floor |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1185 | SD-1186 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE | deleted | D03
7 | SD-1186 | Smoke Detector | Control Building-False Floor |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1186 | SD-1187 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE | deleted | D03
8 | SD-1187 | Smoke Detector | Control Building-False Floor |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1187 | SD-1188 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE | deleted | D03
9 | SD-1188 | Smoke Detector | Control Building-False Floor |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1188 | SD-1189 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE | deleted | D03
10 | SD-1189 | Smoke Detector | Control Building-False Floor |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1189 | SD-1190 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE | deleted | D03
11 | SD-1190 | Smoke Detector | Control Building-False Floor |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1190 | SD-1191 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE | deleted | D03
12 | SD-1191 | Smoke Detector | Control Building-False Floor |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1191 | SD-1192 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE | deleted | D03
13 | SD-1192 | Smoke Detector | Control Building-False Floor |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1192 | SD-1193 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE | deleted | D03
14 | SD-1193 | Smoke Detector | Control Building-False Floor |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1193 | SD-1194 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE | deleted | D03
15 | SD-1194 | Smoke Detector | Control Building-False Floor |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1194 | SD-1195 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE | deleted | D03
16 | SD-1195 | Smoke Detector | Control Building-False Floor |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1195 | SD-1196 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE | deleted | D03
17 | SD-1196 | Smoke Detector | Control Building-False Floor |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1196 | SD-1197 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE | deleted | D03
18 | SD-1197 | Smoke Detector | Control Building-False Floor |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1197 | FACP |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE | deleted | D03
FACP LOOP 3
1 | FACP | Output Port of Loop 3 | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | FACP | SD-1150 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE | deleted | D03
2 | SD-1150 | Smoke Detector | Control Building-False Ceiling |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1150 | SD-1151 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE | deleted | D03
3 | SD-1151 | Smoke Detector | Control Building-False Ceiling |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1151 | SD-1152 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE | deleted | D03
4 | SD-1152 | Smoke Detector | Control Building-False Ceiling |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1152 | SD-1153 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE | deleted | D03
5 | SD-1153 | Smoke Detector | Control Building-False Ceiling |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1153 | SD-1154 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE | deleted | D03
6 | SD-1154 | Smoke Detector | Control Building-False Ceiling |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1154 | SD-1155 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE | deleted | D03
7 | SD-1155 | Smoke Detector | Control Building-False Ceiling |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1155 | SD-1156 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE | deleted | D03
8 | SD-1156 | Smoke Detector | Control Building-False Ceiling |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1156 | SD-1157 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE | deleted | D03
9 | SD-1157 | Smoke Detector | Control Building-False Ceiling |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1157 | SD-1158 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE | deleted | D03
10 | SD-1158 | Smoke Detector | Control Building-False Ceiling |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1158 | SD-1159 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE | deleted | D03
11 | SD-1159 | Smoke Detector | Control Building-False Ceiling |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1159 | SD-1160 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE | deleted | D03
12 | SD-1160 | Smoke Detector | Control Building-False Ceiling |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1160 | SD-1161 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE | deleted | D03
13 | SD-1161 | Smoke Detector | Control Building-False Ceiling |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1161 | SD-1162 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE | deleted | D03
14 | SD-1162 | Smoke Detector | Control Building-False Ceiling |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1162 | SD-1163 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE | deleted | D03
15 | SD-1163 | Smoke Detector | Control Building-False Ceiling |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1163 | SD-1164 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE | deleted | D03
16 | SD-1164 | Smoke Detector | Control Building-False Ceiling |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1164 | SD-1165 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE | deleted | D03
17 | SD-1165 | Smoke Detector | Control Building-False Ceiling |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1165 | SD-1166 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE | deleted | D03
18 | SD-1166 | Smoke Detector | Control Building-False Ceiling |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1166 | SD-1167 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE | deleted | D03
19 | SD-1167 | Smoke Detector | Control Building-False Ceiling |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1167 | SD-1168 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE | deleted | D03
20 | SD-1168 | Smoke Detector | Control Building-False Ceiling |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1168 | SD-1169 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE | deleted | D03
21 | SD-1169 | Smoke Detector | Control Building-False Ceiling |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1169 | SD-1170 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE | deleted | D03
22 | SD-1170 | Smoke Detector | Control Building-False Ceiling |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1170 | FACP |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE | deleted | D03
FACP LOOP 4
1 | FACP | Output Port of Loop 4 | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | FACP | HN-1201 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
2 | HN-1201 | Horn | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (4/6) |  | Note 1 | Note1 | HN-1201 | BR-1201 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
3 | BR-1201 | Beacon - Red | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (4/6) |  | Note 1 | Note1 | BR-1201 | BB-1201 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
4 | BB-1201 | Beacon - Blue | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (4/6) |  | Note 1 | Note1 | BB-1201 | BY-1201 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
5 | BY-1201 | Beacon - Yellow | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (4/6) |  | Note 1 | Note1 | BY-1201 | MAC-1201 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
6 | MAC-1201 | Manual Call Point | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (4/6) |  | Note 1 | Note1 | MAC-1201 | SD-1201 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
7 | SD-1201 | Smoke Detector | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (4/6) |  | Note 1 | Note1 | SD-1201 | SD-1203 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
8 | SD-1203 | Smoke Detector | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (4/6) |  | Note 1 | Note1 | SD-1203 | SD-1202 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
7 | SD-1202 | Smoke Detector | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (4/6) |  | Note 1 | Note1 | SD-1202 | SD-1204 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE | ADDED | D03
8 | SD-1204 | Smoke Detector | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (4/6) |  | Note 1 | Note1 | SD-1204 | MAC-1202 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE | ADDED | D03
9 | MAC-1202 | Manual Call Point | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (4/6) |  | Note 1 | Note1 | MAC-1202 | FACP |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
FACP LOOP 5
1 | FACP | Output Port of Loop 5 | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | FACP | HN-1202 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
2 | HN-1202 | Horn | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (5/6) |  | Note 1 | Note1 | HN-1202 | BR-1202 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
3 | BR-1202 | Beacon - Red | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (5/6) |  | Note 1 | Note1 | BR-1202 | BY-1202 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
4 | BB-1202 | Beacon - Blue | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (5/6) |  | Note 1 | Note1 | BB-1202 | BY-1202 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
5 | BY-1202 | Beacon - Yellow | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (5/6) |  | Note 1 | Note1 | BY-1202 | MAC-1203 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
6 | MAC-1203 | Manual Call Point | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (5/6) |  | Note 1 | Note1 | MAC-1203 | LHD-1201 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
7 | LHD-1201 | Linear Heat Detector | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (5/6) |  | Note 1 | Note1 | LHD-1201 | LHD-1202 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
8 | LHD-1202 | Linear Heat Detector | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (5/6) |  | Note 1 | Note1 | LHD-1202 | LHD-1203 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
9 | LHD-1203 | Linear Heat Detector | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (5/6) |  | Note 1 | Note1 | LHD-1203 | FACP |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
FACP LOOP 6
1 | FACP | Output Port of Loop 6 | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | FACP | SD-1301 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
2 | SD-1301 | Smoke Detector | Telecom Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1301 | SD-1302 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
3 | SD-1302 | Smoke Detector | Telecom Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1302 | SD-1303 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
4 | SD-1303 | Smoke Detector | Telecom Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1303 | HD-1303 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
5 | HD-1303 | Linear Heat Detector | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (5/6) |  | Note 1 | Note1 | HD-1303 | MAC-1303 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE | ADDED | D03
6 | MAC-1303 | Manual Call Point | Telecom Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (4/6) |  | Note 1 | Note1 | MAC-1303 | SD-1304 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE | deleted | D03
7 | SD-1304 | Smoke Detector | Telecom Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1304 | SD-1305 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
8 | SD-1305 | Smoke Detector | Telecom Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1305 | SD-1306 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE | deleted | D03
9 | SD-1306 | Smoke Detector | Telecom Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1306 | SD-1307 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE | deleted | D03
10 | SD-1307 | Smoke Detector | Telecom Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1307 | MAC-1302 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE | deleted | D03
11 | MAC-1302 | Manual Call Point | Telecom Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (4/6) |  | Note 1 | Note1 | MAC-1302 | MAC-1301 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
12 | MAC-1301 | Manual Call Point | Telecom Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (4/6) |  | Note 1 | Note1 | MAC-1301 | HN-1301 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
13 | HN-1301 | Horn | Telecom Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (4/6) |  | Note 1 | Note1 | HN-1301 | BR-1301 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
14 | BR-1301 | Beacon - Red | Telecom Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (4/6) |  | Note 1 | Note1 | BR-1301 | BB-1301 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
15 | BB-1301 | Beacon - Blue | Telecom Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (4/6) |  | Note 1 | Note1 | BB-1301 | BY-1301 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
16 | BY-1301 | Beacon - Yellow | Telecom Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (4/6) |  | Note 1 | Note1 | BY-1301 | 0 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
SIGNALS BETWEEN FACP AND CO2 CONTROL PACKAGE
1 | XA-CO2-1101 | MANUAL/AUTO SELECTOR SWITCH STATUS (FOR PROTECTED AREA) | Control Building |  | BK-GCS-PEDCO-120-SA-PI-0002 |  | - | DI-NIS-R | CO2 Control Panel | FACP |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE | deleted | D03
2 | XRE-CO2-1101 | RELEASED STATUS (FOR PROTECTED AREA) | Control Building |  | BK-GCS-PEDCO-120-SA-PI-0002 |  | - | DI-NIS-R | CO2 Control Panel | FACP |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE | deleted | D03
3 | XI-CO2-1101 | INHIBIT STATUS (FOR PROTECTED AREA) | Control Building |  | BK-GCS-PEDCO-120-SA-PI-0002 |  | - | DI-NIS-R | CO2 Control Panel | FACP |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE | deleted | D03
4 | XF-CO2-1101 | GENERAL FAULT | Control Building |  | BK-GCS-PEDCO-120-SA-PI-0002 |  | - | DI-NIS-R | CO2 Control Panel | FACP |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE | deleted | D03
5 | HS-CO2-1101 | AUTOMAT RELEASE COMMAND (FOR PROTECTED AREA) | Control Building |  | BK-GCS-PEDCO-120-SA-PI-0002 |  | - | DO-NIS-R | FACP | CO2 Control Panel |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE | deleted | D03
Notes:
1- Non-IS Detector is on the Loop. Level of Alarm is N.A. for such Loop-powered.