## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-IN-DT-0017_D01 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1703 |  |  | Transmital Date: 17 Dec 2022
Document Title: Data Sheets For ESD Console/F&G Matrix Panel |  |  |  |  | PEDCO Tr. No.:BK-PEDCO-NISOC-0005-IN-TR-1703 |  |  | Transmital Date: 17 Dec 2022
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-IN-DT-0017_D01 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | لازم است Button هایی که الویت بالاتری دارند COVERED شوند. |  | 1401/2294/388761 | 1401/10/13 | برای تمامی پوش باتن ها PROTECTION COVERED لحاظ گردید.
2 | ACKNOELEDGE BUTTONمی تواند جهت آلارم های جدید همراه با لامپ روشن ثابت آلارم باشد.(توضیح اینکه وقتی آلارمی فعال می شود صدا فعال شده و لامپ مربوطه بصورت چشمک زن می باشد و با فشردن ACK صدا قطع و چشمک زن لامپ به روشن ثابت تبدیل می شود.) |  | 1401/2294/388761 | 1401/10/13 | اضافه گردید. Acknowledge Button
3 | هرگونه سوییچ جهت OVERRIDE سیستم ESD مورد تایید نمی باشد. در صورت نیاز به تعریف OVERRIDEبرای ESD لازم است این اقدام از طریق EWS وبا سطح دسترسی ENGINEERING انجام پذیرد.همچنین در مدت زمان OVERRIDE آلارم های دیداری و شنیداری فعال شده و این فعالیت LOG می گردد. |  | 1401/2294/388761 | 1401/10/13 | درخواست کارفرمای محترم لحاظ گردید.
4 | میمیک پنل مورد نیاز نمی باشد شماتیک واحد به همراه محل قراگیری تجهیزات متعلق به سیستم F&Gنمایش داده شود. |  | 1401/2294/388761 | 1401/10/13 | کنسول F&G به صورت ماتریکس پنل طراحی گردیده است و هر ناحیه به طور مجزا مشخص گردیده است.
5 | آرم ولوگو شرکت مناطق نفت خیزجنوب حداقل سه برابر آرم دیگر شرکت ها در نظر گرفته شود. |  | 1401/2294/388761 | 1401/10/13 | درخواست کارفرمای محترم لحاظ گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: S.Akbari | Signature |  |  |  | Clarified By: | Signature
| Date: 1 Jan 2023 |  |  |  |  | Date: