## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No:BK-GCS-PEDCO-120-AR-DW-0006 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-2337 |  |  | Transmital Date:9/3/2023
Document Title: Architectural Drawing For Fire Water Pumps Shelter |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0004-AR-T-2337 |  |  | Transmital Date:9/3/2023
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-AR-DW-0006_D02 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | 23- توجه به فاصله زیاد بین ترانشه برق با الکتروموتورهای آب آتش نشانی(جوکی پمپ ها و پمپ اصلی)، لازم است به جای کاندوئیت از تراشه فرعی بتنی با ابعاد مناسب استفاده گردد. |  | 1402-2294-264590 | 1402/07/08 | کاندوئیت ها حذف گردید و ترنچ بتنی برای کابل های برق در نظر گرفته شده است.
2 | 24- ترانشه فرعی در زیر سایبان می بایست در جهت CABLE BOX موتور در نظر گرفته شود. |  | 1402-2294-264590 | 1402/07/08 | بر اساس اطلاعات دریافت شده از بخش برق موقعیت صحیح ترنچ ها درنظر گرفته شده است.
3 | 25-آخرین نسخه مورد تائید مدرک AREA CABLE ROUTE در واحد تقویت فشار، ملاک عمل قرار داده شود. |  | 1402-2294-264590 | 1402/07/08 | آخرین مدرک ملاک عمل قرار گرفت.
4 | 26- دلیل در نظر گرفتن کاندوئیت بانک جهت دیزل پمپ آتش نشانی، چیست؟ |  | 1402-2294-264590 | 1402/07/08 | مطابق کامنت ردیف 23، کاندوئیت ها حذف گردید و ترنچ بتنی در نظر گرفته شده است.
5 | 27- تابلو/سوئیچ روشنایی سایبان و مسیر برق رسانی به آن در نقشه مشخص گردد. |  | 1402-2294-264590 | 1402/07/08 | طبق نظر بخش برق تابلو روشنایی در محدوده ای قرار دارد که در این نقشه نمایش داده نمی شود. برای جزئیات بیشتر لطفا به مدارک بخش برق رجوع گردد.
16 | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
17
18 | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
19 | Commented By: | Signature |  |  |  | Clarified By: | Signature
20
21 | Date: |  |  |  |  | Date:
22
23
24
25
26
Legend
Signature