| طرح نگهداشت و افزایش تولید 27 مخزن |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| MTO FOR TRAY/LADDER AND ACCESSORIES نگهداشت و افزایش تولید میدان نفتی بینک |  |  |  |  |  |  |
| D00 | Dec. 2023 | IFI | H.Shakiba | M.Fakharian | S.Faramarzpour |  |
| Rev. | Date | Purpose of Issue/Status | Prepared by: | Checked by: | Approved by: | Client Approval |
| Class:3 |  | Client Doc. Number: F8Z-709076 |  |  |  |  |
| Status: | IDC: Inter-Discipline Check IFC: Issued For Comment IFA: Issued For Approval AFD: Approved For Design AFC: Approved For Construction AFP: Approved For Purchase AFQ: Approved For Quotation IFI: Issued For Information AB-R: As-Built for CLIENT Review AB-A: As-Built –Approved |  |  |  |  |  |

REVISION RECORD SHEET

| PAGE | D00 | D01 | D02 | D03 | D04 |  | PAGE | D00 | D01 | D02 | D03 | D04 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | X |  |  |  |  |  | 51 |  |  |  |  |  |
| 2 | X |  |  |  |  |  | 52 |  |  |  |  |  |
| 3 | X |  |  |  |  |  | 53 |  |  |  |  |  |
| 4 | X |  |  |  |  |  | 54 |  |  |  |  |  |
| 5 | X |  |  |  |  |  | 55 |  |  |  |  |  |
| 6 | X |  |  |  |  |  | 56 |  |  |  |  |  |
| 7 | X |  |  |  |  |  | 57 |  |  |  |  |  |
| 8 |  |  |  |  |  |  | 58 |  |  |  |  |  |
| 9 |  |  |  |  |  |  | 59 |  |  |  |  |  |
| 10 |  |  |  |  |  |  | 60 |  |  |  |  |  |
| 11 |  |  |  |  |  |  | 61 |  |  |  |  |  |
| 12 |  |  |  |  |  |  | 62 |  |  |  |  |  |
| 13 |  |  |  |  |  |  | 63 |  |  |  |  |  |
| 14 |  |  |  |  |  |  | 64 |  |  |  |  |  |
| 15 |  |  |  |  |  |  | 65 |  |  |  |  |  |
| 16 |  |  |  |  |  |  | 66 |  |  |  |  |  |
| 17 |  |  |  |  |  |  | 67 |  |  |  |  |  |
| 18 |  |  |  |  |  |  | 68 |  |  |  |  |  |
| 19 |  |  |  |  |  |  | 69 |  |  |  |  |  |
| 20 |  |  |  |  |  |  | 70 |  |  |  |  |  |
| 21 |  |  |  |  |  |  | 71 |  |  |  |  |  |
| 22 |  |  |  |  |  |  | 72 |  |  |  |  |  |
| 23 |  |  |  |  |  |  | 73 |  |  |  |  |  |
| 24 |  |  |  |  |  |  | 74 |  |  |  |  |  |
| 25 |  |  |  |  |  |  | 75 |  |  |  |  |  |
| 26 |  |  |  |  |  |  | 76 |  |  |  |  |  |
| 27 |  |  |  |  |  |  | 77 |  |  |  |  |  |
| 28 |  |  |  |  |  |  | 78 |  |  |  |  |  |
| 29 |  |  |  |  |  |  | 79 |  |  |  |  |  |
| 30 |  |  |  |  |  |  | 80 |  |  |  |  |  |
| 31 |  |  |  |  |  |  | 81 |  |  |  |  |  |
| 32 |  |  |  |  |  |  | 82 |  |  |  |  |  |
| 33 |  |  |  |  |  |  | 83 |  |  |  |  |  |
| 34 |  |  |  |  |  |  | 84 |  |  |  |  |  |
| 35 |  |  |  |  |  |  | 85 |  |  |  |  |  |
| 36 |  |  |  |  |  |  | 86 |  |  |  |  |  |
| 37 |  |  |  |  |  |  | 87 |  |  |  |  |  |
| 38 |  |  |  |  |  |  | 88 |  |  |  |  |  |
| 39 |  |  |  |  |  |  | 89 |  |  |  |  |  |
| 40 |  |  |  |  |  |  | 90 |  |  |  |  |  |
| 41 |  |  |  |  |  |  | 91 |  |  |  |  |  |
| 42 |  |  |  |  |  |  | 92 |  |  |  |  |  |
| 43 |  |  |  |  |  |  | 93 |  |  |  |  |  |
| 44 |  |  |  |  |  |  | 94 |  |  |  |  |  |
| 45 |  |  |  |  |  |  | 95 |  |  |  |  |  |
| 46 |  |  |  |  |  |  | 96 |  |  |  |  |  |
| 47 |  |  |  |  |  |  | 97 |  |  |  |  |  |
| 48 |  |  |  |  |  |  | 98 |  |  |  |  |  |
| 49 |  |  |  |  |  |  | 99 |  |  |  |  |  |
| 50 |  |  |  |  |  |  | 100 |  |  |  |  |  |

| Cable Tray/Ladder Specification |  |  |  |  |
| --- | --- | --- | --- | --- |
| Mild Steel Sheet, Hot Dip Galvanized Steel Material as per ASTM A 123, 4 Fold, Minimum Galvanizing Thickness 65 Micron |  |  |  |  |
| Standard Length of Tray/Ladder is 3000mm & Height is 100mm. |  |  |  |  |
| Cable Tray/Ladder Shall be Capable of Supporting Following Loads |  |  |  |  |
| 150 mm Width: 30 KG/Linear Meter Thickness: 2mm |  |  |  |  |
| 300 mm Width: 60 KG/Linear Meter Thickness: 2mm |  |  |  |  |
| 500 mm Width: 75 KG/Linear Meter Thickness: 2mm |  |  |  |  |
| 600 mm Width: 90 KG/Linear Meter Thickness: 2.5mm |  |  |  |  |
| 750 mm Width: 120 KG/Linear Meter Thickness: 2.5mm |  |  |  |  |
| 900 mm Width: 150 KG/Linear Meter Thickness: 2.5mm |  |  |  |  |
| Item | Rev | Technical data | Unit | Quantity |
| - Cable Ladder & Accessories |  |  |  |  |
|  | D00 | Cable Ladder Straight,12 Steps, 600Wx100Hx3000L | PCS | 70 |
|  | D00 | Cable Ladder 900 Horizontal Bend, 600w x 100h x Radius 600mm | PCS | 5 |
|  | D00 | Cable Ladder 900 Vertical Inside Bend, 600w x 100h x Radius 600mm | PCS | 5 |
|  | D00 | Cable Ladder 900 Vertical Outside Bend, 600w x 100h x Radius 600mm | PCS | 3 |
|  | D00 | Cable Ladder Tee 900, 600w x 100h x Radius 600mm | PCS | 5 |
|  | D00 | Cable Ladder Cross, 600w x 100h x Radius 600mm | PCS | 10 |
|  | D00 | Cable Ladder Vertical Adjustable Riser, 600w x 100h | PCS | 6 |
|  | D00 | Cable Ladder Reducer Left Hand Side, 600w x 100h | PCS | 8 |
|  | D00 | Cable Ladder Reducer Right Hand Side, 600w x 100h | PCS | 8 |
|  | D00 | Side L Joint Type, 200l x 100h mm, with Mushroom Bolt, Nuts & Flat/Spring Washer | PCS | 250 |
|  | D00 | Holding Clamp Ladder with Hex Bolt, Nuts & Flat/Spring Washer | PCS | 200 |
|  | D00 | Double C Channel Support, 2700l, Thickness 2.5mm, 80 x 50 x50, With Base Plate Welded to C Channel, with 4 No, M12 x 60 with Bolt & Nut & Washer (Expansion) | PCS | 300 |
|  | D00 | Base Plate, with 4 No, M12 x 60 with Bolt & Nut & Washer (Self-Drilling Expansion) | PCS | 100 |
|  | D00 | Bracket Suitable for item 1.14, Thickness 2.5mm, 630l x 150h | PCS | 250 |
| - Cable Tray & Accessories |  |  |  |  |
|  | D00 | Perforated Tray Straight with Cover, 500Wx100Hx3000L | PCS | 20 |
|  | D00 | Perforated Tray 900 Horizontal Bend with Cover, 600w x 100h x Radius 600mm | PCS | 5 |
|  | D00 | Perforated Tray 900 Vertical Inside Bend with Cover, 600w x 100h x Radius 600mm | PCS | 5 |
|  | D00 | Perforated Tray 900 Vertical Outside Bend with Cover, 600w x 100h x Radius 600mm | PCS | 5 |
|  | D00 | Perforated Tray Tee 900, with Cover, 600w x 100h x Radius 600mm | PCS | 5 |
|  | D00 | Perforated Tray Cross, with Cover 600w x 100h x Radius 600mm | PCS | 10 |
|  | D00 | Holding Clamp Tray with Bolt, Nuts & Flat/Spring Washer | PCS | 500 |
|  | D00 | Bracket Suitable for item 1.14, Thickness 2.5mm, 530l x 150h | PCS | 250 |

Bolt & Nut, Flat Washer & Spring Washer

Double C Channel with

Base Plate

Cable Ladder Tee

Multi Bracket

Holding Clamp Tray

Ladder Horizontal Bend

Cover Tray Clamp

Base Plate

s

Cable Ladder

Cable Ladder Cross

Holding Clamp Ladder

Cable Tray Horizontal Bend

Cable Tray Cross

Cable Tray Horizontal Tee

Tray

Notes:

- This document shall be Based on below references:

Document Title: “Electrical Cable Route & Section Layout for Building & Shelter”

Document No.: “BK-GCS-PEDCO-120-EL-PY-0006”

Document Title: “Area Electrical Cable Route & Section Layout”

Document No.: “BK-GCS-PEDCO-120-EL-PY-0005”