## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-EL-MT-0003_D00 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-2143 |  |  | Transmital Date: 24-May-2023
Document Title: MTO For Power & Control Cables |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-EL-TR-2143 |  |  | Transmital Date: 24-May-2023
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-PEDCO-120-EL-MT-0003_D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | This document shall be issued after finalizing or minor comments on "Electrical Power & Control Cable Schedule" and "Area Electrical Cable Route & Section Layout". |  | BK-SUR-ENG-ELE-02-07794 | 2023-06-03
2 | There is conflict between this document and "Electrical Power & Control Cable Schedule" from point of cable length, size and number of core view. It shall be rechecked and modified. |  | BK-SUR-ENG-ELE-02-07794 | 2023-06-03
3 | Considered spare part in tables of document for different size of cables shall be rechecked from contractual point of view base on scope of work & supply and spare part instruction and modified. (If required) |  | BK-SUR-ENG-ELE-02-07794 | 2023-06-03
4 | It shall be clarify UV resistant for outer sheet has been mentioned base on which document. It seems it is not necessary for all cables base on electrical design criteria and specification. |  | BK-SUR-ENG-ELE-02-07794 | 2023-06-03
5 | Cable type of 1C×95 mm2 CU/XPLE/SWA/PVC shall be modified to CU/XPLE/AWA/PVC on page 4. |  | BK-SUR-ENG-ELE-02-07794 | 2023-06-03
6 | Cables type of section 5 on page 6 shall be modified to CU/XPLE/SWA/PVC instead of CU/XPLE/AWA/PVC. |  | BK-SUR-ENG-ELE-02-07794 | 2023-06-03
7 | Next revision of this document shall be submitted after finalizing or minor comments on prerequisite document as above mentioned comments. |  | BK-SUR-ENG-ELE-02-07794 | 2023-06-03
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 03-Jun-23 |  |  |  |  | Date: