## Cover
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
I&C POWER CONSUMPTION SUMMARY
شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 8
9184 – 073 - 053 |  |  | BK |  | GCS | PEDCO | 120 |  | IN | LI | 0007 | D04
طرح نگهداشت و افزایش تولید 27 مخزن
I&C POWER CONSUMPTION SUMMARY نگهداشت و افزایش تولید میدان نفتی بینک
D04 |  | JAN.2024 |  | IFA |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | S.Faramarzpour
D03 |  | AUG.2023 |  | IFA |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | A.M.Mohseni
D02 |  | DEC.2022 |  | IFA |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
D01 |  | APR.2022 |  | IFA |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
D00 |  | FEB.2022 |  | IFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
Class: 1 |  |  |  | CLIENT Doc. Number: F0Z-708973
status: | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved

## REVISION
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
I&C POWER CONSUMPTION SUMMARY
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 8
9184 – 073 - 053 |  |  | BK | GCS |  | PEDCO | 120 | IN | LI | 0007 |  | D04
REVISION RECORD SHEET
Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D01 |  | D02 | D03 | D04
1 | X | X | X |  | X |  | X |  | 65
2 | X | X | X |  | X |  | X |  | 66
3 | X | X | [6 empty] | 67
4 | X | X | X |  | X |  | X |  | 68
5 | X | X | X |  | X |  | X |  | 69
6 |  | X | X |  | X |  |  |  | 70
7 |  |  |  |  | X |  | X |  | 71
8 |  |  |  |  | X |  | X |  | 72
9 | [8 empty] | 73
10 | [8 empty] | 74
11 | [8 empty] | 75
12 | [8 empty] | 76
13 | [8 empty] | 77
14 | [8 empty] | 78
15 | [8 empty] | 79
16 | [8 empty] | 80
17 | [8 empty] | 81
18 | [8 empty] | 82
19 | [8 empty] | 83
20 | [8 empty] | 84
21 | [8 empty] | 85
22 | [8 empty] | 86
23 | [8 empty] | 87
24 | [8 empty] | 88
25 | [8 empty] | 89
26 | [8 empty] | 90
27 | [8 empty] | 91
28 | [8 empty] | 92
29 | [8 empty] | 93
30 | [8 empty] | 94
31 | [8 empty] | 95
32 | [8 empty] | 96
33 | [8 empty] | 97
34 | [8 empty] | 98
35 | [8 empty] | 99
36 | [8 empty] | 100
37 | [8 empty] | 101
38 | [8 empty] | 102
39 | [8 empty] | 103
40 | [8 empty] | 104
41 | [8 empty] | 105
42 | [8 empty] | 106
43 | [8 empty] | 107
44 | [8 empty] | 108
45 | [8 empty] | 109
46 | [8 empty] | 110
47 | [8 empty] | 111
48 | [8 empty] | 112
49 | [8 empty] | 113
50 | [8 empty] | 114
51 | [8 empty] | 115
52 | [8 empty] | 116
53 | [8 empty] | 117
54 | [8 empty] | 118
55 | [8 empty] | 119
56 | [8 empty] | 120
57 | [8 empty] | 121
58 | [8 empty] | 122
59 | [8 empty] | 123
60 | [8 empty] | 124
61 | [8 empty] | 125
62 | [8 empty] | 126
63 | [8 empty] | 127
64 | [8 empty] | 128

## REFERENCES
NISOC |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
I&C POWER CONSUMPTION SUMMARY
شماره پیمان: |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 3 از 8
9184 – 073 - 053 |  | BK | GCS | PEDCO | 120 | IN | LI | 0007 | D04
REFERENCE DOCUMENTS:
| I/O LIST FOR CONTROL SYSTM | [7 empty] | BK-GCS-PEDCO-120-IN-LI-0002
| I/OLIST FOR ESD SYSTEM | [7 empty] | BK-GCS-PEDCO-120-IN-LI-0003
| I/O LIST FOR F&G SYSTEM | [7 empty] | BK-GCS-PEDCO-120-IN-LI-0004
| SPECIFICATION FOR INSTRUMENTATION | [7 empty] | BK-GNRAL-PEDCO-000-IN-SP-0001
| SPECIFICATION FOR CONTROL SYSTEM | [7 empty] | BK-GNRAL-PEDCO-000-IN-SP-0002
| SPECIFICATION FOR ESD SYSTEM | [7 empty] | BK-GNRAL-PEDCO-000-IN-SP-0003
| SPECIFICATION FOR ESD SYSTEM | [7 empty] | BK-GNRAL-PEDCO-000-IN-SP-0012
| SPECIFICATION FOR INSTRUMENT AND CONTROL OF PACKAGE UNIT SYSTEM(PU | [7 empty] | BK-GNRAL-PEDCO-000-IN-SP-0004

## UPS 110 VAC
NISOC |  |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
I&C POWER CONSUMPTION SAMMARY
شماره پیمان: |  |  |  |  | پروژه | بسته کاری |  | صادرکننده |  | تسهیلات |  | رشته | نوع مدرک |  | سریال |  | نسخه | شماره صفحه: 4 از 8
9184 – 073 - 053 |  |  |  |  | BK | GCS |  | PEDCO |  | 120 |  | IN | LI |  | 0007 |  | D04
INST./CONTROL UPS 110 VAC POWER CONSUMPTION TABLE
- Table (1) is represents AC UPS power consumption for inst./control system. The estimation is based on the design of control systems, comprising of various equipment located in Control Room/Field.
| ITEM | DESCRIPTION |  |  |  | PANEL QTY (Note 1) | BACK UP TIME | ESTIMATTED I/O (NOTE 3) |  |  | POWER CONSUMPTION (W) (Note 1)( AS PER APPENDIX A,B) |  |  | FEEDER QTY |  | TOTAL POWER CONSUMPTION (W)
| 1 | DCS SYSTEM PANEL (AS PER APPENDEX "A") |  | Power Supply for CPUs ( 2 No. redundant) |  | 1 | 2 hr. | 400 |  |  | 600 |  |  | 2 Nos. (Redundant) |  | 1100
|  |  |  | 110/24 VDC Power Supply |  |  | 2 hr. |  |  |  | 500 |  |  | 2 Nos. (Redundant)
|  |  |  | Socket - 110 VAC |  |  | - |  |  |  | 200 |  |  | -
| 2 | DCS MARSHALING PANEL (AS PER APPENDEX "B") |  | 110/24 VDC Power Supply ( 2 No. redundant) |  | 3 | 2 hr. | - |  |  | 810 |  |  | 2 Nos. (Redundant) |  | 810
|  |  |  | Socket - 110 VAC |  |  | - |  |  |  | 200 |  |  | -
| 3 | ESD SYSTEM PANEL (AS PER APPENDEX "A") |  | Power Supply for CPUs ( 2 No. redundant) |  | 1 | 2 hr. | 200 |  |  | 600 |  |  | 2 Nos. (Redundant) |  | 1000
|  |  |  | 110/24 VDC Power Supply |  |  | 2 hr. |  |  |  | 400 |  |  | 2 Nos. (Redundant)
|  |  |  | Socket - 110 VAC |  |  | - |  |  |  | 200 |  |  | -
| 4 | ESD MARSHALING PANEL (AS PER APPENDEX "B") |  | 110/24 VDC Power Supply |  | 2 | 2 hr. | - |  |  | 430 |  |  | 2 Nos. (Redundant) |  | 430
|  |  |  | Socket - 110 VAC |  |  | - |  |  |  | 200 |  |  | -
| ITEM | DESCRIPTION |  |  |  | PANEL QTY (Note 1) | BACK UP TIME | ESTIMATTED I/O (NOTE 3) |  |  | UNIT POWER CONSUMPTION (W) (Note 1) |  |  | FEEDER QTY |  | TOTAL POWER CONSUMPTION (W)
| 5 | ELECRO GAS COMPRESSOR UCP A/B/C SYSTEM AND MARSHALING CABINET |  |  |  | 3 | 2 hr. | 3x200 |  |  | 1500 |  |  | 2 Nos. (Redundant) |  | 4500
| 6 | DEHYDRATION PACKAGE(UCP/BMS) |  |  |  | 2 | 2 hr. | 2x60 |  |  | 500 |  |  | 2 Nos. (Redundant) | 1 | 1000
| 7 | PAGING SYSTEM |  |  |  | 1 | 2 hr. | - |  |  | 1000 |  |  | 2 Nos. (Redundant) | 1 | 1000
| 8 | AIR COMPRESSOR UCP A/B |  |  |  | 2 | 2 hr. | 2x100 |  |  | 1000 |  |  | 2 Nos. (Redundant) | 2 | 2000
| 9 | AIR DRAYER LOCAL LCP |  |  |  | 2 | 2 hr. | - |  |  | 800 |  |  | 2 Nos. (Redundant) | 2 | 1600
| 10 | NITROGEN PACKAGE UCP A/B |  |  |  | 1 | 2 hr. | 100 |  |  | 1000 |  |  | 2 Nos. (Redundant) | 2 | 1000
| 11 | OPERATOR WORKSTATION (INCLUDING DCS, ESD, PACKAGE OWSs) |  |  |  | 4 | 2 hr. | - |  |  | 741 |  |  | 1 No. ( Socket) | 4 | 2964
| 12 | DCS ENGINEERING WORKSTATION |  |  |  | 1 | 2 hr. | - |  |  | 713 |  |  | 1 No. ( Socket) | 4 | 713
| 13 | ESD ENGINEERING WORKSTATION |  |  |  | 1 | 2 hr. | - |  |  | 713 |  |  | 1 No. ( Socket) | 4 | 713
| 14 | F&G OPERATOR/ ENGINEERING WORKSTATION |  |  |  | 1 | 2 hr. | - |  |  | 713 |  |  | 1 No. ( Socket) | 4 | 713
| 15 | PRINTER |  |  |  | 3 | 2 hr. | - |  |  | 600 |  |  | 3 No. ( Socket) | 4 | 1800
TABLE 1
|  |  | TOTAL POWER CONSUMPTION (W) | [12 empty] | 19543
|  |  | TOTAL POWER CONSUMPTION CONSIDERING SPARE CAPACITY (W) | [12 empty] | 23451.6
Note 1 : Shall Be Finalized After Purchase Through Vendor Final Documents. Power supply modules QTY, Voltage/Amp Range, Spare capacity… will be specified by vendor considering project documents.
Note 3: UPS power for HVAC Panel shall be supplied by vendor. Only 400VAC , 3 phase will be supplied by EPC contractor.
Note 3: Power Consumption of panels have been estimatted considering project I/O count. Refer to '' I/O List For Control System Doc.No.BK-GCS-PEDCO-120-IN-LI-0002 , I/O List For ESD System Doc.No.BK-GCS-PEDCO-120-IN-LI-0003 , I/O List For F&G System Doc.No.BK-GCS-PEDCO-120-IN-LI-0003
Note 4 : UPS of CCTV panel is not considered.It will be provided by vendor.
D04
D04
D04
D04

## NON UPS 230 VAC
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
I&C POWER CONSUMPTION SAMMARY
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 5 از 8
9184 – 073 - 053 |  |  |  | BK | GCS | PEDCO | 120 |  | IN | LI | 0007 | D04
INST./CONTROL NON- UPS 230 VAC POWER CONSUMPTION TABLE
- Table (2) is represents AC UPS power consumption for inst./control system. The estimation is based on the design of control systems, comprising of various equipment located in Control Room.
| ITEM | DESCRIPTION |  |  | UNIT POWER CONSUMPTION (W) (Note 1) | [5 empty] | QTY. (Note 1) | TOTAL POWER CONSUMPTION (W) + 500 W for 1 Socket per system
| 1 | Cabinet Utilities For DCS (Heater, Fan , Light, Socket) |  |  | 400 | [5 empty] | 4 | 2100
| 2 | Cabinet Utilities For ESD (Heater, Fan , Light, Socket) |  |  | 400 | [5 empty] | 3 | 1700
| 3 | Cabinet Utilities For F&G (Heater, Fan , Light, Socket) |  |  | 400 | [5 empty] | 3 | 1700
| 4 | Cabinet Utilities For Gas Compressor UCP(Heater, Fan , Light ,Socket) |  |  | 400 | [5 empty] | 3 | 1700
| 5 | Cabinet Utilities For Dehydration BMS( if any) (Heater, Socket, Fan , Light, Socket) |  |  | 400 | [5 empty] | 1 | 900
| 6 | Cabinet Utilities For Total Flooding UCP(Heater, Socket, Fan , Light, Socket) |  |  | 400 | [5 empty] | 1 | 900
| 7 | Cabinet Utilities For Paging Cabinet (Heater, Socket, Fan , Light, Socket) |  |  | 400 | [5 empty] | 1 | 900
| 8 | Cabinet Utilities For Air Compressor UCP(Heater, Socket, Fan , Light, Socket) |  |  | 400 | [5 empty] | 2 | 1300
| 9 | Cabinet Utilities For Nitrogen package UCP(Heater, Socket, Fan , Ligh, Sockett) |  |  | 400 | [5 empty] | 2 | 1300
| 10 | Control Desk Sockets |  |  | 500 | [5 empty] | 7 | 3500
| TOTAL POWER CONSUMPTION | [10 empty] | 16000
TABLE 2
|  |  | TOTAL POWER CONSUMPTION (W) | [8 empty] | 16000
|  |  | TOTAL POWER CONSUMPTION CONSIDERING SPARE CAPACITY (W) | [8 empty] | 19200
Note 1 : Shall Be Finalized After Purchase Through Vendor Final Documents.
D04
D04
D04

## 24 VDC CHARGER
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
I&C POWER CONSUMPTION SAMMARY
شماره پیمان: |  |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات |  | رشته | نوع مدرک |  | سریال |  | نسخه | شماره صفحه: 6 از 8
9184 – 073 - 053 |  |  |  | BK | GCS |  | PEDCO | 120 |  | IN | LI |  | 0007 |  | D04
INST./CONTROL UPS 24 VDC POWER CONSUMPTION TABLE
- Table (3) is represents 24V DC UPS power consumption for F&G system. The estimation is based on the design of F&G systems, comprising of various equipment located in Control Room/Field.
| ITEM | DESCRIPTION |  |  | PANEL QTY (Note 1) | BACK UP TIME | ESTIMATTED I/O (NOTE 4) |  | POWER CONSUMPTION (W) ( Refer to appendix A,B) |  |  | FEEDER QTY |  | TOTAL POWER CONSUMPTION FOR QUIESENCE MODE(W) (Note 3) |  |  | TOTAL POWER CONSUMPTION FOR ALARM MODE (W) (Note 3)
| 1 | F&G SYSTEM PANEL |  |  | 1 | 24hr. | 265 |  | 1400 |  |  | 2 Nos. (Redundant) |  | 1600 |  |  | 2700
( for Quiescence- Refer to appendix A)
[6 empty] | 5 MIN |  |  | 2500
(for alarm mode- Refer to appendix A)
| 2 | F&G MARSHALLING PANEL |  |  | 2 | 24hr. |  |  | 200
( for Quiescence- Refer to appendix B)
| 1 | FACP system |  |  | 1 | 24hr. | - |  | 400 ( for Quiescence) |  |  | 2 Nos. (Redundant) |  | 540 |  |  | -
| 2 | FACP Detectors |  |  |  | 24hr. |  |  | 140 (for Quiescence mode)
[6 empty] | 5 MIN |  |  | 500 (for alarm mode) |  |  |  |  | - |  |  | 900
| 3 | FIRE PROTECTION AND TOTAL FLOODING SYSTEM UCP |  |  | 1 | 5 MIN | 50 |  | 800 |  |  | 2 Nos. (Redundant) | 2 | - |  |  | 800
|  |  | TOTAL POWER CONSUMPTION FOR 5 MIN BACK UP TIME (W) (Note 3) | [10 empty] | 4400
|  |  | TOTAL POWER CONSUMPTION FOR 24 HOURS BACK UP TIME (W) (Note 3) | [10 empty] | 2140
|  |  | TOTAL POWER CONSUMPTION CONSIDERING SPARE CAPACITYFOR 5 MIN BACK UP TIME (W) | [10 empty] | 5280
|  |  | TOTAL POWER CONSUMPTION CONSIDERING SPARE CAPACITY FOR 24 HOURS BACK UP TIME (W) | [10 empty] | 2568
Note 1 : Shall Be Finalized After Purchase Through Vendor Final Documents. Note 2: Deleted Note 3: DC charger shall supply 2KW + Spare, for 24H back up time but also it shall be capable to prepare 4.3KW+ Spare, as a peak power consumption in alarming conditions for 5 Min back up time. it shall be considered during battery sizing in related documents. Note 4: Power Consumption of panels have been estimatted considering project I/O count. Refer to '' I/O List For Control System Doc.No.BK-GCS-PEDCO-120-IN-LI-0002 , I/O List For ESD System Doc.No.BK-GCS-PEDCO-120-IN-LI-0003 , I/O List For F&G System Doc.No.BK-GCS-PEDCO-120-IN-LI-0003.

## (APPENDIX A)
NISOC |  |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
I&C POWER CONSUMPTION SAMMARY
شماره پیمان: |  |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه | شماره صفحه: 7 از 8
9184 – 073 - 053 |  |  |  |  | BK | GCS | PEDCO | 120 | IN | LI | 0007 |  | D04
(APPENDIX "A")
| ITEM | DESCRIPTION |  |  |  | QTY |  | UNIT POWER CONSUMPTION (W) (Note 1)( 1.5 contingency) |  |  |  | TOTAL POWER CONSUMPTION (W)
| 1 | DCS SYSTEM PANEL (As per last DCS I/O List) |  | Interface Base Plates |  | 8 |  | 8.25 |  |  |  | 66
| 2 |  |  | Commuication Processor Module |  | 7 |  | 3.6 |  |  |  | 25.2
| 3 | DI : | 219 | DI Module 16Channel (Note 2) |  | 20 |  | 5.25 |  |  |  | 105 |  |  |  |  | DI-NR | 192 | 7.68 | 8 | - | -
| 4 | DO : | 91 | DO Module 16 Channel (Note 2) |  | 9 |  | 10.2 |  |  |  | 91.8 |  |  |  |  | DO-NR | 69 | 2.76 | 3 | DO-R | 2 | 1 | 1
| 5 | AI : | 98 | AI Module 8 Channel (Note 2) |  | 18 |  | 2.25 |  |  |  | 40.5 |  |  |  |  | AI-NR | 33 | 2.75 | 3 | AI-R | 46 | 3.8333 | 4
| 6 | AO : | 26 | AO Module 8 Channel (Note 2) |  | 5 |  | 9 |  |  |  | 45 |  |  |  |  | AO-R | 23 | 3.8333 | 4 | - | -
| 7 |  |  | Industrial Ethernet Switch |  | 2 |  | 22.5 |  |  |  | 45
| 8 |  |  | Spare |  | 1 SET |  | 70 |  |  |  | 70
[8 empty] | TOTAL : |  |  |  | 488.5
| ITEM | DESCRIPTION |  |  |  | QTY |  | UNIT POWER CONSUMPTION (W) (Note 1)( 1.5 contingency) |  |  |  | TOTAL POWER CONSUMPTION (W)
| 1 | ESD SYSTEM PANEL (As per last DCS I/O List) |  | Interface Base Plates |  | 8 |  | 8.25 |  |  |  | 66
| 2 | DI-R : | 47 | DI Module 16 Channel (Note 2) |  | 5 |  | 15 |  |  |  | 75 |  |  |  |  | DI-R | 39 | 1.95 | 2
| 3 | DO-R : | 107 | DO Module 16 Channel (Note 2) |  | 10 |  | 9 |  |  |  | 90 |  |  |  |  | DO-R | 91 | 11.375 | 12
| 4 | AI-R : | 72 | AI Module 8 Channel (Note 2) |  | 13 |  | 6.75 |  |  |  | 87.75 |  |  |  |  | AI-R | 59 | 11.8 | 12
| 5 |  |  | Spare |  | 1 SET. |  | 70 |  |  |  | 70
388.75
| ITEM | PANEL NAME |  | DETECTOR TYPE | 24H / 5 MIN | QTY |  | UNIT POWER CONSUMPTION (W) (Note 1)( 1.5 contingency) |  |  |  | TOTAL POWER CONSUMPTION FOR 24H (W) |  |  | TOTAL POWER CONSUMPTION FOR 5 MIN (W)
| 1 |  |  | Flame Detector : | 24H | 19 |  | 1 |  |  |  | 19 |  |  | 0
|  | F&G SYSTEM PANEL 24VDC (External) For field |  | Flame Detector : | 5 MIN | 19 |  | 8 |  |  |  | 0 |  |  | 152 | Flammable Gas Detector-ir | AI-R |  | 33 | 1 | 33
| 2 |  |  | Flammable Gas Detector : | 24H | 33 |  | 1 |  |  |  | 33 |  |  | 0 | Hydrogen Gas Detector | AI-R |  | 3 | 1 | 3
| 2 |  |  | Flammable Gas Detector : | 5 MIN | 33 |  | 13 |  |  |  | 0 |  |  | 429 | Hydrogen Gas Detector | AI-R |  | 3 | 1 | 3
| 3 |  |  | Toxic Gas Detector : | 24H | 33 |  | 1 |  |  |  | 33 |  |  | 0 | Toxic Gas Detector | AI-R |  | 33 | 30 | 990
| 3 |  |  | Toxic Gas Detector : | 5 MIN | 33 |  | 13 |  |  |  | 0 |  |  | 429 | Toxic Gas Detector | AI-R |  | 33 | 30 | 990
| 4 |  |  | Hydrogen Gas Detector : | 24H | 3 |  | 1 |  |  |  | 3 |  |  | 0
| 4 |  |  | Hydrogen Gas Detector : | 5 MIN | 3 |  | 13 |  |  |  | 0 |  |  | 39
| 5 |  |  | Manual Call Point : | 24H | 19 |  | 0 |  |  |  | 0 |  |  | 0
| 6 |  |  | Heat Detector : | 24H | 3 |  | 3 |  |  |  | 9 |  |  | 0
| 7 |  |  | Linear Heat Detector : | 24H | 4 |  | 4.2 |  |  |  | 16.8 |  |  | 0
| 8 |  |  | Beacon : | 5 MIN | 30 |  | 1 |  |  |  | 0 |  |  | 30
| 9 |  |  | Horn : | 5 MIN | 10 |  | 6 |  |  |  | 0 |  |  | 60
| 1 | F&G SYSTEM PANEL (As per last F&G I/O List) 24VDC (Internal) |  | CPU | 24H/5 MIN | 2 |  | 285 |  |  |  | 570 |  |  | 570
| 2 |  |  | DI Module 24 Channel | 24H/5 MIN | 6 |  | 15 |  |  |  | 90 |  |  | 90
| 3 | AI-R : | 88 | DO Module 10 Channel | 24H/5 MIN | 34 |  | 9 |  |  |  | 306 |  |  | 306
| 4 | DI-NR : | 47 | AI Module 6 Channel | 24H/5 MIN | 36 |  | 6.75 |  |  |  | 243 |  |  | 243
| 5 | DO-NR : | 130 | Spare | 24H/5 MIN | 1 |  | 72 |  |  |  | 72 |  |  | 72
[6 empty] | TOTAL POWER CONSUMPTION FOR 24 HOURS BACK UP TIME : | [5 empty] | 1394.8
[6 empty] | TOTAL POWER CONSUMPTION FOR 5 MIN BACK UP TIME : | [8 empty] | 2420
Note 1 : Shall Be Finalized After Purchase Through Vendor Final Documents. ( As per Siemens base )
Note 2: Number of channel per card in this project will be estimated by vendor considering minimum amount, specified in project specification and also vendor practic. For UPS calculation average for redundant cards have been considered to estimate cards QTYs.
D04

## (APPENDIX B)
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
I&C POWER CONSUMPTION SAMMARY
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه | شماره صفحه: 8 از 8
9184 – 073 - 053 |  |  |  | BK | GCS | PEDCO | 120 | IN | LI | 0007 |  | D04
(APPENDIX "B")
| ITEM | DESCRIPTION |  |  | QTY |  | UNIT POWER CONSUMPTION (W) (Note 1)( 1.5 contingency) |  |  |  | TOTAL POWER CONSUMPTION (W)
| 1 | DCS MARSHALING PANEL | Barrier |  | 150 |  | 2.6 |  |  |  | 390
| 2 |  | Relay Coils |  | 350 |  | 1 |  |  |  | 350
| 3 |  | Spare |  | 1 SET |  | 70 |  |  |  | 70
[7 empty] | TOTAL : |  |  |  | 810
| 1 | ESD MARSHALING PANEL | Barrier |  | 70 |  | 2.6 |  |  |  | 182
| 2 |  | Relay Coils |  | 170 |  | 1 |  |  |  | 170
| 3 |  | Spare |  | 1 SET |  | 70 |  |  |  | 70
[7 empty] | TOTAL : |  |  |  | 422
| 1 | F&G MARSHALING PANEL | Relay Coils |  | 130 |  | 1 |  |  |  | 130
| 2 |  | Spare |  | 1 SET |  | 70 |  |  |  | 70
[5 empty] | TOTAL POWER CONSUMPTION FOR 24 HOURS BACK UP TIME : | [5 empty] | 200
Note 1 : Shall Be Finalized After Purchase Through Vendor Final Documents. ( As per Siemens base )
D04