|  |
| --- |
| **طرح نگهداشت و افزایش تولید 27 مخزن** |
| **CALCULATION NOTE FOR TOTAL FLOODING DEMAND FOR EXTENSION OF EXISTING ELECT. BUILDING** **نگهداشت و افزایش تولید میدان نفتی بینک** |
|  |  |  |  |  |  |  |
| D03 | JAN. 2024 | AFD | A.Sabzei | M.Fakharian | A.M.MOHSENI |  |
| D02 | APR. 2023 | AFD | A.H.Saber | M.Fakharian | A.M.MOHSENI |  |
| D01 | MAR. 2022 | AFD | A.H.Saber | M.Fakharian | M.MEHRSHAD |  |
| D00 | JAN. 2022 | IFC | A.H.Saber | M.Fakharian | M.MEHRSHAD |  |
| **Rev.** | **Date** | **Purpose of Issue/Status** | **Prepared by:** | **Checked by:** | **Approved by:** | **CLIENT Approval** |
| **Class: 2** | **CLIENT Doc. Number:** **F0Z-708986** |
| **Status:** | **IDC: Inter-Discipline Check****IFC: Issued For Comment** **IFA: Issued For Approval****AFD: Approved For Design** **AFC: Approved For Construction** **AFP: Approved For Purchase****AFQ:** Approved For Quotation **IFI: Issued For Information****AB-R: As-Built for CLIENT Review** **AB-A: As-Built –Approved** |

**REVISION RECORD SHEET**

|  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **PAGE** | **D00** | **D01** | **D02** | **D03** | **D04** |  | **PAGE** | **D00** | **D01** | **D02** | **D03** | **D04** |
| **1** | X | X | X | X |  | **66** |  |  |  |  |  |
| **2** | X | X | X | X |  | **67** |  |  |  |  |  |
| **3** | X |  |  |  |  | **68** |  |  |  |  |  |
| **4** | X |  |  |  |  | **69** |  |  |  |  |  |
| **5** | X |  |  |  |  | **70** |  |  |  |  |  |
| **6** | X |  | X | X |  | **71** |  |  |  |  |  |
| **7** | X |  | X |  |  | **72** |  |  |  |  |  |
| **8** |  |  | X | X |  | **73** |  |  |  |  |  |
| **9** |  |  | X | X |  | **74** |  |  |  |  |  |
| **10** |  |  |  |  |  | **75** |  |  |  |  |  |
| **11** |  |  |  |  |  | **76** |  |  |  |  |  |
| **12** |  |  |  |  |  | **77** |  |  |  |  |  |
| **13** |  |  |  |  |  | **78** |  |  |  |  |  |
| **14** |  |  |  |  |  | **79** |  |  |  |  |  |
| **15** |  |  |  |  |  | **80** |  |  |  |  |  |
| **16** |  |  |  |  |  | **81** |  |  |  |  |  |
| **17** |  |  |  |  |  | **82** |  |  |  |  |  |
| **18** |  |  |  |  |  | **83** |  |  |  |  |  |
| **19** |  |  |  |  |  | **84** |  |  |  |  |  |
| **20** |  |  |  |  |  | **85** |  |  |  |  |  |
| **21** |  |  |  |  |  | **86** |  |  |  |  |  |
| **22** |  |  |  |  |  | **87** |  |  |  |  |  |
| **23** |  |  |  |  |  | **88** |  |  |  |  |  |
| **24** |  |  |  |  |  | **89** |  |  |  |  |  |
| **25** |  |  |  |  |  | **90** |  |  |  |  |  |
| **26** |  |  |  |  |  | **91** |  |  |  |  |  |
| **27** |  |  |  |  |  | **92** |  |  |  |  |  |
| **28** |  |  |  |  |  | **93** |  |  |  |  |  |
| **29** |  |  |  |  |  | **94** |  |  |  |  |  |
| **30** |  |  |  |  |  | **95** |  |  |  |  |  |
| **31** |  |  |  |  |  | **96** |  |  |  |  |  |
| **32** |  |  |  |  |  | **97** |  |  |  |  |  |
| **33** |  |  |  |  |  | **98** |  |  |  |  |  |
| **34** |  |  |  |  |  | **99** |  |  |  |  |  |
| **35** |  |  |  |  |  | **100** |  |  |  |  |  |
| **36** |  |  |  |  |  | **101** |  |  |  |  |  |
| **37** |  |  |  |  |  | **102** |  |  |  |  |  |
| **38** |  |  |  |  |  | **103** |  |  |  |  |  |
| **39** |  |  |  |  |  | **104** |  |  |  |  |  |
| **40** |  |  |  |  |  | **105** |  |  |  |  |  |
| **41** |  |  |  |  |  | **106** |  |  |  |  |  |
| **42** |  |  |  |  |  | **107** |  |  |  |  |  |
| **43** |  |  |  |  |  | **108** |  |  |  |  |  |
| **44** |  |  |  |  |  | **109** |  |  |  |  |  |
| **45** |  |  |  |  |  | **110** |  |  |  |  |  |
| **46** |  |  |  |  |  | **111** |  |  |  |  |  |
| **47** |  |  |  |  |  | **112** |  |  |  |  |  |
| **48** |  |  |  |  |  | **113** |  |  |  |  |  |
| **49** |  |  |  |  |  | **114** |  |  |  |  |  |
| **50** |  |  |  |  |  | **115** |  |  |  |  |  |
| **51** |  |  |  |  |  | **116** |  |  |  |  |  |
| **52** |  |  |  |  |  | **117** |  |  |  |  |  |
| **53** |  |  |  |  |  | **118** |  |  |  |  |  |
| **54** |  |  |  |  |  | **119** |  |  |  |  |  |
| **55** |  |  |  |  |  | **120** |  |  |  |  |  |
| **56** |  |  |  |  |  | **121** |  |  |  |  |  |
| **57** |  |  |  |  |  | **122** |  |  |  |  |  |
| **58** |  |  |  |  |  | **123** |  |  |  |  |  |
| **59** |  |  |  |  |  | **124** |  |  |  |  |  |
| **60** |  |  |  |  |  | **125** |  |  |  |  |  |
| **61** |  |  |  |  |  | **126** |  |  |  |  |  |
| **62** |  |  |  |  |  | **127** |  |  |  |  |  |
| **63** |  |  |  |  |  | **128** |  |  |  |  |  |
| **64** |  |  |  |  |  | **129** |  |  |  |  |  |

**CONTENTS**

[1.0 INTRODUCTION 4](#_Toc156647976)

[2.0 Scope 5](#_Toc156647977)

[3.0 NORMATIVE REFERENCES 5](#_Toc156647978)

[3.1 Local Codes and Standards 5](#_Toc156647979)

[3.2 International Codes and Standards 5](#_Toc156647980)

[3.3 The Project Documents 5](#_Toc156647981)

[3.4 ENVIRONMENTAL DATA 5](#_Toc156647982)

[4.0 CALCULATION 6](#_Toc156647983)

[4.1 Calculation Report (Capacitor Bank Room) 6](#_Toc156647984)

[4.2 Calculation Report (HV Room) 7](#_Toc156647985)

[4.3 Calculation Report (LV Room) 7](#_Toc156647986)

[4.4 Calculation Report (cable gallary Room) 8](#_Toc156647987)

[5.0 CONCLUSION 9](#_Toc156647988)

1. **INTRODUCTION**

Binak oilfield in Bushehr province is a part of the southern oilfields of Iran, is located 20 km northwest of Genaveh city.

With the aim of increasing production of oil from Binak oilfield, an EPC/EPD Project has been defined by NIOC/NISOC and awarded to Petro Iran Development Company (PEDCO). Also PEDCO (as General Contractor) has assigned the EPC-packages of the Project to "Hirgan Energy - Design and Inspection" JV.

As a part of the Project, a New Gas Compressor Station (adjacent to existing Binak GCS) shall be constructed to gather of 15 MMSCFD (approx.) associated gases and compress & transfer them to Siahmakan GIS.

**GENERAL DEFINITION**

The following terms shall be used in this document.

|  |  |
| --- | --- |
| CLIENT:  | National Iranian South Oilfields Company (NISOC)  |
| PROJECT: | Binak Oilfield Development – Surface Fcilities; New Gas Compressor Station |
| EPD/EPC CONTRACTOR (GC): | Petro Iran Development Company (PEDCO) |
| EPC CONTRACTOR: | Joint Venture of : Hirgan Energy – Design & Inspection (D&I) Companies |
| VENDOR: | The firm or person who will fabricate the equipment or material. |
| EXECUTOR:  | Executor is the party which carries out all or part of construction and/or commissioning for the project. |
| THIRD PARTY INSPECTOR (TPI): | The firm appointed by EPD/EPC CONTRACTOR (GC) and approved by CLIENT (in writing) for the inspection of goods. |
| SHALL: | Is used where a provision is mandatory. |
| SHOULD: | Is used where a provision is advisory only. |
| WILL:  | Is normally used in connection with the action by CLIENT rather than by an EPC/EPD CONTRACTOR, supplier or VENDOR. |
| MAY:  | Is used where a provision is completely discretionary. |

1. **Scope**

The objective of this report is to estimate CO2 requirement for new extension of switchgear room for Binak Oilfield Development.

1. **NORMATIVE REFERENCES**

## Local Codes and Standards

* IPS-E-SF-160 Engineering Standard for CO2 Gas Fire Extinguishing Systems.

## International Codes and Standards

* IEC 60529 Specification for Degrees of Protection Provided by Enclosures
* NFPA 12 CO2 Fixed Fire Protection Systems
* NFPA 72 National Fire Alarm Code
* ISO 3500 Gas cylinders – Seamless steel CO2 cylinders for fixed fire-fighting installations on ships
* ISO 3500/A1 Amendment 1 to Standard 3500:2005
* IEC 6183 Fire protection equipment – Carbon dioxide extinguishing systems for use on premises – Design and installation

## The Project Documents

* BK-GNRAL-PEDCO-000-SA-SP-0005 Specification for Total Flooding System

## ENVIRONMENTAL DATA

Refer to "Process Basis of Design; Doc. No. BK-GNRAL-PEDCO-000-PR-DB-0001 ".

1. **CALCULATION**

**CO2 SYSTEM**

CO2 total flooding shall be provided for:

* Capacitor Bank Room

03

* High Voltage Room
* Low Voltage Room
* Cable Gallery

**Dimension:**

|  |  |
| --- | --- |
| Room | Dimension (Width x Length x Height) - Meters |
| Capacitor Bank Room | 6.8 x 4.2 x 4.1 |
| High Voltage Room | 24.7 x 5.3 x 4 |
| Low Voltage Room | 29.8 x 5.3 x 4 |
| Cable Gallery | 29.8 x 10.8 x 2 |

## Calculation Report (Capacitor Bank Room)

|  |  |
| --- | --- |
| Zone : | Capacitor Bank Room |
| Equipment:  | Electrical Panels & Cables |
| Volume : | 6.8 x 4.2 x 4.1 = 117 m3 |
| Area Classification: | Class C-electrical fire |
| System :  | Automatic CO2  |
| Code & Standard :  | NFPA 12 |
| Type of System: | Total flooding - Multiple System |
| Type of Fire : | Deep seated |
| Flooding factor :  | 1.33 Kg/ m3 (according to table 5.4.2.1 NFPA 12) |
| Safety Factor:  | 1.1 |
| Discharge Time :  | 7 Minutes (according to 5.5.2.3 NFPA 12) |
| Concentration of CO2:  | 30 % in 2 minutes  |
| Formula : | Total CO2 required = (Vol.) x (Flooding Factor) x ( Safety Factor)  |
| CO2 Required: | 171 Kg |
| Cylinder Capacity : | 67 Lit ( 45 Kg) |
| No. of Cylinders : | 4 |

## Calculation Report (HV Room)

|  |  |
| --- | --- |
| Zone : | High Voltage Room |
| Equipment:  | Electrical Panels & Cables |
| Volume : | 24.7 x 5.3 x 4 =524 m3 |
| Area Classification: | Class C-electrical fire |
| System :  | Automatic CO2  |
| Code & Standard :  | NFPA 12 |
| Type of System: | Total flooding - Multiple System |
| Type of Fire : | Deep seated |
| Flooding factor :  | 1.33 Kg/ m3 (according to table 5.4.2.1 NFPA 12) |
| Safety Factor:  | 1.1 |
| Discharge Time :  | 7 Minutes (according to 5.5.2.3 NFPA 12) |
| Concentration of CO2:  | 30 % in 2 minutes  |
| Formula : | Total CO2 required = (Vol.) x (Flooding Factor) x ( Safety Factor)  |
| CO2 Required: | 767 Kg |
| Cylinder Capacity : | 67 Lit ( 45 Kg) |
| No. of Cylinders : | 17 |
|  |  |

## Calculation Report (LV Room)

|  |  |
| --- | --- |
| Zone : | Low Voltage Room |
| Equipment:  | Electrical Panels & Cables |
| Volume : | 29.8 x 5.3 x 4 = 632 m3 |
| Area Classification: | Class C-electrical fire |
| System :  | Automatic CO2  |
| Code & Standard :  | NFPA 12 |
| Type of System: | Total flooding - Multiple System |
| Type of Fire : | Deep seated |
| Flooding factor :  | 1.33 Kg/ m3 (according to table 5.4.2.1 NFPA 12) |
| Safety Factor:  | 1.1 |
| Discharge Time :  | 7 Minutes (according to 5.5.2.3 NFPA 12) |
| Concentration of CO2:  | 30 % in 2 minutes  |
| Formula : | Total CO2 required = (Vol.) x (Flooding Factor) x ( Safety Factor)  |
| CO2 Required: | 925 Kg |
| Cylinder Capacity : | 67 Lit ( 45 Kg) |
| No. of Cylinders : | 21 |
|  |  |

## Calculation Report (cable gallary Room)

|  |  |
| --- | --- |
| Zone : | Cable Gallery Room03 |
| Equipment:  | Electrical Panels & Cables |
| Volume : | 29.8 x 10.8 x 2=643 m3 |
| Area Classification: | Class C-electrical fire |
| System :  | Automatic CO2  |
| Code & Standard :  | NFPA 12 |
| Type of System: | Total flooding - Multiple System |
| Type of Fire : | Deep seated |
| Flooding factor :  | 1.33 Kg/ m3 (according to table 5.4.2.1 NFPA 12) |
| Safety Factor:  | 1.1 |
| Discharge Time :  | 7 Minutes (according to 5.5.2.3 NFPA 12) |
| Concentration of CO2:  | 30 % in 2 minutes  |
| Formula : | Total CO2 required = (Vol.) x (Flooding Factor) x ( Safety Factor)  |
| CO2 Required: | 942 Kg |
| Cylinder Capacity : | 67 Lit ( 45 Kg) |
| No. of Cylinders : | 21 |
|  |  |

1. **CONCLUSION**

With the provision of CO2 system the summary of calculated CO2 extinguishing Media demand to protect Rooms in substation building will be as following table:

03

|  |  |  |
| --- | --- | --- |
| **Area** | **Total required** | **No. of Main Cylinders** |
| **Capacitor Bank room** | 171 Kg | 4 |
| **HV Room** | 767 kg | 17 |
| **LV Room** | 925 Kg | 21 |
| **Cable Gallery Room** | 942 Kg | 21 |

Therefore total number of required cylinder for total flooding system (base on biggest volume) in this building **942 Kg (21 Cylinders)** of CO2 gas is needed**.**