## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GNRAL-PEDCO-000-PI-SP-0011_D01 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1607 |  |  | Transmital Date: 26-Nov.-2022
Document Title: SPECIFICATION FOR WELDING OF PLANT PIPING SYSTEM |  |  |  |  | PEDCO Tr. No.:BK-PEDCO-NISOC-0005-PI-TR-1607 |  |  | Transmital Date: 26-Nov.-2022
[5 empty] | CRS No: PEDCO-CRS-BK-GNRAL-PEDCO-000-PI-SP-0011_D01 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | در بند 2.1 صقحه 5 استانداردهاي زير اضاقه شود: IPS-C-PI-270 Construction standard for welding of transportation pipeline IPS-C-PI-290 Construction standard for welding of plant piping systems IPS-M-GM-375 Arc welding equipment and accessories IPS-C-PI-140 Construction standard for transportation pipelines IPS-M-PI-150 Material standard for flanges and fittings IPS-M-PI-190 Material and equipment standard for line pipe IPS-M-PI-110 Material and equipment standard for valves |  | BK-SUR-ENG-PIP-00-01462 | 05-Sep.-2021 | اعمال گردید. |  |  | See Item 21
2 | در بند 2.2 صقحه 5 استانداردهاي زير اضاقه شود: B36.10 Welded and Seamless Wrought Steel Pipe B36.19 Stainless Steel Pipe B31.4 Pipeline Transportation Systems for Liquid Hydrocarbons Section II, Part C Welding Rods, Electrodes, and Filler Metals Section II, Part A Ferrous material specification |  | BK-SUR-ENG-PIP-00-01462 | 05-Sep.-2021 | اعمال گردید. |  |  | See Item 21
3 | در بند 2.2 صقحه 5 استانداردهاي زير اضاقه شود: A833 Indentation Hardness of Metallic Materials by Comparison Hardness Testers E110 Standard Test Method for Indentation Hardness of Metallic Materials by Potable Hardness Testers E140 Standard Hardness Conversion Tables for Metals E562 Boiler and Pressure Vessel Code - Non-Destructive Examination Boiler and Pressure Vessel Code - Welding and Brazing Qualifications G48 Standard Test Methods for Pitting and Crevice Corrosion Resistance of Stainless Steels and Related Alloys by Use of Ferric Chloride Solution |  | BK-SUR-ENG-PIP-00-01462 | 05-Sep.-2021 | اعمال گردید. |  |  | Closed
4 | در بند 2.2 صقحه 5 استانداردهاي زير اضاقه شود: API 1104 Welding of pipelines and related facilities MR 0175 /ISO 15156 Sulfide Stress Cracking Resistant Materials for Oil Field Equipment |  | BK-SUR-ENG-PIP-00-01462 | 05-Sep.-2021 | اعمال گردید. |  |  | Closed
5 | در بند 6 بايستي يه WPQ و PQR هم اشاره شود |  | BK-SUR-ENG-PIP-00-01462 | 05-Sep.-2021 | اعمال گردید. |  |  | Closed
6 | با توجه به اينكه مدارك زير هنوز نهايي نشده است لذا امكان دارد كامنتهاي جديد پس از نهايي شدن مدارك ارسال گردد. 1- MATERIAL SELECTION REPORT & CORROSION STUDY, 2- PIPING MATERIAL SPECIFICATION 3- PIPING WALL THIKNESS CALCULATION |  | BK-SUR-ENG-PIP-00-01462 | 05-Sep.-2021 | ارسال شده اند. |  |  | See Items below
7 | بند 6.2.1.6 حذف گردد. |  | BK-SUR-ENG-PIP-01-06344 | 05-Dec.-2022 | اعمال گردید.
8 | دربند 6.4.1.1، نوع گواهينامه الكترودهاي جوشكاري بايد EN 10204 Type 3.2 باشد. |  | BK-SUR-ENG-PIP-01-06344 | 05-Dec.-2022 | اعمال گردید.
9 | در بند 6.4.1.1 زير بند b، عبارت درج شده در رابطه با 9% Ni Material حذف گردد. |  | BK-SUR-ENG-PIP-01-06344 | 05-Dec.-2022 | اعمال گردید.
10 | در بند 6.4.1.1 زير بند ‍C، به Table2 اشاره شده كه در مدرك وجود ندارد. |  | BK-SUR-ENG-PIP-01-06344 | 05-Dec.-2022 | نامگذاری شد.
11 | دربند6.4.1.1 زير بند f، حذف گردد. |  | BK-SUR-ENG-PIP-01-06344 | 05-Dec.-2022 | اعمال گردید.
12 | در جدول صفحه 10، براي جوشكاري متريال كربن استيل استفاده از الكترودهاي E-XX16 و E309-15, E309-16 حذف گردد |  | BK-SUR-ENG-PIP-01-06344 | 05-Dec.-2022 | اعمال گردید.
13 | استفاده از روش جوشكاري GMAW مجاز نبوده و از بند 8.3.7.1 حذف گردد. |  | BK-SUR-ENG-PIP-01-06344 | 05-Dec.-2022 | اعمال گردید.
14 | در بند 8.5، عبارت "Type certificates for sour service applications are not acceptable." حذف گردد. |  | BK-SUR-ENG-PIP-01-06344 | 05-Dec.-2022 | اعمال گردید.
15 | در بند 8.5، منظور از عبارت "Shielding and purging gases shall be welding grade" مشخص نميباشد. |  | BK-SUR-ENG-PIP-01-06344 | 05-Dec.-2022 | اصلاح گردید.
16 | ويرايش بند 9.2.6.1 قابل قبول نميباشد. |  | BK-SUR-ENG-PIP-01-06344 | 05-Dec.-2022 | اعمال گردید.
17 | در بند 11.6، عبارت "or welder" حذف گردد. |  | BK-SUR-ENG-PIP-01-06344 | 05-Dec.-2022 | به درخواست کارفرمای اصلی بوده است.
18 | حذف بندهاي 12.3.2.7، 12.3.2.9 و 12.3.2.10 قابل قبول نميباشد. |  | BK-SUR-ENG-PIP-01-06344 | 05-Dec.-2022 | جنین سرویس هایی در این پروژه موجود نیست.
19 | بند12.3.2.11 در استاندارد IPS-C-PI-290 موجود بوده و اضافه كردن هر گونه مطلبي با اين شماره بند در مدرك اشتباه ميباشد. مطلب فوق ميتواند با شماره بند 12.3.2.12 اضافه شده و نياز به انجام عمليات تنش زدايي نيز بر اساس الزامات استاندارد NACE MR 0175 براي محيط ترش تعيين گردد. |  | BK-SUR-ENG-PIP-01-06344 | 05-Dec.-2022 | بند فوق مطابق نظر کارفرمای اصلی تایید شده است.
20 | پيوست 1 ضميمه نشده است. |  | BK-SUR-ENG-PIP-01-06344 | 05-Dec.-2022 | به صورت جداگانه به مدرک صمیمه شده است.
21 | ساير نقطه نظرات روي مدرك درج شده است. |  | BK-SUR-ENG-PIP-01-06344 | 05-Dec.-2022 | اعمال گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: F.Amiri M.Torkaman | Signature |  |  |  | Clarified By: S.Faramarzpour | Signature
| Date:05-Dec-2022 |  |  |  |  | Date:05-Dec-2022