## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No:BK-GCS-PEDCO-120-IN-DT-0011 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-2467 |  |  | Transmital Date: 11/5/2023
Document Title: Data Sheets For Control/Regulator valves |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-IN-TR-2467 |  |  | Transmital Date: 11/5/2023
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-IN-DT-0011_D03 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | در مورد تگ LCV-2114 لازم است متریال الزامات NACE را دارا باشد. |  | 1402-2294-358453 | 1402/09/06 | مطابق نظر کارفرمای محترم اصلاح شد.
2 | در مورد تگ های PCV-2315A/B/C در مورد عملکرد آن Actuator در حالت Air Failure و Air Action هر دو حالت Open در نظر گرفته شده است. در این رابطه نیاز به شفاف سازی و رفع ابهام و در صورت نیاز اصلاح دارد. |  | 1402-2294-358453 | 1402/09/06 | مطابق نظر کارفرمای محترم اصلاح شد.
4 | میزان کلاس نشتی در نظر گرفته شده برای تمامی شیرها مطابق Spec نمیباشد و مورد تایید کارفرما نیست. |  | 1402-2294-358453 | 1402/09/06 | مطابق نظر کارفرمای محترم اصلاح شد. |  |  |  | 5.5 | 0.59
[9 empty] | #REF! | #REF!
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required) | [8 empty] | #REF!
#REF!
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor |  |  |  | 1.1
| Commented By: | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: |  |  |  |  | Date: