| # | Clarification Title | Clarification Description (Rev.00) | Conclusion (Rev.00) (VENDOR to Confirm & Consider in the Final Offers) | Clarification Description (Rev.01) | Conclusion (Rev.01) (VENDOR to Confirm & Consider in the Final Offers) | Conclusion (Rev.02-Final) (VENDOR to Confirm & Consider in the Final Offers) |
| --- | --- | --- | --- | --- | --- | --- |
| GENERAL |  |  |  |  |  |  |
|  | Documents Priority | Vendor to confirm that in case of contradiction between this TCL and offer; vendor confirmation of compliance through this technical clarification is governed and shall be followed by vendor after order. In such case offer won’t be considered as basis of any claim after order. | Confirmed | Closed |  |  |
|  | Deviation List | Bidder shall confirm his full compliance to meet all purchaser documents listed and attached to MR, code / standards listed in MR with ref. No. "BK-GCS-PEDCO-120-ME-MR-0006" as well as MR requirements. All deviations shall be listed in project deviation form, attach to this TCL, signed and stamped. Notes: 1-Any exception and deviation from the requirements of MR and the related specifications including referenced codes & standards shall be clearly declared by vendor in writing for purchaser’s approval at bid stage by using of the format included in “Letter Of Conformity” attached to material requisition. Raising no deviation to any single requirement means full compliance of vendor quotation to that requirement. Purchaser has no responsibility to discover deviations or alternatives scattered over the proposal in addition to what proclaimed explicitly in deviation list; hence such deviation (if any) is disregarded and shall not be considered for vendor claim in future. (Vendor to confirm) 2- Bidder shall confirm that all MR attachments listed in MR are available for her for review at bid stage. 3-Considering items 1 & 2, please note that any deviation at detail stage will not be accepted by purchaser. | Confirmed See Deviation list | Please refer to purchaser’s comment on vendor’s DEVIATION LIST | See our replies on document | Meeting conclusion-16.08.2023: Please refer to agreed deviation list. |
|  | Documents Priority | Bidder to confirm his compliance with documents priority stated in MR. Any conflict between the documents shall be notified by bidder to purchaser and resolved by his agreement | Confirmed | Closed |  |  |
|  | Requirement For Documents | Bidder to confirm that documents required after purchase order shall be submitted in accordance with “Vendor documents min. requirement list” attached to the MR. | Confirmed Note: some items are not applicable, moreover for air end made by GHH Rand, only the GHH Rands’ standard documents are available to issue | Closed |  |  |
|  | Documents | Bidder shall provide following documents while bidding: 1- Copy of valid quality system certificate(ISO 9001/2 or 3) 2- Sub- vendors / sub-suppliers list 3- Deviation list with letter of conformity (Refer to item A2 above) 4- Reference and Experience List 5- Joint venture agreement (If any) with any company to design / fabrication of equipment. In case of joint venture ; qualified documents of the company who is part of joint venture shall be also submitted | - Has already sent through TP00 - See TP00 - See TP00 - See TP00 - N/A | Closed |  |  |
|  | Sub-vendors | Bidder to confirm that Sub-Vendors shall be selected from Project’s AVL. | Confirmed | Closed |  |  |
|  | Painting specification | Bidder to confirm that surface preparation and painting of all equipment material including valves , pipes , fittings and everything within the package are in accordance with project painting specification with ref. "BK-GNRAL-PEDCO-000-PI-SP-0006" attached to MR. | Confirmed but for the Air end which GHH Rand will follow his own standard | Closed |  |  |
|  | Specification | Bidder to confirm that Packing, Marking, Preservation and Preparation for Shipment will be done in accordance to the project specification with Doc. No; BK-GNRAL-PEDCO-000-QC-PR-0045 attached to the MR. | Confirmed | Closed |  |  |
|  | Inspection and Test Plan | Inspection and Test Plan / Quality Control Plan and their related inspection level (Witness, Hold, Review and Approval) shall be at least in accordance with MR and all project requirement such as NDT PROCEDURE. Any deviation is not accepted unless otherwise specified in deviation list and approved by Purchaser. | Confirmed but For GHH AIR end, only normally enclosed certificates in GHH rand’s air end for tests are available to issue | ITP will be finalized during PIM | Confirmed | Closed |
|  | Material Certificate | Bidder to confirm that for all pressure parts and those required special consideration or stainless steel as well as for supports the material certificate should be in accordance with EN 10204, 3.1 Material certificate for non-pressure parts shall be in accordance with EN 10204, 2.2 | Confirmed for the main components | Material certificate shall be given for all components | Deviation: only main components | Meeting conclusion-16.08.2023: Material certificated will be submitted by the vendor according to approved ITP in PIM. Closed. |
|  | Scope | Bidder shall confirm the scope of work and supply are fully in accordance with MR and its attachment with considering following items: 1- The consequences of HAZOP and SIL study shall be in vendor scope of supply and work. 2- Participation in technical meeting whenever it is necessary by Purchaser/Client to close engineering document after order is in vendor scope 3- Lifting beams ( Spreader beams) for erection with sling shackle and etc shall be designed and supplied by vendor 4- N2 preservation with pressure regulator, valve & flexible hoses during transportation & 18 months of site storage based on requirements in MR shall be in vendor scope of supply / work. 5- All utility conditions shall be as per document "Basic engineering design data (10‐BD‐00‐PR‐SPC‐0001)". Moreover bidder shall consider utility noted condition as per project design data. If other utility condition is needed, whole required facilities is in vendor scope of work/supply. 6- Anchor bolts | - Confirmed - Confirmed - Confirmed if required - Confirmed - Confirmed - Confirmed | Closed |  |  |
|  | Applied standard | Applied Standards for equipment design, fabrication and test shall be listed | See TP00 For pressure parts, ASME SEC VIII | Noted |  | Meeting conclusion-16.08.2023: All deviation have been submitted by the vendor on deviation list. Closed. |
|  | outdoor installation/ operation under project site conditions | Vendor shall confirm Air Compressor Packages, Dryer Packages and N2 generation package are fully suitable for outdoor installation/operation under project site conditions “Process Basis of Design; BK-GNRAL-PEDCO-000-PR-DB-0001 “without requiring any additional protection. | Confirmed but under shelter | Closed |  |  |
|  | Suitability of utility characteristics available at site | Vendor shall confirm suitability of utility characteristics available at site as per project site conditions “Process Basis of Design; BK-GNRAL-PEDCO-000-PR-DB-0001 “. Supplying all facility for utility distribution and regulation shall be part of the vendor scope. | Confirmed | Closed |  |  |
|  | Warranty | Vendor shall warranty the engineering, materials and workmanship of the equipment/goods. Under this warranty, all materials, parts, and assemblies found to be defective during the guarantee period shall be replaced free of charge by VENDOR. Also, The guarantee period shall be eighteen (18) months from the date of delivery or twelve (12) months from the installation date of each equipment/packages at site. | Confirmed | Closed |  |  |
|  | Project’s MR | Vendor shall follow project’s MR with its Attachments (Revision D01, updated) as Attachment#1 of this TCL. | Noted | Closed |  |  |
| PROCESS |  |  |  |  |  |  |
|  | General comment | Considering that in vendor’s proposal, Compressors of Nitrogen and Air production packages have been considered the same, therefore the proposal shall be totally revised by vendor based on project requirements. | Noted, See TP01 with considering new project requirements |  |  | Meeting conclusion-16.08.2023: On both packages wet air receiver and dryer on vendor scope of work and supply. (On N2 package dryer shall be considered by the vendor.) Closed. |
|  | General comment | Vendor shall follow Latest revision of project documents as Attachment#2 of this TCL. | Confirmed | Closed |  |  |
|  | General comment | Vendor shall be capable to generate nitrogen with purity of 99.9% | 99% is confirmed |  |  | Meeting conclusion-16.08.2023: 99.9% will be followed by the vendor. Closed. |
| MECHANIC |  |  |  |  |  |  |
|  | Document Requirement | Bidder to submit all required documents with tender as per “VDR Form” in the MR. For example below documents: 1-Marked up and Filled out MR scope of supply and works (It shall be signed and stamped) 2-GAD for air compressors, air dryers and nitrogen generators with dimensions, all auxiliaries and heaviest part weight table (by considering air cooler in the package) 3-Cross sectional drawing for compressors with BOM 4-Performance Curves 5-Equipment data sheet in each standard format 6-Utility consumption and load list 7-Spare part list 8-Special tool list 9-P&ID’s dedicated for air compressor, dryer and nitrogen generation packages with all equipment, instruments and lube oil, cooling (if required) and control systems. 10-Noise Data 11-Equipment List on detail for mechanical and other items | - Noted, see revised TP01 - Preliminary drawings are quoted - After PO - See TP01 - Preliminary DSH are in TP - See TP01 - Project spec will be followed - N/A - See TP01 - 85 dBA @ 1 meter with sound canopy - See TP, more details are available APO | 1- Marked up and Filled out MR scope of supply and works (It shall be signed and stamped) - Closed - Closed - Closed - Closed - Closed - Closed - Closed - Closed - Closed - Closed - Closed | Noted, it will be provided at the time of PO | Meeting conclusion-16.08.2023: Project's MR will be signed and stamped by vendor and will be submitted. Closed. |
|  | Major comment | Air compressed supplied for instrument / plant air and nitrogen package shall be separate from each other. 2 Oil-free screw compressors, one in duty operation and one as stand by mode to supply compressed air for instrument and plant air (PK-C-2203 A/B) and 1 Oil-free screw compressor to supply compressed air for nitrogen package (PK-C-2204) shall be considered by vendor as per project requirement. | Confirmed | Closed |  |  |
|  | Interconnecting piping | Design and supply of all interconnecting piping between equipment and all instruments, valves and … on them is in the vendor's scope. Also all between skid piping (including supporting) c/w all instrument and valve on them shall be designed, prefabricated and supplied by vendor. Detailed isometric DWGs shall be submitted for them. Note1: On skid piping to be assembled at vendor's shop. Note2; Out side skid piping to be prefabricated and match marked for site assembling. | Confirmed Final location plan to be decided by PARS COMPRESSOR, | Noted, but it shall be with Hirgan Energy approval | Confirmed | Meeting conclusion-16.08.2023: Vendor confirmed. Closed. |
|  | Heat tracing c/w supports, clips and etc. | Design and supply of heat tracing c/w supports, clips, and other provisions (including panels, heating cables and relevant connectors, electrical cables, junction boxes and thermostats) shall be part of the vendor scope. | N/A | Closed |  |  |
|  | Insulation c/w supports, clips and etc. | Design and supply of insulation c/w supports, clips shall be in vendor’s scope of supply and work. | Confirm to supply loosely | Closed |  |  |
|  | Commissioning spare parts | Pre-commissioning, commissioning and start up spare parts shall be supplied by vendor. Vendor shall confirm to provide all required spare parts as per project spare part list attached to MR. | Confirmed | Closed |  |  |
|  | Two years spare part | Two years spare parts shall be considered in vendor’s base offer as per project spare part list attached to MR. | Confirmed | Closed |  |  |
|  | Capital spare part | Capital spare parts to be considered as optional offer. | Not offered | Closed |  |  |
|  | Vent and Drain of Packages | All vents and drains of the packages to be valved, manifolded and to be routed to the edge of skid. | Confirmed as much as technically possible/applicable | Closed |  |  |
|  | Tie-in | All Tie-in for equipment in the packages shall be equipped will flange and valves | Confirmed for skid’s Tie-ins, Since we have air service, no need isolation valve for all air service equipment during maintenance It just make the package more expensive | Closed |  |  |
|  | Coupling | The coupling shall be of the API671 forged-steel, non-lubricated, flexible-element spacer type. The flexible elements shall be stainless steel metallic disk. | Confirmed | Closed |  |  |
|  | Coupling balancing | Vendor shall specify the coupling balancing grade and balancing method as per API671. | Confirmed | Closed |  |  |
|  | PMI, pickling and passivation | Positive material identification (PMI), pickling and passivation for non-carbon steel material to be included in vendor’s scope of work. | PMI is confirmed for SS material | Closed |  |  |
|  | Skid of the packages | Vendor shall specify number of skid inside package with dimension and weight and preliminary general arrangement. 2-In case of multi skid, please clarify if there is any special procedure for installing and assembling of loose parts. 3-Each skid shall be furnished with 4-point lifting facility and no. two earth lugs located at opposite sides and nameplate made of SS material. 4-Vendor shall specify space required around the skid for maintenance. | See GAD in TP, more details are available after PO | Noted |  | Meeting conclusion-16.08.2023: Closed. |
|  | Inlet condition of compressor | Inlet condition of compressor shall be considered as ambient condition of site as per relevant project specification for Site Condition " Process Basis of Design; BK-GNRAL-PEDCO-000-PR-DB-0001 ". In this regard, air compressor shall be sized for worse case condition of AMB site condition and in any condition the outlet condition as per project duty spec. shall be met. | Confirmed | Closed |  |  |
|  | Lube oil system for air compressor | Lube oil system for bearings of air compressors shall be in vendor’s scope of supply and work and its dedicated P&ID with all auxiliaries such as pumps, oil cooler, reservoir and instruments shall be submitted by vendor in next revision of technical offer. | See TP | Noted |  | Meeting conclusion-16.08.2023: Vendor confirmed. Closed. |
|  | Noise level | If noise enclosure will be required for meeting the project noise limit, it shall be supplied by vendor. Any required facilities for ventilation, fire and gas detection and fire extenuation (if any) for enclosure shall be supplied by vendor. | quoted | Closed |  |  |
|  | Material | Below requirements shall be followed by vendor: -Material ASTM No. to be submitted for compressor and its auxiliaries. -Compressor casing shall be made of cast iron. -Rotors and shafts shall be forged and heat‐treated steel. -Timing gear shall be forged steel. -Gear box housing material shall be C.S. -The instrument air lines and the other air piping shall be galvanized CS based on project requirement “Piping Corrosion study and material selection report; BK-GCS-PEDCO-120-PI-RT-0001”. -Oil pumps casing shall be C.S. -Oil pumps impellers shall be S.S. -Oil cooler, shell shall be C.S and tube shall be SS 316 L -Oil piping shall be SS 316L. | - Air end: GHH rand data only, not possible to change -Galv CS is confirmed -oil pump casing :CS is confirmed -impeller: SS is confirmed -Oil cooler: Aluminum, Manufacturer std -Oil piping: 316 is confirmed | -Closed -Closed -Closed Oil cooler, shell shall be C.S and tube shall be SS 316 L -Oil piping shall be SS 316L. | Oil cooler is plate fin type and made by Aluminum Oil piping 316 L is confirmed | Meeting conclusion-16.08.2023: All items that can not be followed by the vendor will be added to the deviation list. Closed. |
|  | Motor Power | The air compressor motor name plate power (exclusive of the service factor) and after derating shall be more than 110% of maximum required power by air compressor (including all losses such as gear box coupling and etc.) in all cases including PSV setting and etc. Vendor to confirm this requirement. | Confirmed | Closed |  |  |
|  | Applied Standards | Applied Standards for equipment design, fabrication and test shall be listed. ISO10440-2 standard shall be followed by vendor for air compressors. | ISO 10440 part 2 is not applicable due to higher discharge pressure related to this standard, | It Shall Be Mentioned In Deviation List | Already mentioned | Meeting conclusion-16.08.2023: Manufacture STD for compressor is acceptable, all other deviation with project’s requirments will be added to the deviation list. Closed. |
|  | Vendor’s Scope | All vents and drains of the package to be valved, manifolded and to be routed to the edge of skid. | Confirmed as much as applicable | closed |  |  |
|  | Inspection and Test | Test procedures and acceptance criteria will be checked after order with project specifications and related standards. Vendor to confirm to follow project standard and spec. | Manufacturer standard shall be followed | Project Standard and Spec shall be followed by vendor | Noted | Meeting conclusion-16.08.2023: ITP will be finalized during PIM and subjected to the client’s approval. Closed. |
|  | Purchaser’s approval | Regarding technical offer, diameter, dimension and thickness of each equipment will be checked after receiving vendor calculation and data after order and comments in detail shall be followed without cost impact. | Confirmed | Closed |  |  |
|  | Guarantee | Performance, Process and Mechanical Guarantee shall be in the vendor's scope. | Confirmed | Closed |  |  |
|  | Corrosion allowance | For all parts made of carbon steel, corrosion allowance of 3.2 mm shall be considered by vendor. Also vendor shall follow project document “Piping Corrosion study and material selection report; BK-GCS-PEDCO-120-PI-RT-0001” attached to MR. | Confirmed | Closed |  |  |
| MECHANIC FIX |  |  |  |  |  |  |
|  | Fixed equipment mechanical data sheet such as drum | Vendor shall submit relevant mechanical data sheet to define shell/head/nozzle/support type & materials & dimension and designing assumption(J.E. / C.A. & etc.…) | After PO Project specifications will be followed | Noted and closed. |  |  |
|  | Special tools | Special tools for lifting of vessel (i.e. spread bar and skirt bracing if required based vendor’s lifting calculation & relevant bolts/nuts/gasket, Hydraulic bolt tensioning device for bolts greater than 1-1/2” and etc ), shall be considered in vendor’s scope. | Confirmed- if required | Noted and closed. |  |  |
|  | Lifting/Shipping | Shipping calculation, hydrotest stability calculation and relevant drawings & temporary shipping support for all equipment shall be considered in vendor’s scope and submitted for purchaser’s review at detail stage. Please confirm. | Confirmed | Noted and closed. |  |  |
|  | preservation | N2 purging preservation with following conditions shall be consider in vendor’s scope of work & supply (it shall be considered in vendor’s base price not as optional): 1-All opening shall be sealed with a suitable metal cover and gasket. Vessels shall be filled with nitrogen gas at a pressure of 0.5 kg/cm2(g). 2-The equipment shall have a temporary gauge to determine purge pressure. 3-Vendor shall submit N2 filling procedure for purchaser/contractor approval at detail stage. 4-All the required ancillaries such as metal covers, bolts & nuts, gaskets and pressure gauge shall be provided by vendor. Please confirm and modify your offer.( using silica gel instead of N2 purge is not acceptable and shall be omit from your offer.) | Confirmed | Noted and closed. |  |  |
|  | Access for internal loading/unloading | Manhole / hand hole Access for internal loading/unloading of drums | Confirmed | Noted and closed. |  |  |
|  | Nozzle WRC | Local stress analysis of shells under external loads from piping system and attachments (platforms, pipe supports, davit, lifting lug) shall be included in strength calculation. And also, nozzle load shall be considered according to Allowable Nozzle loads on static Equipment ( as per project specification) should be done. Please note that wherever WRC is not applicable FEA shall be done to evaluate local stresses. The original file (native file) of all analysis including all input data and results should be provided by Vendor. Please confirm. | Confirmed | Noted and closed. |  |  |
|  | Loading Data & Anchor Bolt Data | Anchor bolt data (Size, number, B.C.D. ,material ,…) and final loading data including erection, operating and hydro tests shear and moment due to wind and earthquake shall be provided by vendor 1 month after purchase order. Please confirm. | Confirmed (1.5 months) | Noted and closed. |  |  |
|  | PWHT | When stress relieving is required, whole equipment in one piece without removable internals shall be located in the Furnace. All surfaces of flanges shall be protected by vendor due to prevent of damage . Use of direct flame is not approved. | Confirmed | Noted and closed. |  |  |
|  | Referenced documents | Referenced documents, specifications and STDs specified in project MR shall be fully followed by vendor. In addition, for major components within the package, following codes and standards (Latest Editions) shall be considered by vendor: 1- Pressure Vessel Design: ASME BPVC VIII Div. 1 2- Materials: ASME BPVC Sec. II, ASTM 4- Nozzle and External Load Design: WRC 537 5- Wind: ASCE 7 6- Seismic: ASCE 7 | Confirmed | Noted and closed. |  |  |
|  | Material | Material ASTM No. of all package parts including grade and designation shall be specified in equipment datasheets. Furthermore, MDMT, design temp. and pressures shall be specified as well as requirement of impact test and heat treatment. | Confirmed | Noted and closed. |  |  |
|  | Plates | Sliding plates, templates, liners, insert plate & shims (whichever is applicable) are in vendor’s scope of supply. | Confirmed | Noted and closed. |  |  |
|  | Piping Support | All internal piping, valves and fittings with their supports for cooling, sealing, purging, vent, drain and lubrication shall be provided and installed by Vendor. Any auxiliary connection inside B.L shall be flanged type and extended up to the skid's boundary. | Confirmed | Noted and closed. |  |  |
|  | Walk way | In order to provide access to all parts of package, Walkways, platforms, ladders & handrails shall be considered by Vendor | Confirmed as per manufacturer standard | Noted and closed. |  |  |
|  | Seismic/Wind parameters | Vendor shall follow project specifications for Seismic/Wind parameters. Below data shall be considered as minimum requirements: - For seismic: - Code: ASCE 7-10 - Importance Factor: 1. 25 - Site Class: D - Ss = 0.781 - S1 = 1.25 - Fa = 1 - Fv =1.5 - Design wind speed: 120 km/h @10m - Wind Exposure: C | Confirmed | Noted and closed. |  |  |
|  | Grid plate and Grating | The floor shall be covered with grid plate which is suitably supported to prevent excessive deflection. Checkered plate for walkway or other places that end user may use, is not acceptable. Hot dip galvanized grating with four clips per each piece of grating shall be considered for bottom of all walkways. | Confirmed | Noted and closed. |  |  |
|  | Drain nozzle height | Drain valve height shall have enough space for operation and maintenance. | Confirmed | Noted and closed. |  |  |
|  | Passages and all open surfaces | Passages and all open surfaces around the equipment shall be covered with gratings. All the grating penetrations (piping, cables, etc.) shall be bordered with a flat bar which will act as a foot guard. | Confirmed | Noted and closed. |  |  |
|  | Commissioning & Start-up | All items required for commissioning & start-up inside the package shall be supplied by vendor. Necessary quantities of catalysts, cartridges, chemicals, desiccant, molecular sieve, etc., whichever is applicable and required for start-up and initial operation of the package shall be supplied by vendor. | Confirmed | Noted and closed. |  |  |
|  | P&IDs | Purchaser P&IDs to be fully reviewed by vendor and if any extra provisions for control and reliable operation is needed, to be announced by vendor ay bid stage. | Confirmed | Noted and closed. |  |  |
|  | Shop-assembled | The unit shall be shop-assembled to the maximum extent practical to minimize on-site erection work. All skids and equipment that mate directly (without interconnecting piping by the purchaser) shall be trial fit in the vendor’s shop. The vendor shall identify all loose-shipped components requiring field installation in the proposal. | Confirmed | Noted and closed. |  |  |
|  | pressure vessels Specification | All pressure vessels inside the package shall comply with requirements explained in Specification for Welded Pressure Vessel BK-GNRAL-PEDCO-000-ME-SP-0001 attached to material requisition. |  | Noted and closed. |  |  |
|  | Nozzle Flange | All nozzles shall be flanged with Welding neck flanges. For nozzle sizes smaller than 2”, long-welding-neck flanges are required. | Confirmed For nozzle less than 2”, we will us threaded connection as per air service practice inside the package | Noted threaded connection shall not be used in pressurized case. | Some threaded connection to be used for air service only. Considering flange connection has huge impact on size and cost, please clarify | Meeting conclusion-16.08.2023: For compressor manufacturer STD will be followed, for all other components project’s requirements will be followed. For Dryer threaded connection will be used and will be added to the deviation list. PCC: Noted and closed |
|  | Standard Drawings | All details of pressure vessels designed according to ASME BPVC VIII shall follow Standard Drawings for Fixed Equipment attached to this file. | For package, the manufacturer standard For Pressure vessels, this drawings will be followed | Noted and closed. |  |  |
|  | Vessel Support type | Vessels with diameters (OD) and weights greater than 1000 mm and 1200 kg, respectively; are not allowed to be supported by legs. | Confirmed | Noted and closed. |  |  |
|  | Lifting Lug | The skid shall be provided with lifting lugs for a four-point lift. Lifting and transport of the skid, complete with all equipment mounted, shall not permanently distort or otherwise damage the skid or the machinery mounting surfaces. | Lifting method will be as per Package Manufacturer standard | Noted and closed. |  |  |
|  | Overall plot plan | A preliminary overall plot plan shall be added to the next revision by bidder to show approximate arrangement and dimensions of the package. | Confirmed | Noted and closed. |  |  |
|  | Documents | Bidder to submit all required documents with tender as per “RFD Form” in the MR. For example below documents: 1-Marked up and Filled out MR scope of supply and works (It shall be signed and stamped) 2-GA DWG with outline dimensions and weights related to this project 3-A complete Equipment List 4-Noise Data 5-Utility Consumption and load List 6-Spare Part List 7-NDT 8-Hydrostatic test report 9-PWHT report (if required by code) 10-VPIS 11-Marking, packing, shipping procedure 12-Manufacturing & assembly 13-Name plate 14-ITP 15-Painting procedure and sand blast 16-Final book | - Ok - See TP - See TP - 85 dBA @ 1 meter with sound canopy - See TP - As per project list - After PO - After PO - After PO (if required) - After PO - After PO - After PO - After PO - See TP - After PO - After PO | - Noted and closed. - Noted but It shall be signed and stamped. - Noted and closed. - Noted and closed. - Noted and closed. - Noted and closed. - Noted and closed. - Noted and closed. - Noted and closed. - Noted and closed. - Noted and closed. - Noted and closed. - Noted and closed. - Noted and closed. - Noted and closed. - Noted and closed. |  | Meeting conclusion-16.08.2023: Vendor Confirmed. Closed. |
|  | Native file | Bidder to confirm that all native files due to all calculations and drawings shall be submitted for purchaser approval after order. | Confirmed for non-technological items | Noted and closed. |  |  |
|  | Comments on Vendor’s Proposal and its attachments | Please refer to the Attachment #1 of this TCL for Mechanical comments on the offer. | Noted | Noted and closed. |  |  |
| PIPING & MATERIAL |  |  |  |  |  |  |
|  | PMS | Project PMS shall be followed by vendor. | Confirmed | Noted and closed. |  |  |
|  | General arrangement drawing | Air & N2 Package General arrangement drawing shall be issued by vendor. | Confirmed | Noted and closed. |  |  |
|  | 3D model | PDMS 3D model shall be issued by vendor. | Confirmed but the catalogue to be provided by customer |  |  | Meeting conclusion-16.08.2023: Catalogue will be submitted by the Client. Vendor Confirmed to submit PDMS. Closed. |
|  | VPIS | VPIS will be finalized after P.O. (Piping Doc. shall be added to document which listed to document list) | Confirmed |  |  | Noted and closed. |
|  | PLOT PLAN | Please confirm arrangement of packages on plot plan drawing | Noted |  |  | Noted and closed. |
| INSTRUMENT & CONTROL |  |  |  |  |  |  |
|  | Control System Requirements | VENDOR shall follow BK-GNRAL-PEDCO-000-IN-SP-0004 and provide the requirement of type C package for nitrogen package, air compressor and sufficient controller for air dryer in field as mentioned in this document. VENDOR shall comply with all the requirements and mentioned any mismatch in deviation list which is attached to the PMR. As minimum: 1-UCP with redundant CPU/PS dedicated for each train to be provided by vendor. 2-SIL rated loops for protection and trip to be merged inside UCP panel for each train. (redundancy for IO is required) 3- Monitoring of machine protection signals could be also merged inside UCP panel due to vendor design (required transmitters/transducer for temperature/vibration and etc. sensors to be considered for UCP connection otherwise separate panel, at least VMS to be provided. ) | Confirmed MMS is not applicable for this size of machines | LCP is required for each compressors for on/off and commissioning/startup. Microprocessor based LCP is required for dryer. Regarding Machine monitoring at list minimum requirements as per API to be respected (vibration for trip…): As per Specification, ‘’Based on the vendor's experience and recommendation, non‐contacting vibration and axial transducers shall be supplied, installed and calibrated in accordance with API 670’’. Please recheck, since it is vendor responsibility to prepare suitable devices for best performance and safety. | One PLC base common UCP and local (non-PLC) control panel for st/SP of motors will be provided MMS is not applicable for this range of compressors, API-670 could not be followed | Meeting conclusion-16.08.2023: Vendor Confirmed. Closed. Relevant item for vibration will be added to the deviation list. PCC: Added to Deviation list |
|  | Instrumentation | Regarding supplying instrument on datasheet), bidder is requested to consider all instruments mentioned on project datasheet. VENDOR shall follow BK-GNRAL-PEDCO-000-IN-SP-0001 for instrumentation devices and all other details mentioned in this document. VENDOR shall comply with all the requirements and mentioned any mismatch in deviation list which is attached to the PMR. | Confirmed Packages will be mounted in safe area | Noted. |  | Meeting conclusion-16.08.2023: Closed. |
|  | Instrumentation Valves | VENDOR shall follow below documents for valves and other documents as mentioned in these documents. - BK-GNRAL-PEDCO-000-IN-SP-0005 - BK-GNRAL-PEDCO-000-IN-SP-0006 - BK-GNRAL-PEDCO-000-IN-SP-0007 VENDOR shall comply with all the requirements and mentioned any mismatch in deviation list which is attached to the PMR. | Confirmed | Noted. |  | Meeting conclusion-16.08.2023: Closed. |
|  | Connection with MCC | If MCC is supplied by VENDOR all interfaces shall be supplied by VENDOR. Below signals are typically defined in this project to be provided for electrical interfaces: - Start command (2 sec high pulse) - Stop command (2 sec high pulse) - Trip command (low signal for trip) - Run/Stop Status (high signal for run status) - Local/Remote status (high signal for local status) - Tripped on Fault (high signal for fault status) Available for remote control (high signal for available status) | MCC is not in our scope of supply | To be closed by electrical Dep. IRP SHALL BE PROVIDED BY VENDOR. | IRP is not in PCC scope | Meeting conclusion-16.08.2023: Vendor design for packages start and stop via UCP and LP shall be provided by the vendor. PCC: Confirmed |
|  | Cable | VENDOR shall follow BK-GNRAL-PEDCO-000-IN-SP-0010 for cables and all other details mentioned in this document. VENDOR shall comply with all the requirements and mentioned any mismatch in deviation list which is attached to the PMR. | Confirmed | Noted. |  | Meeting conclusion-16.08.2023: Closed. |
|  | Terminals | All terminals shall be screw type. VENDOR shall note that each core/pair/etc. of cable shall be wired to dedicated terminal | Confirmed | Noted. |  | Meeting conclusion-16.08.2023: Closed. |
|  | Panel Dimension | VENDOR shall specify the estimated number and dimension of panels. | After PO | Noted. |  | Meeting conclusion-16.08.2023: Closed. |
|  | Required Power | VENDOR shall specify the estimated power required (non-UPS and UPS) | See The load list in TP | Noted. |  | Meeting conclusion-16.08.2023: Closed. |
|  | Special Tools | VENDOR shall supply all special tools for compressor and axillary devices. This is included the special cables (not mentioned in BK-GNRAL-PEDCO-000-IN-SP-0010), MODBUS sockets, software and etc. The list shall be provided separately. | N/A | Noted. |  | Meeting conclusion-16.08.2023: Closed. |
|  | Protection Instruments | The protective instruments shall be according to API-670. VENDOR shall comply with all the requirements and mentioned any mismatch in deviation list which is attached to the PMR. | N/A | As per project specification: 5.4.6.2 (Mod.) Based on the vendor's experience and recommendation, non‐contacting vibration and axial transducers shall be supplied, installed and calibrated in accordance with API 670. | N/A for this range of compressors | Meeting conclusion-16.08.2023: Refer to Instrument item 1. Closed. |
|  | Software | VENDOR shall supply all the software (including the passwords, licenses and program sources). The programs shall be supplied with all tags, descriptions and etc. The software programs shall be installed on engineering laptops and also supplied on CD/DVD. | Confirmed | Noted. |  |  |
|  | Sequence controller | VENDOR shall clearly specify the scenario for sequence controlling of compressor and dryer also nitrogen package, the interfaces signals, required hardware (e.g. panels, if any) and additional control or on/off valves. | See TP | OPEN-To be updated as per project request in item nos. 1و15 | Please clarify | Meeting conclusion-16.08.2023: Preliminary control block diagram will be revised. Closed. |
|  | Start-up | VENDOR shall clearly state the start-up sequence. It shall be mentioned if any additional instrument or valve is required. Also, the interface signals shall be mentioned (if any) | See TP | OPEN_ be updated as per project request in item nos. 1و15 | Please clarify | Meeting conclusion-16.08.2023: Preliminary control block diagram will be revised. Closed. |
|  | Spare part | VENDOR shall supply all commissioning/ 2 years spare part as per NISOC procedure, attached to PMR | Confirmed | OPEN- To be updated as per project request in item nos. 1, 15. Spare part for UCP shall be considered. | Noted but it has huge cost impact | Meeting conclusion-16.08.2023: Spare part will be submitted according to project requirements. Closed. |
|  | NEW ITEM |  |  | As per project specification, PLC based UCP (for control and safety) dedicated to each compressor is requested for both package (N2 and air): -One PLC based UCP for each compressor (totally 2.Nos. located on control room) for Air compressor package (type C). -One PLC based UCP for nitrogen package (located on control room) (type C). -Redundancy for CPU/power supply /critical and safety I/Os and communication link to be considered in each UCP. Separate SIL rated system for ESD signals (could be relay based ESD part inside UCP) shall be considered in parallel as safety back up logic. - LCP is required for each compressors for on/off and commissioning/startup and gauge boarding. -Project Spec to be respected for packages type C. -Microprocessor based LCP is required for each dryer. -Regarding Machine monitoring at list minimum requirements as per API to be respected (vibration for trip…) | Please clearly clarify if only S7-400 FH is required? Because it has huge cost and time impact. Also we could provide sequence control through above remote UCP or local panel, please clarify MMS is not applicable | Meeting conclusion-16.08.2023: Refer to IN-12. Closed. |
|  | New Item |  |  | Since MCC is supplied by VENDOR : - Interface signals between MCC and UCP (VIA IRP) and LCP shall be considered in vendor scope. Below signals are typically defined in this project: - Start command - Stop command - Trip command - Run/Stop Status - Local/Remote status Fault status | MCC is not in our scope but we will provide local power distribution panel. Moreover, below signals are typically defined in LCP: Start push buttons Stop push buttons Run/Stop lamp Status Following items will be considered in UCP (remote): Local/Remote selector switch (software key) | Meeting conclusion-16.08.2023: Refer to IN-1. Closed. |
|  | New Item |  |  | Project Instrument Hook UP drawing (BK-GCS-PEDCO-120-IN-DG-0002), Shall be Followed by vendor | Confirmed for beyond the compressor skid. It means it will be followed for dryer, N2 package and interconnecting. | Meeting conclusion-16.08.2023: Closed. |
| SAFETY |  |  |  |  |  |  |
|  | Noise Level | Noise levels of items should not exceed 85 dbA @ 1m. | Confirmed | Closed |  |  |
| ELECTRICAL |  |  |  |  |  |  |
|  | Specification | All electrical equipment shall comply with electrical references & standard that mentioned on material requisition. IPS-E-EL-100 (1), IPS-M-EL-131 (2) & IPS-M-PM-290(2). | Confirmed | Closed |  |  |
|  | Vendor Scope of Work | All documents related to electrical equipment shall be submitted by vendor such as preliminary load list, electrical equipment list, motor data sheet, motor outline drawing & etc. | Confirmed | Closed |  |  |
|  | Vendor Scope of Work | Vendor list & sub vendor list of manufacture shall be according to project AVL. | Confirmed | Closed |  |  |
|  | Vendor Scope of Work | The cable from switchgear to package panel is by client, but the cable in the package form panel to each equipment is by vendor. In other word, from client point of view, there is only one load which assumed the power demand of package is the total load. This note is valid for both nitrogen & air package. (Tie in between client & vendor is main panel). | Confirmed | mentioned standards have been attached |  | Meeting conclusion-16.08.2023: 3 feeders will be considered on the battery limit of vendor by the contractor. Vendor Confirmed. Closed. |
|  | Vendor Scope of Work | According to item 4, the total electrical load is required not each one separately. | Confirmed | Closed |  |  |
|  | Vendor Scope of Work | Since the power & control cables in the skid is by vendor, therefore the cable list in the package shall be according to “BK-GNRAL-PEDCO-000-EL-SP-0014”. Interconnection in the skid is by vendor. | Confirmed | Closed |  |  |
|  | Vendor Scope of Work | Supplier shall design the routing of the power & control cable inside package. | Confirmed | More information, The cable & power from switchgear (400V, 3Phase & 50Hz), to main package panel (in field) is by contractor, but the cable in the package from main panel to each equipment (on skid) is by vendor. In other word, from contractor point of view, there are 3 below loads: - Instrument & Plant Air Package (PK-C-2203A) - Instrument & Plant Air Package (PK-C-2203B) - Nitrogen Package (PK-2204) (Tie in between contractor & vendor is main panel which panel will be provided by vendor). Therefore the total power demand shall be specified by vendor. | Noted, We will receive 3 pairs of power cable only from customer | Meeting conclusion-16.08.2023: 3 feeders will be considered on the battery limit of vendor by the contractor. Vendor Confirmed. Closed. |
|  | Vendor Scope of Work | If AC UPS or DC UPS & batteries are required, vendor shall provide all necessary documents (such as calculation, list etc.) & supply required equipment according to purchaser standards. | Confirmed | Closed |  |  |
|  | Spare Part | A complete set of spare parts for commissioning shall be supplied for each motor. | Confirmed | Closed |  |  |
|  | Test & Inspection | The equipment shall be factory tested. Certified copies of test reports shall be submitted to the purchaser. | Confirmed | Closed |  |  |
|  | Vendor Scope of Work | Data sheet & Specification of LV induction motor have been attached. Please follow them. | Confirmed | Closed |  |  |
|  | Deviation | Deviation of power cables is not acceptable & according to item 6, cables shall be XLPE & armored. | Confirmed, Deviation is withdrawn | Closed |  |  |
|  | Vendor Scope of Work | New: The engineering & procurement of package shall be according to “BK-GNRAL-PEDCO-000-EL-SP-0011”. | Confirmed |  |  | Meeting conclusion-16.08.2023: Vendor confirmed. Closed. |
|  | Vendor Scope of Work | New: The method of start & stop of air compressor & interlock with other equipment shall be specified. | See TP and PID |  |  | Meeting conclusion-16.08.2023: All relevant items will be considered on Cause and effect and control philosophy by the vendor. Closed. |
|  | Vendor Scope of Work | New: The method of start & stop of nitrogen package & interlock between main motor & auxiliary loads of N2 package shall be specified. | See TP/PID |  |  | Meeting conclusion-16.08.2023: Closed. |
|  | Vendor Scope of Work | I/O List shall be issued by vendor. | After PO |  |  | Meeting conclusion-16.08.2023: Closed. |
| STRUCTURE |  |  |  |  |  |  |
|  | Earthquake load | Use ASCE7-10 for earthquake load | Confirmed | Closed |  |  |
|  | Anchor bolt | The type & location of the anchor bolt should be provided. | Confirmed | Closed |  |  |
|  | Skid | The exact dimensions & size of the skid and the proper alignment under the skid should be determined. | Confirmed | Closed |  |  |
|  | Loads and center mass | The static & dynamic loads of the equipment and the level of the center mass the device should be determined. | Confirmed | Closed |  |  |