## Cover
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR PRESSURE / DIFF. PRESSURE TRANSMITTER
شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه
9184 – 073 - 053 |  |  | BK |  | GCS | PEDCO | 120 |  | IN | DT | 0004 | D03
طرح نگهداشت و افزایش تولید 27 مخزن
DATA SHEETS FOR PRESSURE / DIFF. PRESSURE TRANSMITTER نگهداشت و افزایش تولید میدان نفتی بینک
D03 |  | FEB.2024 |  | AFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | S.Faramarzpour
D02 |  | AUG.2023 |  | AFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
D01 |  | MAR.2023 |  | IFA |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
D00 |  | APR.2022 |  | IFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: | CLIENT Approval
Class: 1 |  |  |  | CLIENT Doc. Number: F9Z-708925
status: | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved

## REVISION
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR PRESSURE / DIFF. PRESSURE TRANSMITTER
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه
9184 – 073 - 053 |  |  | BK | GCS |  | PEDCO | 120 | IN | DT | 0004 |  | D03
REVISION RECORD SHEET
Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D01 | D02 | D03 | D04
1 | X | X | X |  | X |  |  |  | 65
2 | X | X | X |  | X |  |  |  | 66
3 | X | X | [6 empty] | 67
4 | X | X | [6 empty] | 68
5 | X | X | [6 empty] | 69
6 | X | X | X |  | X |  |  |  | 70
7 | X | X | [6 empty] | 71
8 | X | X | X |  | X |  |  |  | 72
9 | X | X | X |  | X |  |  |  | 73
10 | [8 empty] | 74
11 |  |  | X |  | X |  |  |  | 75
12 | [8 empty] | 76
13 | [8 empty] | 77
14 | [8 empty] | 78
15 | [8 empty] | 79
16 | [8 empty] | 80
17 | [8 empty] | 81
18 | [8 empty] | 82
19 | [8 empty] | 83
20 | [8 empty] | 84
21 | [8 empty] | 85
22 | [8 empty] | 86
23 | [8 empty] | 87
24 | [8 empty] | 88
25 | [8 empty] | 89
26 | [8 empty] | 90
27 | [8 empty] | 91
28 | [8 empty] | 92
29 | [8 empty] | 93
30 | [8 empty] | 94
31 | [8 empty] | 95
32 | [8 empty] | 96
33 | [8 empty] | 97
34 | [8 empty] | 98
35 | [8 empty] | 99
36 | [8 empty] | 100
37 | [8 empty] | 101
38 | [8 empty] | 102
39 | [8 empty] | 103
40 | [8 empty] | 104
41 | [8 empty] | 105
42 | [8 empty] | 106
43 | [8 empty] | 107
44 | [8 empty] | 108
45 | [8 empty] | 109
46 | [8 empty] | 110
47 | [8 empty] | 111
48 | [8 empty] | 112
49 | [8 empty] | 113
50 | [8 empty] | 114
51 | [8 empty] | 115
52 | [8 empty] | 116
53 | [8 empty] | 117
54 | [8 empty] | 118
55 | [8 empty] | 119
56 | [8 empty] | 120
57 | [8 empty] | 121
58 | [8 empty] | 122
59 | [8 empty] | 123
60 | [8 empty] | 124
61 | [8 empty] | 125
62 | [8 empty] | 126
63 | [8 empty] | 127
64 | [8 empty] | 128

## REFERENCE
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR PRESSURE / DIFF. PRESSURE TRANSMITTER
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
9184 – 073 - 053 |  |  | BK | GCS | PEDCO | 120 | IN | DT | 0004 | D03
REFERENCE DOCUMENTS :
|  | Specification For Instrumentation | [6 empty] | BK-GNRAL-PEDCO-000-IN-SP-0001
|  | Process Basis Of Design | [6 empty] | BK-GNRAL-PEDCO-000-PR-DB-0001
|  | Piping Material Specification | [6 empty] | BK-GCS-PEDCO-120-PI-SP-0001
|  | Hazardous Area Classification Layout | [6 empty] | BK-GCS-PEDCO-120-SA-PY-0002
|  | Instrument & Control System Design Criteria | [6 empty] | BK-GCS-PEDCO-120-IN-DC-0002
|  | Symbol & Legend For PFD and P&ID | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0001
|  | P&ID - Gas Compression Inlet Gas Pipeline (Binak) | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0002
|  | P&ID - Gas Compression Inlet Gas Pipeline (Golkhari) | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0003
|  | P&ID - Slug Catcher System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0004
|  | P&ID - Gas Compression Inlet Knock Out Drum | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0005
|  | P&ID - 1st Stage Gas Compression Suction Drums | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0006
|  | P&ID - 1st Stage Gas Compression Compressors | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0007
|  | P&ID - 1st Stage Gas Compression Air Coolers | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0008
|  | P&ID - 2nd Stage Gas Compression Suction Drums | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0009
|  | P&ID - 2nd Stage Gas Compression Compressors | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0010
|  | P&ID - 2nd Stage Gas Compression Air Coolers | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0011
|  | P&ID - 2nd Stage Gas Compression Discharge Drum | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0012
|  | P&ID - Gas Compression Dehydration Package | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0013
|  | P&ID - Lean Glycol Storage Tank | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0014
|  | P&ID - Instrument & Plant Air System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0015
|  | P&ID - Nitrogen Generation System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0016
|  | P&ID - Close Drain System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0017
|  | P&ID - Corrosion Inhibitor Package | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0018
|  | P&ID - Methanol Injection Package | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0019
|  | P&ID - LP Flare System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0020
|  | P&ID - Oily Water Sewer | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0021
|  | P&ID - Fuel Gas System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0022
|  | P&ID - Diesel Oil System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0023
|  | P&ID - Potable Water System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0024
|  | P&ID - Glycol Sump Drum | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0025
|  | P&ID - Fire Water Network | [6 empty] | BK-GCS-PEDCO-120-SA-PI-0001
|  | P&ID - Total Flooding System For Extension of Existing Elect. Building | [6 empty] | BK-GCS-PEDCO-120-SA-PI-0002

## Notes
NISOC |  |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR PRESSURE / DIFF. PRESSURE TRANSMITTER
شماره پیمان: |  |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
9184 – 073 - 053 |  |  |  |  | BK | GCS | PEDCO | 120 | IN | DT | 0004 | D03
GENERAL NOTES:
1 - Zero and span adjustment shall be included and be accessible from outside in addition to Hand Held Communicator.
2 - Over range protection (at least 1.3 of full scale) shall be considered.
3 - 304 Stainless Steel name plate shall be supplied for all instruments specified in this document. Following details shall be engraved on them:
• Tag Number • Range Limit • Manufacture Model • Manufacturer’s Name • Serial Number • Supply Voltage • Output Signal • Hazardous Area Certification
4 - Painting shall be in accordance with manufacturer standard.
5 - VTA : Vendor To Advise
6 - N/A : Not Applicable
7 - Environmental condition for field instrumentation of Binak Oilfield shall be considered as per the followings:
Maximum ambient temperature: 50 (°C) (Note *) Minimum ambient temperature: 5 (°C) (Note *) Maximum steel surface exposed to sun: 85 (°C) (Note *) Maximum summer dry bulb: 50 (°C) (Note *) DB/RH for Summer HVAC Design: 41 °C / 61 % (Note **/ Note***) DB FOR Winter HVAC Design: 6 °C (Note **) * Refer to “Process Basis Of Design Doc No.: BK-GNRAL-PEDCO-000-PR-DB-0001". ** Refer to " HVAC Design Criteria; N.I.O.C. NO.: F-1-B-422001". *** Refer to “NISOC Meteorological Studies Report".
Relative Humidity:
• Maximum Design relative humidity (%): 100 • Minimum Design relative humidity (%): 0
8 - Material Test Certificate and calibration Certificate for all transmitters to be submitted by Vendor.
9 - This Data Sheets Has Been Prepared As Per Below Standard :
• IPS-M-IN-110 Material and equipment standard for pressure instruments • IPS-E-IN-110 Engineering standard for pressure instruments • IPS-C-IN-110 Construction standard for pressure instruments
10 - Material Test Certificate and calibration Certificate for all transmitters to be submitted by Vendor.
11 - All PT/DPT shall meet the following Radio Frequency Immunity (RFI) requirements that shall be tested at the acceptance test stage. Basic reference standard is IEC 60801 (part 3) for design and manufacturing considerations.
12 - Tropicalization shall be applied to protect electrical circuits and electronic cards from being degraded by corrosion and/or fungus growth.

## DCS PT
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR PRESSURE / DIFF. PRESSURE TRANSMITTER
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده |  | تسهیلات | رشته | نوع مدرک |  | سریال | نسخه
9184 – 073 - 053 |  |  |  | BK | GCS | PEDCO |  | 120 | IN | DT |  | 0004 | D03
DCS PRESSURE TRANSMITTER
GENERAL DATA |  | 1 | Tag No. | [7 empty] | SEE NEXT PAGE
|  | 2 | P&ID No. | [7 empty] | SEE NEXT PAGE
|  | 3 | Equipment No. / Line No. | [7 empty] | SEE NEXT PAGE
|  | 4 | Area Classification | [7 empty] | ZONE 2, IIB T4
|  | 5 | Piping Class | [7 empty] | SEE NEXT PAGE
OPERATING CONDITIONS |  | 6 | Fluid | [7 empty] | SEE NEXT PAGE
|  | 7 | Phase | [7 empty] | SEE NEXT PAGE
|  | 8 | Operating Pressure | [5 empty] | (bar-g) |  | SEE NEXT PAGE
|  | 9 | Design Pressure | [5 empty] | (bar-g) |  | SEE NEXT PAGE
|  | 10 | Operating Temperature | [5 empty] | (°C) |  | SEE NEXT PAGE
|  | 11 | Design Temperature | [5 empty] | (°C) |  | SEE NEXT PAGE
TRANSMITTER |  | 12 | Element Type | [5 empty] | (NOTE 4) |  | SEE NEXT PAGE
|  | 13 | Size of Process Connection | [7 empty] | SEE NEXT PAGE
|  | 14 | Rating of Process Connection | [7 empty] | SEE NEXT PAGE
|  | 15 | Element Material | [7 empty] | SEE NEXT PAGE
|  | 16 | Enclosure Material | [7 empty] | Die cast aluminium
|  | 17 | Instrument Range | [7 empty] | SEE NEXT PAGE
|  | 18 | Power Supply | [7 empty] | 24 VDC-Loop powered
|  | 19 | Output Signal | [7 empty] | 4-20mA
|  | 20 | Communication Protocol | [7 empty] | SMART HART(4-20mA)
|  | 21 | Electrical Connection | [7 empty] | 2* ISO M20 x 1.5
|  | 22 | Electrical Certification | [7 empty] | EEx "i"
|  | 23 | Ingress Protection | [7 empty] | IP-65 as minimum
|  | 24 | Accuracy | [7 empty] | 0.1% F.S
|  | 25 | Repeatability | [7 empty] | +/- 0.1% or better
|  | 26 | Span and Zero Adjustment | [7 empty] | Required
|  | 27 | Over Range Protection | [7 empty] | Yes
DIAPHRAGM SEAL |  | 28 | Type | [7 empty] | N/A
|  | 29 | Size (In) | [7 empty] | N/A
|  | 30 | Fill Fluid | [7 empty] | N/A
|  | 31 | Diaphragm Material | [7 empty] | N/A
|  | 32 | Capillary Material | [7 empty] | N/A
|  | 33 | Capillary Length | [7 empty] | N/A
OPTIONS |  | 34 | Integral Indicator |  |  |  | Display Unit |  |  |  | Required |  |  |  | Bar-g
|  | 35 | Mounting Brackets | [7 empty] | Required, 2" Support Pipe (Note 3)
|  | 36 | Manifold |  |  |  | Body Material |  |  |  | 2 Way Block & Bleed Manifold |  |  |  | 316 S.S.L
|  | 37 | Connection | [7 empty] | 1/2 " NPT (Note 2,5,7)
|  | 38 | Manifold Model |  |  |  | Manifold Manufacturer |  |  |  | - |  |  |  | VTA
|  | 39 | Integral Indicator Style | [7 empty] | LCD TYPE
|  | 40 | NACE Requirements | [7 empty] | SEE NEXT PAGE
PURCHASING DATA |  | 41 | Model |  |  |  | Manufacturer |  |  |  | Will Be Finilized Later |  |  | Will Be Finilized Later
|  | 42 | Supplier |  |  |  | Order |  |  |  | Will Be Finilized Later |  |  | Will Be Finilized Later
NOTES : | VTA : VENDOR TO ADVISE
1 : Wetted part shall be according to NACE MR0175/ISO 15156 as per list.
2 : All manifolds shall be suitable for connection to transmitter and process line.
3 : Mounting Yoke, U-bolt , Nuts and all accessories shall be supplied by vendor.
4 : Suitable element type to be confirmed by vendor.
5 : For manifold rating, refer to "Piping Material Specification Doc No.: BK-GCS-PEDCO-120-PI-SP-0001
6 : Burn out direction shall be capable to set.
7 : Instrument/Process connection to be as bellows:
- Process Connection:1/2" NPTF
- Instrument Connection: 1/2" NPTF
- Drain Connection: 1/4" NPTF

## DCS PT LIST
NISOC |  |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR PRESSURE / DIFF. PRESSURE TRANSMITTER
شماره پیمان: |  |  |  |  | پروژه | بسته کاری | صادرکننده |  |  | تسهیلات | رشته | نوع مدرک |  | سریال |  | نسخه
9184 – 073 - 053 |  |  |  |  | BK | GCS | PEDCO |  |  | 120 | IN | DT |  | 0004 |  | D03
DCS PRESSURE TRANSMITTERS
Rev. | Item No. | Tag No. | SYSTEM/SIL Rated | P&ID No. |  | Equipment No. / Line No. |  | Piping Class/ Rating | Manifold Rating | Fluid | Phase | Design Pressure (Barg) | Operating Pressure (Barg) | Design Temp. (°C) | Operating Temp. (°C) | Calibration Range (Barg) (Note 2) | Instrument Range (Barg) (Note 1) | Element Type | Element Material | Size of Process Connection / rate of process connection | Over Range protection (Note 2) | Manifold Requirement (Block & Bleed) | NACE | Model | Remark
D03 | 1 | PIT-2102 | DCS | BK-GCS-PEDCO-120-PR-PI-0002 |  | GAS-111-0001-AN07-6"-PT |  | AN07 / 150# | 6000# | PROCESS GAS | GAS | 18.2 | 7.5 | 85 | 46.11/26.67 | 0-15 | VTA | Diaphragm | SS 316L | 1/2" NPT / 6000# | up to1.3 times design pressure | 2 Way Manifold | YES | VTA
D03 | 2 | PIT-2104 | DCS | BK-GCS-PEDCO-120-PR-PI-0003 |  | GAS-111-0001-FN07-8"-PT |  | FN07 / 600# | 6000# | PROCESS GAS | GAS | 90 | 7.5 | 175 | 32/15.5 | 0-15 | VTA | Diaphragm | SS 316L | 1/2" NPT / 6000# | up to1.3 times design pressure | 2 Way Manifold | YES | VTA
D03 | 3 | PIT-2112 | DCS | BK-GCS-PEDCO-120-PR-PI-0004 (1 of 2) |  | V-2104 |  | - / 150# | 6000# | PROCESS GAS | GAS | FV/9 | 5.5 | 85 | 32/15.5 | 0-10 | VTA | Diaphragm | SS 316L | 1/2" NPT / 6000# | up to1.3 times design pressure | 2 Way Manifold | YES | VTA
D03 | 4 | PIT-2114 | DCS/SIL 1 | BK-GCS-PEDCO-120-PR-PI-0004 (2 of 2) |  | CDH-112-0015-CN07-4"-PT |  | CN07 / 300# | 3000# | WATER+HYDROCARBON | LIQUID | 47.7 | 18.5 | 155 | 5/50 | 0-36 | VTA | Diaphragm | SS 316L | 1/2" NPT / 3000# | up to1.3 times design pressure | 2 Way Manifold | YES | VTA
D03 | 5 | PIT-2117 | DCS | BK-GCS-PEDCO-120-PR-PI-0005 |  | V-2105 |  | - / 150# | 6000# | PROCESS GAS | GAS | FV/9 | 5.3 | 85 | 37.17/19.23 | 0-10 | VTA | Diaphragm | SS 316L | 1/2" NPT / 6000# | up to1.3 times design pressure | 2 Way Manifold | YES | VTA
D03 | 6 | PIT-2121A | DCS | BK-GCS-PEDCO-120-PR-PI-0006 (1 of 3) |  | GAS-111-0031A-CN05-8"-ET |  | CN05 / 300# | 3000# | PROCESS GAS | GAS | 47.7 | 4.9 | 155 | 36.78/18.88 | 0-9 | VTA | Diaphragm | SS 316L | 1/2" NPT / 3000# | up to1.3 times design pressure | 2 Way Manifold | YES | VTA
D03 | 7 | PIT-2121B | DCS | BK-GCS-PEDCO-120-PR-PI-0006 (2 of 3) |  | GAS-111-0031A-CN05-8"-ET |  | CN05 / 300# | 3000# | PROCESS GAS | GAS | 47.7 | 4.9 | 155 | 36.78/18.88 | 0-9 | VTA | Diaphragm | SS 316L | 1/2" NPT / 3000# | up to1.3 times design pressure | 2 Way Manifold | YES | VTA
D03 | 8 | PIT-2121C | DCS | BK-GCS-PEDCO-120-PR-PI-0006 (3 of 3) |  | GAS-111-0031A-CN05-8"-ET |  | CN05 / 300# | 3000# | PROCESS GAS | GAS | 47.7 | 4.9 | 155 | 36.78/18.88 | 0-9 | VTA | Diaphragm | SS 316L | 1/2" NPT / 3000# | up to1.3 times design pressure | 2 Way Manifold | YES | VTA
D03 | 9 | PIT-2135A | DCS | BK-GCS-PEDCO-120-PR-PI-0011 (1 of 3) |  | GAS-111-0057A-FS00-4"-NP |  | FS00 / 600# | 3000# | PROCESS GAS | GAS | 62.4 | 54.1 | 175 | 60 | 0-100 | VTA | Diaphragm | SS 316L | 1/2" NPT / 3000# | up to1.3 times design pressure | 2 Way Manifold | YES | VTA
D03 | 10 | PIT-2135B | DCS | BK-GCS-PEDCO-120-PR-PI-0011 (2 of 3) |  | GAS-111-0057B-FS00-4"-NP |  | FS00 / 600# | 3000# | PROCESS GAS | GAS | 62.4 | 54.1 | 175 | 60 | 0-100 | VTA | Diaphragm | SS 316L | 1/2" NPT / 3000# | up to1.3 times design pressure | 2 Way Manifold | YES | VTA
D03 | 11 | PIT-2135C | DCS | BK-GCS-PEDCO-120-PR-PI-0011 (3 of 3) |  | GAS-111-0057C-FS00-4"-NP |  | FS00 / 600# | 3000# | PROCESS GAS | GAS | 62.4 | 54.1 | 175 | 60 | 0-100 | VTA | Diaphragm | SS 316L | 1/2" NPT / 3000# | up to1.3 times design pressure | 2 Way Manifold | YES | VTA
D03 | 12 | PIT-2151 | DCS | BK-GCS-PEDCO-120-PR-PI-0013 (1 of 3) |  | GAS-111-0179-FN05-6"-PT |  | FN05 / 600# | 6000# | PROCESS GAS | GAS | 90 | 52.92 | 175 | 60 | 0-100 | VTA | Diaphragm | SS 316L | 1/2" NPT / 6000# | up to1.3 times design pressure | 2 Way Manifold | YES | VTA
D03 | 13 | PIT-2161 | DCS | BK-GCS-PEDCO-120-PR-PI-0014 |  | TK-2102 |  | - / 150# | 3000# | LEAN GLYCOL | LIQUID | ATM+FULL OF WATER+160mbarg/-7mbarg | 0.01 | 85 | AMB | 0-0.2 | VTA | Diaphragm | SS 316L | 1/2" NPT / 3000# | up to1.3 times design pressure | 2 Way Manifold | NO | VTA
D03 | 14 | PIT-2201 | DCS | BK-GCS-PEDCO-120-PR-PI-0015 (1 of 2) |  | PLA-112-0010-AN04-1 1/2"-PT |  | AN04 / 150# | 3000# | PLANT AIR | GAS | 18.2 | 9 | 90 | 65 | 0-18 | VTA | Diaphragm | SS 316L | 1/2" NPT / 3000# | up to1.3 times design pressure | 2 Way Manifold | NO | VTA
D03 | 15 | PIT-2203 | DCS | BK-GCS-PEDCO-120-PR-PI-0015 (2 of 2) |  | ISA-112-0012-AZ00-2"-NP |  | AZ00 / 150# | 3000# | INSTRUMENT AIR | GAS | 18.2 | 8 | 85 | 65 | 0-16 | VTA | Diaphragm | SS 316L | 1/2" NPT / 3000# | up to1.3 times design pressure | 2 Way Manifold | NO | VTA
D03 | 16 | PIT-2213 | DCS | BK-GCS-PEDCO-120-PR-PI-0016 |  | NIT-112-0024-AN01-2"-PT |  | AN01 / 150# | 3000# | NITROGEN RECEIVER | GAS | 18.2 | 7.5 | 85 | 60 | 0-15 | VTA | Diaphragm | SS 316L | 1/2" NPT / 3000# | up to1.3 times design pressure | 2 Way Manifold | NO | VTA
D03 | 17 | PIT-2214 | DCS | BK-GCS-PEDCO-120-PR-PI-0016 |  | NIT-112-0024-AN01-2"-PT |  | AN01 / 150# | 3000# | NITROGEN RECEIVER | GAS | 18.2 | 7.5 | 85 | 60 | 0-15 | VTA | Diaphragm | SS 316L | 1/2" NPT / 3000# | up to1.3 times design pressure | 2 Way Manifold | NO | VTA
D03 | 18 | PIT-2252 | DCS | BK-GCS-PEDCO-120-PR-PI-0020 (2 of 3) |  | FL-112-0004-AN07-12"-PT |  | AN07 / 150# | 6000# | FLARE GAS | GAS | F.V/6 | 0.5 | 85 | 36 ~ 272 | 0-1 | VTA | Diaphragm | SS 316L | 1/2" NPT / 6000# | up to1.3 times design pressure | 2 Way Manifold | YES | VTA
D03 | 19 | PIT-2272 | DCS | BK-GCS-PEDCO-120-PR-PI-0022 |  | FLG-112-0006-AN07-3"-PT |  | AN07 / 150# | 6000# | FUEL GAS | GAS | 18.2 | 4.9 | 85 | 19/37 | 0-9 | VTA | Diaphragm | SS 316L | 1/2" NPT / 6000# | up to1.3 times design pressure | 2 Way Manifold | YES | VTA
D03 | 20 | PIT-2271 | DCS | BK-GCS-PEDCO-120-PR-PI-0022 |  | FLG-112-0110-AN07-4"-PT |  | AN07 / 150# | 6000# | FUEL GAS | GAS | 18.2 | 4.9 | 85 | 19/37 | 0-9 | VTA | Diaphragm | SS 316L | 1/2" NPT / 6000# | up to1.3 times design pressure | 2 Way Manifold | YES | VTA
D03 | 21 | PIT-2191 | DCS | BK-GCS-PEDCO-120-PR-PI-0025 |  | V-2107 |  | - / 150# | 3000# | GLYCOL SUMP DRUM | LIQUID | F.V/3.5 | 0.01 | 85 | AMB | 0-0.2 | VTA | Diaphragm | SS 316L | 1/2" NPT / 3000# | up to1.3 times design pressure | 2 Way Manifold | NO | VTA
D03 | 22 | PIT-2301 | DCS | BK-GCS-PEDCO-120-SA-PI-0001 (2 of 2) |  | FWA-113-0025-AN04-12"-PT |  | AN04 / 150# | 3000# | FIRE WATER | LIQUID | 13.9 | 10.4 | 85 | AMB | 0-22 | VTA | Diaphragm | SS 316L | 1/2" NPT / 3000# | up to1.3 times design pressure | 2 Way Manifold | NO | VTA
NOTE:
1- Instrument range shall be finalized by vendor.
2- Pressure limit valve to be considered by vendor (as per project specification and related standards due to vendor selected instrument range )
3- Existing data to be submitted /confirmed by client.
4- For manifold rating (treaded connection), bolt & gasket material refer to "Piping Material Specification DOC No.: BK-GCS-PEDCO-120-PI-SP-0001
5- Transmitters shall be of the smart transmitter type with HART communication protocol.
D03

## ESD PT
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR PRESSURE / DIFF. PRESSURE TRANSMITTER
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده |  | تسهیلات | رشته | نوع مدرک |  | سریال | نسخه
9184 – 073 - 053 |  |  |  | BK | GCS | PEDCO |  | 120 | IN | DT |  | 0004 | D03
ESD PRESSURE TRANSMITTER
GENERAL DATA |  | 1 | Tag No. | [7 empty] | SEE NEXT PAGE
|  | 2 | P&ID No. | [7 empty] | SEE NEXT PAGE
|  | 3 | Equipment No. / Line No. | [7 empty] | SEE NEXT PAGE
|  | 4 | Area Classification | [7 empty] | ZONE 2, IIB T4
|  | 5 | Piping Class | [7 empty] | SEE NEXT PAGE
OPERATING CONDITIONS |  | 6 | Fluid | [7 empty] | SEE NEXT PAGE
|  | 7 | Phase | [7 empty] | SEE NEXT PAGE
|  | 8 | Operating Pressure | [5 empty] | (bar-g) |  | SEE NEXT PAGE
|  | 9 | Design Pressure | [5 empty] | (bar-g) |  | SEE NEXT PAGE
|  | 10 | Operating Temperature | [5 empty] | (°C) |  | SEE NEXT PAGE
|  | 11 | Design Temperature | [5 empty] | (°C) |  | SEE NEXT PAGE
TRANSMITTER |  | 12 | Element Type | [5 empty] | (NOTE 4) |  | SEE NEXT PAGE
|  | 13 | Size of Process Connection | [7 empty] | SEE NEXT PAGE
|  | 14 | Rating of Process Connection | [7 empty] | SEE NEXT PAGE
|  | 15 | Element Material | [7 empty] | SEE NEXT PAGE
|  | 16 | Enclosure Material | [7 empty] | Die cast aluminium
|  | 17 | Instrument Range | [7 empty] | SEE NEXT PAGE
|  | 18 | Power Supply | [7 empty] | 24 VDC-Loop powered
|  | 19 | Output Signal | [7 empty] | 4-20mA
|  | 20 | Communication Protocol | [7 empty] | SMART HART(4-20mA)
|  | 21 | Electrical Connection | [7 empty] | 2* ISO M20 x 1.5
|  | 22 | Electrical Certification | [7 empty] | EEx "i"
|  | 23 | Ingress Protection | [7 empty] | IP-65 as minimum
|  | 24 | Accuracy | [7 empty] | 0.1% F.S
|  | 25 | Repeatability | [7 empty] | +/- 0.1% or better
|  | 26 | Span and Zero Adjustment | [7 empty] | Required
|  | 27 | Over Range Protection | [7 empty] | Yes
DIAPHRAGM SEAL |  | 28 | Type | [7 empty] | N/A
|  | 29 | Size (In) | [7 empty] | N/A
|  | 30 | Fill Fluid | [7 empty] | N/A
|  | 31 | Diaphragm Material | [7 empty] | N/A
|  | 32 | Capillary Material | [7 empty] | N/A
|  | 33 | Capillary Length | [7 empty] | N/A
OPTIONS |  | 34 | Integral Indicator |  |  |  | Display Unit |  |  |  | Required |  |  |  | Bar-g
|  | 35 | Mounting Brackets | [7 empty] | Required, 2" Support Pipe (Note 3)
|  | 36 | Manifold |  |  |  | Body Material |  |  |  | 2 Way Block & Bleed Manifold |  |  |  | 316 S.S.L
|  | 37 | Connection | [7 empty] | 1/2 " NPT (Note 2,5,7)
|  | 38 | Manifold Model |  |  |  | Manifold Manufacturer |  |  |  | - |  |  |  | VTA
|  | 39 | Integral Indicator Style | [7 empty] | LCD TYPE
|  | 40 | NACE Requirements | [7 empty] | SEE NEXT PAGE
PURCHASING DATA |  | 41 | Model |  |  |  | Manufacturer |  |  |  | Will Be Finilized Later |  |  | Will Be Finilized Later
|  | 42 | Supplier |  |  |  | Order |  |  |  | Will Be Finilized Later |  |  | Will Be Finilized Later
NOTES : | VTA : VENDOR TO ADVISE
1 : Wetted part shall be according to NACE MR0175/ISO 15156 as per list.
2 : All manifolds shall be suitable for connection to transmitter and process line.
3 : Mounting Yoke, U-bolt , Nuts and all accessories shall be supplied by vendor.
4 : Suitable element type to be confirmed by vendor.
5 : For manifold rating, refer to "Piping Material Specification Doc No.: BK-GCS-PEDCO-120-PI-SP-0001
6 : Burn out direction shall be capable to set.
7 : Instrument/Process connection to be as bellows:
- Process Connection:1/2" NPTF
- Instrument Connection: 1/2" NPTF
- Drain Connection: 1/4" NPTF

## ESD PT LIST
NISOC |  |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR PRESSURE / DIFF. PRESSURE TRANSMITTER
شماره پیمان: |  |  |  |  | پروژه | بسته کاری | صادرکننده |  |  | تسهیلات | رشته | نوع مدرک |  | سریال |  | نسخه
9184 – 073 - 053 |  |  |  |  | BK | GCS | PEDCO |  |  | 120 | IN | DT |  | 0004 |  | D03
ESD PRESSURE TRANSMITTERS
Rev. | Item No. | Tag No. | SYSTEM/SIL Rated | P&ID No. |  | Equipment No. / Line No. |  | Piping Class/ Rating | Manifold Rating | Fluid | Phase | Design Pressure (Barg) | Operating Pressure (Barg) | Design Temp. (°C) | Operating Temp. (°C) | Calibration Range (Barg) (Note 2) | Instrument Range (Barg) (Note 1) | Element Type | Element Material | Size of Process Connection / rate of process connection | Over Range protection (Note 2) | Manifold Requirement (Block & Bleed) | NACE | Model | Remark
D03 | 1 | PIT-2111 | ESD ( NOTE 5 ) | BK-GCS-PEDCO-120-PR-PI-0004 (1 of 2) |  | GAS-111-0012-AN07-8"-PT |  | AN07 / 150# | 6000# | PROCESS GAS | GAS | 18.2 | 5.5 | 85 | 32/15.5 | 0-10 | VTA | Diaphragm | SS 316L | 1/2" NPT / 6000# | up to1.3 times design pressure | 2 Way Manifold | YES | VTA
D03 | 2 | PIT-2114A | ESD ( NOTE 5 ) | BK-GCS-PEDCO-120-PR-PI-0004 (2 of 2) |  | CDH-111-0010-AS00-4"-NP |  | AS00 / 150# | 3000# | WATER+HYDROCARBON | LIQUID | 13.9 | 5.5 | 85 | 32/15.5 | 0-10 | VTA | Diaphragm | SS 316L | 1/2" NPT / 3000# | up to1.3 times design pressure | 2 Way Manifold | YES | VTA
D03 | 3 | PIT-2216A | ESD ( NOTE 5 ) | BK-GCS-PEDCO-120-PR-PI-0004 (2 of 2) |  | CDH-112-0012-CN05-3"-PT |  | CN05 / 300# | 3000# | WATER+HYDROCARBON | LIQUID | 47.7 | 19.5 | 155 | 5/50 | 0-38 | VTA | Diaphragm | SS 316L | 1/2" NPT / 3000# | up to1.3 times design pressure | 2 Way Manifold | YES | VTA
D03 | 4 | PIT-2115 | ESD ( NOTE 5 ) | BK-GCS-PEDCO-120-PR-PI-0004 (2 of 2) |  | CDH-112-0015-CN07-4"-PT |  | CN07 / 300# | 3000# | WATER+HYDROCARBON | LIQUID | 47.7 | 18.5 | 155 | 5/50 | 0-36 | VTA | Diaphragm | SS 316L | 1/2" NPT / 3000# | up to1.3 times design pressure | 2 Way Manifold | YES | VTA
D03 | 5 | PIT-2116B | ESD ( NOTE 5 ) | BK-GCS-PEDCO-120-PR-PI-0004 (2 of 2) |  | CDH-112-0013-CN05-3"-PT |  | CN05 / 300# | 3000# | WATER+HYDROCARBON | LIQUID | 47.7 | 19.5 | 155 | 5/50 | 0-10 | VTA | Diaphragm | SS 316L | 1/2" NPT / 3000# | up to1.3 times design pressure | 2 Way Manifold | YES | VTA
D03 | 6 | PIT-2114B | ESD ( NOTE 5 ) | BK-GCS-PEDCO-120-PR-PI-0004 (2 of 2) |  | CDH-111-0011-AS00-4"-NP |  | AS00 / 150# | 3000# | WATER+HYDROCARBON | LIQUID | 13.9 | 5.5 | 85 | 32/15.5 | 0-38 | VTA | Diaphragm | SS 316L | 1/2" NPT / 3000# | up to1.3 times design pressure | 2 Way Manifold | YES | VTA
D03 | 7 | PIT-2116 | ESD/ SIL 2 (NOTE 5) | BK-GCS-PEDCO-120-PR-PI-0005 |  | GAS-111-0005-AN07-10"-PT |  | AN07 / 150# | 6000# | PROCESS GAS | GAS | 18.2 | 5.3 | 85 | 37.17/19.23 | 0-10 | VTA | Diaphragm | SS 316L | 1/2" NPT / 6000# | up to1.3 times design pressure | 2 Way Manifold | YES | VTA
D03 | 8 | PIT-2122A | ESD/SIL 2 ( NOTE 5 ) | BK-GCS-PEDCO-120-PR-PI-0007 (1 of 3) |  | GAS-111-0031A-CN05-8"-ET |  | CN05 / 300# | 3000# | PROCESS GAS | GAS | 47.7 | 4.9 | 155 | 36.78/18.88 | 0-9 | VTA | Diaphragm | SS 316L | 1/2" NPT / 3000# | up to1.3 times design pressure | 2 Way Manifold | YES | VTA
D03 | 9 | PIT-2125A | ESD ( NOTE 5 ) | BK-GCS-PEDCO-120-PR-PI-0007 (1 of 3) |  | GAS-111-0036A-CN05-6"-NP |  | CN05 / 300# | 3000# | PROCESS GAS | GAS | 47.7 | 19 | 155 | 124.8/113.1 | 0-38 | VTA | Diaphragm | SS 316L | 1/2" NPT / 3000# | up to1.3 times design pressure | 2 Way Manifold | YES | VTA
D03 | 10 | PIT-2122B | ESD ( NOTE 5 ) | BK-GCS-PEDCO-120-PR-PI-0007 (2 of 3) |  | GAS-111-0031B-CN05-8"-ET |  | CN05 /300# | 3000# | PROCESS GAS | GAS | 47.7 | 4.9 | 85 | 36.78/18.88 | 0-9 | VTA | Diaphragm | SS 316L | 1/2" NPT / 3000# | up to1.3 times design pressure | 2 Way Manifold | YES | VTA
D03 | 11 | PIT-2125B | ESD ( NOTE 5 ) | BK-GCS-PEDCO-120-PR-PI-0007 (2 of 3) |  | GAS-111-0036B-CN05-6"-NP |  | CN05 / 300# | 3000# | PROCESS GAS | GAS | 47.7 | 19 | 155 | 124.8/113.1 | 0-38 | VTA | Diaphragm | SS 316L | 1/2" NPT / 3000# | up to1.3 times design pressure | 2 Way Manifold | YES | VTA
D03 | 12 | PIT-2122C | ESD ( NOTE 5 ) | BK-GCS-PEDCO-120-PR-PI-0007 (3 of 3) |  | GAS-111-0031C-CN05-8"-ET |  | CN05 /300# | 3000# | PROCESS GAS | GAS | 47.7 | 4.9 | 85 | 36.78/18.88 | 0-9 | VTA | Diaphragm | SS 316L | 1/2" NPT / 3000# | up to1.3 times design pressure | 2 Way Manifold | YES | VTA
D03 | 13 | PIT-2125C | ESD ( NOTE 5 ) | BK-GCS-PEDCO-120-PR-PI-0007 (3 of 3) |  | GAS-111-0036C-CN05-6"-NP |  | CN05 / 300# | 3000# | PROCESS GAS | GAS | 47.7 | 19 | 155 | 124.8/113.1 | 0-38 | VTA | Diaphragm | SS 316L | 1/2" NPT / 3000# | up to1.3 times design pressure | 2 Way Manifold | YES | VTA
D03 | 14 | PIT-2131A | ESD/SIL 2 ( NOTE 5 ) | BK-GCS-PEDCO-120-PR-PI-0010 (1 of 3) |  | GAS-111-0044A-CN05-6"-ET |  | CN05 / 300# | 3000# | PROCESS GAS | GAS | 47.7 | 18.1 | 155 | 59.88 | 0-36 | VTA | Diaphragm | SS 316L | 1/2" NPT / 3000# | up to1.3 times design pressure | 2 Way Manifold | YES | VTA
D03 | 15 | PIT-2134A | ESD/SIL 2 ( NOTE 5 ) | BK-GCS-PEDCO-120-PR-PI-0010 (1 of 3) |  | GAS-111-0051A-FN05-6"-IS |  | FN05 / 600# | 6000# | PROCESS GAS | GAS | 90 | 54.8 | 175 | 142.3/149.5 | 0-100 | VTA | Diaphragm | SS 316L | 1/2" NPT / 6000# | up to1.3 times design pressure | 2 Way Manifold | YES | VTA
D03 | 16 | PIT-2131B | ESD ( NOTE 5 ) | BK-GCS-PEDCO-120-PR-PI-0010 (2 of 3) |  | GAS-111-0044B-CN05-6"-ET |  | CN05 / 300# | 3000# | PROCESS GAS | GAS | 47.7 | 18.1 | 155 | 59.88 | 0-36 | VTA | Diaphragm | SS 316L | 1/2" NPT / 3000# | up to1.3 times design pressure | 2 Way Manifold | YES | VTA
D03 | 17 | PIT-2134B | ESD ( NOTE 5 ) | BK-GCS-PEDCO-120-PR-PI-0010 (2 of 3) |  | GAS-111-0051B-FN05-6"-IS |  | FN05 / 600# | 6000# | PROCESS GAS | GAS | 90 | 54.8 | 175 | 142.3/149.5 | 0-100 | VTA | Diaphragm | SS 316L | 1/2" NPT / 6000# | up to1.3 times design pressure | 2 Way Manifold | YES | VTA
D03 | 18 | PIT-2131C | ESD ( NOTE 5 ) | BK-GCS-PEDCO-120-PR-PI-0010 (3 of 3) |  | GAS-111-0044C-CN05-6"-ET |  | CN05 / 300# | 3000# | PROCESS GAS | GAS | 47.7 | 18.1 | 155 | 60 | 0-36 | VTA | Diaphragm | SS 316L | 1/2" NPT / 3000# | up to1.3 times design pressure | 2 Way Manifold | YES | VTA
D03 | 19 | PIT-2134C | ESD ( NOTE 5 ) | BK-GCS-PEDCO-120-PR-PI-0010 (3 of 3) |  | GAS-111-0051C-FN05-6"-IS |  | FN05 / 600# | 6000# | PROCESS GAS | GAS | 90 | 54.8 | 175 | 142.3/149.5 | 0-100 | VTA | Diaphragm | SS 316L | 1/2" NPT / 6000# | up to1.3 times design pressure | 2 Way Manifold | YES | VTA
D03 | 20 | PIT-2202 | ESD ( NOTE 5 ) | BK-GCS-PEDCO-120-PR-PI-0015 (1 of 2) |  | PLA-112-0010-AN04-1 1/2"-PT |  | AN04 / 150# | 3000# | PLANT AIR | GAS | 18.2 | 9 | 90 | 65 | 0-18 | VTA | Diaphragm | SS 316L | 1/2" NPT / 3000# | up to1.3 times design pressure | 2 Way Manifold | NO | VTA
D03 | 21 | PIT-2201A | ESD/SIL 1 ( NOTE 5 ) | BK-GCS-PEDCO-120-PR-PI-0015 (2 of 2) |  | ISA-112-0012-AZ00-2"-NP |  | AZ00 / 150# | 3000# | INSTRUMENT AIR | GAS | 18.2 | 8 | 85 | 65 | 0-16 | VTA | Diaphragm | SS 316L | 1/2" NPT / 3000# | up to1.3 times design pressure | 2 Way Manifold | NO | VTA
D03 | 22 | PIT-2201B | ESD/SIL 1 ( NOTE 5 ) | BK-GCS-PEDCO-120-PR-PI-0015 (2 of 2) |  | ISA-112-0012-AZ00-2"-NP |  | AZ00 / 150# | 3000# | INSTRUMENT AIR | GAS | 18.2 | 8 | 85 | 65 | 0-16 | VTA | Diaphragm | SS 316L | 1/2" NPT / 3000# | up to1.3 times design pressure | 2 Way Manifold | NO | VTA
D03 | 23 | PIT-2201C | ESD/SIL 1 ( NOTE 5 ) | BK-GCS-PEDCO-120-PR-PI-0015 (2 of 2) |  | ISA-112-0012-AZ00-2"-NP |  | AZ00 / 150# | 3000# | INSTRUMENT AIR | GAS | 18.2 | 8 | 85 | 65 | 0-16 | VTA | Diaphragm | SS 316L | 1/2" NPT / 3000# | up to1.3 times design pressure | 2 Way Manifold | NO | VTA
D03 | 24 | PIT-2211 | ESD/SIL 2 ( NOTE 5 ) | BK-GCS-PEDCO-120-PR-PI-0016 |  | NIT-112-0024-AN01-2"-PT |  | AN01 / 150# | 3000# | NITROGEN RECEIVER | GAS | 18.2 | 7.5 | 85 | 60 | 0-15 | VTA | Diaphragm | SS 316L | 1/2" NPT / 3000# | up to1.3 times design pressure | 2 Way Manifold | NO | VTA
D03 | 25 | PIT-2222A | ESD ( NOTE 5 ) | BK-GCS-PEDCO-120-PR-PI-0017 (2 of 2) |  | CDH-112-0031-AN07-2"-PT |  | AN07 / 150# | 6000# | CLOSED DRAIN | LIQUID | 18.2 | 0.8 | 85 | 5 | 0-1.6 | VTA | Diaphragm | SS 316L | 1/2" NPT / 6000# | up to1.3 times design pressure | 2 Way Manifold | YES | VTA
D03 | 26 | PIT-2222B | ESD ( NOTE 5 ) | BK-GCS-PEDCO-120-PR-PI-0017 (2 of 2) |  | CDH-112-0146-AN07-2"-PT |  | AN07 / 150# | 6000# | CLOSED DRAIN | LIQUID | 18.2 | 0.8 | 85 | 5 | 0-1.6 | VTA | Diaphragm | SS 316L | 1/2" NPT / 6000# | up to1.3 times design pressure | 2 Way Manifold | YES | VTA
D03 | 27 | PIT-2251A | ESD ( NOTE 5 ) | BK-GCS-PEDCO-120-PR-PI-0020 (2 of 3) |  | CDH-112-0036-AN07-2"-PT |  | AN07 / 150# | 6000# | FLARE PUMP | LIQUID | 18.2 | 0.6 | 85 | 5 | 0-1.2 | VTA | Diaphragm | SS 316L | 1/2" NPT / 6000# | up to1.3 times design pressure | 2 Way Manifold | YES | VTA
D03 | 28 | PIT-2251B | ESD ( NOTE 5 ) | BK-GCS-PEDCO-120-PR-PI-0020 (2 of 3) |  | CDH-112-0147-AN07-2"-PT |  | AN07 / 150# | 6000# | FLARE PUMP | LIQUID | 18.2 | 0.6 | 85 | 5 | 0-1.2 | VTA | Diaphragm | SS 316L | 1/2" NPT / 6000# | up to1.3 times design pressure | 2 Way Manifold | YES | VTA
NOTE:
1- Instrument range shall be finalized by vendor.
2- Pressure limit valve to be considered by vendor (as per project specification and related standards due to vendor selected instrument range )
3- Existing data to be submitted /confirmed by client.
4- For manifold rating (treaded connection), bolt & gasket material refer to "Piping Material Specification DOC No.: BK-GCS-PEDCO-120-PI-SP-0001
5- Transmitters shall be of the smart transmitter type with HART communication protocol, SIL rated also write protected.
D03

## PDT
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR PRESSURE / DIFF. PRESSURE TRANSMITTER
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده |  | تسهیلات | رشته | نوع مدرک |  | سریال | نسخه
9184 – 073 - 053 |  |  |  | BK | GCS | PEDCO |  | 120 | IN | DT |  | 0004 | D03
DIFF. PRESSURE TRANSMITTER
GENERAL DATA |  | 1 | Tag No. | [7 empty] | SEE NEXT PAGE
|  | 2 | P&ID No. | [7 empty] | SEE NEXT PAGE
|  | 3 | Equipment No. / Line No. | [7 empty] | SEE NEXT PAGE
|  | 4 | Area Classification | [7 empty] | ZONE 2, IIB T4
|  | 5 | Piping Class | [7 empty] | SEE NEXT PAGE
OPERATING CONDITIONS |  | 6 | Fluid | [7 empty] | SEE NEXT PAGE
|  | 7 | Phase | [7 empty] | SEE NEXT PAGE
|  | 8 | Operating Pressure | [5 empty] | (bar-g) |  | SEE NEXT PAGE
|  | 9 | Design Pressure | [5 empty] | (bar-g) |  | SEE NEXT PAGE
|  | 10 | Operating Temperature | [5 empty] | (°C) |  | SEE NEXT PAGE
|  | 11 | Design Temperature | [5 empty] | (°C) |  | SEE NEXT PAGE
TRANSMITTER |  | 12 | Element Type | [5 empty] | (NOTE 4) |  | SEE NEXT PAGE
|  | 13 | Size of Process Connection | [7 empty] | SEE NEXT PAGE
|  | 14 | Rating of Process Connection | [7 empty] | SEE NEXT PAGE
|  | 15 | Element Material | [7 empty] | SEE NEXT PAGE
|  | 16 | Enclosure Material | [7 empty] | Die cast aluminium
|  | 17 | Instrument Range | [7 empty] | SEE NEXT PAGE
|  | 18 | Power Supply | [7 empty] | 24 VDC-Loop powered
|  | 19 | Output Signal | [7 empty] | 4-20mA
|  | 20 | Communication Protocol | [7 empty] | SMART HART(4-20mA)
|  | 21 | Electrical Connection | [7 empty] | 2* ISO M20 x 1.5
|  | 22 | Electrical Certification | [7 empty] | EEx "i"
|  | 23 | Ingress Protection | [7 empty] | IP-65 as minimum
|  | 24 | Accuracy | [7 empty] | 0.1% F.S
|  | 25 | Repeatability | [7 empty] | +/- 0.1% or better
|  | 26 | Span and Zero Adjustment | [7 empty] | Required
|  | 27 | Over Range Protection | [7 empty] | Yes
DIAPHRAGM SEAL |  | 28 | Type | [7 empty] | N/A
|  | 29 | Size (In) | [7 empty] | N/A
|  | 30 | Fill Fluid | [7 empty] | N/A
|  | 31 | Diaphragm Material | [7 empty] | N/A
|  | 32 | Capillary Material | [7 empty] | N/A
|  | 33 | Capillary Length | [7 empty] | N/A
OPTIONS |  | 34 | Integral Indicator |  |  |  | Display Unit |  |  |  | Required |  |  |  | Bar
|  | 35 | Mounting Brackets | [7 empty] | Required, 2" Support Pipe (Note 3)
|  | 36 | Manifold |  |  |  | Body Material |  |  |  | 5 Way Block & Bleed Manifold |  |  |  | 316 S.S.L
|  | 37 | Connection | [7 empty] | 1/2 " NPT (Note 2,5,7)
|  | 38 | Manifold Model |  |  |  | Manifold Manufacturer |  |  |  | - |  |  |  | VTA
|  | 39 | Integral Indicator Style | [7 empty] | LCD TYPE
|  | 40 | NACE Requirements | [7 empty] | SEE NEXT PAGE
PURCHASING DATA |  | 41 | Model |  |  |  | Manufacturer |  |  |  | Will Be Finilized Later |  |  | Will Be Finilized Later
|  | 42 | Supplier |  |  |  | Order |  |  |  | Will Be Finilized Later |  |  | Will Be Finilized Later
NOTES : | VTA : VENDOR TO ADVISE
1 : Wetted part shall be according to NACE MR0175/ISO 15156 as per list.
2 : All manifolds shall be suitable for connection to transmitter and process line.
3 : Mounting Yoke, U-bolt , Nuts and all accessories shall be supplied by vendor.
4 : Suitable element type to be confirmed by vendor.
5 : For manifold rating, refer to "Piping Material Specification Doc No.: BK-GCS-PEDCO-120-PI-SP-0001
6 : Burn out direction shall be capable to set.
7 : Instrument/Process connection to be as bellows:
- Process Connection:1/2" NPTF
- Instrument Connection: 1/2" NPTF
- Drain Connection: 1/4" NPTF

## PDT LIST
NISOC |  |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR PRESSURE / DIFF. PRESSURE TRANSMITTER
شماره پیمان: |  |  |  |  | پروژه | بسته کاری | صادرکننده |  |  | تسهیلات | رشته |  | نوع مدرک |  | سریال | نسخه
9184 – 073 - 053 |  |  |  |  | BK | GCS | PEDCO |  |  | 120 | IN |  | DT |  | 0004 | D03
DIFF. PRESSURE TRANSMITTERS LIST
Rev. | Item No. | Tag No. | SYSTEM/SIL Rated | P&ID No. |  | Equipment No. / Line No. |  | Piping Class/ Rating | Manifold Rating | Fluid | Phase | Design Pressure (Bar-g) | Operating Pressure (Bar-g) | Design Temp. (°C) | Operating Temp. (°C) | Calibration Range (Bar) (Note 2) | Instrument Range (Barg) (Note 1) | Element Type | Element Material | Size of Process Connection / rate of process connection | Over Range Protection (Note 2) | Manifold Requirement (Block & Bleed) | NACE | Model | Remark
D03 | 1 | PDIT-2111 | DCS | BK-GCS-PEDCO-120-PR-PI-0004 (1 of 2) |  | GAS-111-0019-AN07-8"-PT |  | AN07 / 150# | 6000# | SLUG CATCHER | GAS | FV/9 | 5.3 | 85 | 31.86/15.35 | 0-6 | VTA | Diaphragm | SS 316L | 1/2" NPT / 6000# | up to1.3 times design pressure | 5-Way Valve (1/2"NPTFx1/2"NPTF ) | YES | VTA
D03 | 2 | PDIT-2112 | DCS | BK-GCS-PEDCO-120-PR-PI-0005 |  | V-2105 |  | - / 150# | 6000# | PROCESS GAS | GAS | FV/9 | 5.1 | 85 | 19/37 | 0-6 | VTA | Diaphragm | SS 316L | 1/2" NPT / 6000# | up to1.3 times design pressure | 5-Way Valve (1/2"NPTFx1/2"NPTF ) | YES | VTA
D03 | 3 | PDIT-2121A | DCS | BK-GCS-PEDCO-120-PR-PI-0006 (1 of 3) |  | V-2101-A |  | - / 150# | 6000# | PROCESS GAS | GAS | FV/20 | 4.9 | 85 | 36.78/18.88 | 0-6 | VTA | Diaphragm | SS 316L | 1/2" NPT / 6000# | up to1.3 times design pressure | 5-Way Valve (1/2"NPTFx1/2"NPTF ) | YES | VTA
D03 | 4 | PDIT-2121B | DCS | BK-GCS-PEDCO-120-PR-PI-0006 (2 of 3) |  | V-2101-B |  | - / 150# | 6000# | PROCESS GAS | GAS | FV/20 | 4.9 | 85 | 36.78/18.88 | 0-6 | VTA | Diaphragm | SS 316L | 1/2" NPT / 6000# | up to1.3 times design pressure | 5-Way Valve (1/2"NPTFx1/2"NPTF ) | YES | VTA
D03 | 5 | PDIT-2121C | DCS | BK-GCS-PEDCO-120-PR-PI-0006 (3 of 3) |  | V-2101-C |  | - / 150# | 6000# | PROCESS GAS | GAS | FV/20 | 4.9 | 85 | 36.78/18.88 | 0-6 | VTA | Diaphragm | SS 316L | 1/2" NPT / 6000# | up to1.3 times design pressure | 5-Way Valve (1/2"NPTFx1/2"NPTF ) | YES | VTA
D03 | 6 | PDIT-2131A | DCS | BK-GCS-PEDCO-120-PR-PI-0009 (1 of 3) |  | V-2102-A |  | - / 300# | 3000# | PROCESS GAS | GAS | FV/22 | 18.1 | 115.5 | 60 | 0-20 | VTA | Diaphragm | SS 316L | 1/2" NPT / 3000# | up to1.3 times design pressure | 5-Way Valve (1/2"NPTFx1/2"NPTF ) | YES | VTA
D03 | 7 | PDIT-2131B | DCS | BK-GCS-PEDCO-120-PR-PI-0009 (2 of 3) |  | V-2102-B |  | - / 300# | 3000# | PROCESS GAS | GAS | FV/22 | 18.1 | 115.5 | 60 | 0-20 | VTA | Diaphragm | SS 316L | 1/2" NPT / 3000# | up to1.3 times design pressure | 5-Way Valve (1/2"NPTFx1/2"NPTF ) | YES | VTA
D03 | 8 | PDIT-2131C | DCS | BK-GCS-PEDCO-120-PR-PI-0009 (3 of 3) |  | V-2102-C |  | - / 300# | 3000# | PROCESS GAS | GAS | FV/22 | 18.1 | 115.5 | 60 | 0-20 | VTA | Diaphragm | SS 316L | 1/2" NPT / 3000# | up to1.3 times design pressure | 5-Way Valve (1/2"NPTFx1/2"NPTF ) | YES | VTA
D03 | 9 | PDIT-2143 | DCS | BK-GCS-PEDCO-120-PR-PI-0012 |  | GAS-111-0366-FN05-6"-PT |  | FN05 / 600# | 6000# | PROCESS GAS | GAS | 90 | 53.9 | 175 | 59.9 | 0-60 | VTA | Diaphragm | SS 316L | 1/2" NPT / 6000# | up to1.3 times design pressure | 5-Way Valve (1/2"NPTFx1/2"NPTF ) | YES | VTA
D03 | 10 | PDIT-2141 | DCS | BK-GCS-PEDCO-120-PR-PI-0012 |  | V-2103 |  | - / 600# | 6000# | PROCESS GAS | GAS | FV/62 | 53.9 | 130 | 59.9 | 0-60 | VTA | Diaphragm | SS 316L | 1/2" NPT / 6000# | up to1.3 times design pressure | 5-Way Valve (1/2"NPTFx1/2"NPTF ) | YES | VTA
NOTE:
1- Instrument range shall be finalized by vendor.
2- Pressure limit valve to be considered by vendor (as per project specification and related standards due to vendor selected instrument range )
3- Existing data to be submitted /confirmed by client.
4- For manifold rating (treaded connection), bolt & gasket material refer to "Piping Material Specification DOC No.: BK-GCS-PEDCO-120-PI-SP-0001
5- Transmitters shall be of the smart transmitter type with HART communication protocol.
D03