## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-IN-DT-0004_D02 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-2323 |  |  | Transmital Date: 29 Aug 2023
Document Title: Data Sheets For Pressure/Diff. Pressure Transmitter |  |  |  |  | PEDCO Tr. No.:BK-PEDCO-NISOC-0005-IN-TR- 2323 |  |  | Transmital Date: 29 Aug 2023
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-IN-DT-0004_D02 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
D01
1 | برای برخی ادوات به عنوان مثال PIT-2135A/B/C علیرغم اینکه روی خطوط گاز نصب می‌شوند استاندارد NACE در نظر گرفته نشده است. لازم است این موارد اصلاح گردد. |  | 1402/2294/260127 | 1402/07/04 | مطابق نظر کارفرمای محترم مدرک اصلاح گردید.
2 | برای برخی از ادوات میزان Manifold Rating و Rate of process connection مطابقت ندارد به عنوان مثال PIT-2114A، لازم است این موارد اصلاح گردد. |  | 1402/2294/260127 | 1402/07/04 | مطابق نظر کارفرمای محترم مدرک اصلاح گردید.
3
4
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: | Signature
| Date: |  |  |  |  | Date: