## Cover
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
INSTRUMENT CABLE LIST
شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 5
9184 – 073 - 053 |  |  | BK |  | PPL | PEDCO | 320 |  | IN | LI | 0007 | D01
طرح نگهداشت و افزایش تولید 27 مخزن
INSTRUMENT CABLE LIST نگهداشت و افزایش تولید میدان نفتی بینک
D01 |  | FEB.2024 |  | IFA |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | S.Faramarzpour
D00 |  | SEP.2023 |  | IFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | S.Faramarzpour
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
Class: 1 |  |  |  | CLIENT Doc. Number: F0Z-708614
status: | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved

## Revisions
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
INSTRUMENT CABLE LIST
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 5
9184 – 073 - 053 |  |  | BK | PPL |  | PEDCO | 320 | IN | LI | 0007 |  | D01
Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D01 |  | D02 | D03 | D04
1 | X | X | [6 empty] | 65
2 | X | X | [6 empty] | 66
3 | X | [7 empty] | 67
4 | X | [7 empty] | 68
5 | X | X | [6 empty] | 69
6 | [8 empty] | 70
7 | [8 empty] | 71
8 | [8 empty] | 72
9 | [8 empty] | 73
10 | [8 empty] | 74
11 | [8 empty] | 75
12 | [8 empty] | 76
13 | [8 empty] | 77
14 | [8 empty] | 78
15 | [8 empty] | 79
16 | [8 empty] | 80
17 | [8 empty] | 81
18 | [8 empty] | 82
19 | [8 empty] | 83
20 | [8 empty] | 84
21 | [8 empty] | 85
22 | [8 empty] | 86
23 | [8 empty] | 87
24 | [8 empty] | 88
25 | [8 empty] | 89
26 | [8 empty] | 90
27 | [8 empty] | 91
28 | [8 empty] | 92
29 | [8 empty] | 93
30 | [8 empty] | 94
31 | [8 empty] | 95
32 | [8 empty] | 96
33 | [8 empty] | 97
34 | [8 empty] | 98
35 | [8 empty] | 99
36 | [8 empty] | 100
37 | [8 empty] | 101
38 | [8 empty] | 102
39 | [8 empty] | 103
40 | [8 empty] | 104
41 | [8 empty] | 105
42 | [8 empty] | 106
43 | [8 empty] | 107
44 | [8 empty] | 108
45 | [8 empty] | 109
46 | [8 empty] | 110
47 | [8 empty] | 111
48 | [8 empty] | 112
49 | [8 empty] | 113
50 | [8 empty] | 114
51 | [8 empty] | 115
52 | [8 empty] | 116
53 | [8 empty] | 117
54 | [8 empty] | 118
55 | [8 empty] | 119
56 | [8 empty] | 120
57 | [8 empty] | 121
58 | [8 empty] | 122
59 | [8 empty] | 123
60 | [8 empty] | 124
61 | [8 empty] | 125
62 | [8 empty] | 126
63 | [8 empty] | 127
64 | [8 empty] | 128

## Notes & References
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
INSTRUMENT CABLE LIST
شماره پیمان: |  |  |  | پروژه |  | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک |  | سریال | نسخه | شماره صفحه: 3 از 5
9184 – 073 - 053 |  |  |  | BK |  | PPL |  | PEDCO | 320 | IN | LI |  | 0007 | D01
GENERAL NOTES:
1- Cable length will be finalized after approval of Instrument location.
2- Gland Size will be finalized after Instrument Cable/Cable Gland P.O
3- Cutting column/Drum no. will be finalized after cable P.O.
4- All cables shall be accordance with Flame retardant standard IEC 60332
5- Fire Resistant cables shall be accordance with standard IEC 60331.
6- All conductors shall be accordance with standard IEC 60228 and the material shall be Tinned cupper.
7- Outer sheath Material :
Flame Retardant : PVC , Color : Light Blue for I.S. & Gray for N.I.S
Fire Resistant : PVC , Color : Light Blue with Red Strip for I.S. & Gray with Red Strip for N.I.S & Red for F&G
[6 empty] | 8- Cable type legend : | [9 empty] | 9- Junction Box Numbering : :
[5 empty] | X - X X - X - X | [9 empty] | JBX - X - XXXX
| BL: Light Blue | [8 empty] | F: Fire resistance | [6 empty] | Sequence No.
| BR: Light Blue/Red Strip | [8 empty] | FA: Fire resistance, Armoured
| GY: Gray | [8 empty] | A: Armoured | [6 empty] | A : Analoge
| GR: Gray /Red Strip | [8 empty] | N: None | [6 empty] | D : Digital
| RD: Red | [15 empty] | S : Solenoid
D : DCS
| Number of core | [15 empty] | E : ESD
| or pair or triad | [10 empty] | 1: 1 mm² |  |  |  |  | F : F&G
2: 1.5 mm²
3: 2.5 mm²
[7 empty] | P: Pair |  |  |  |  | 4: 6 mm²
[7 empty] | C: Core |  |  |  |  | 5: 16 mm²
[7 empty] | T: Triad |  |  |  |  | 6: 35 mm²
REFERENCES:
| 1 | BK-PPL-PEDCO-320-IN-LI-0002_D02 - I/O LIST FOR CONTROL/ESD SYSTEM
| 2 | BK-GNRAL-PEDCO-000-IN-SP-0010-D00 SPECIFICATION FOR INSTRUMENT & F&G CABLES
| 3 | BK-PPL-PEDCO-320-IN-DG-0007_D02 NSTRUMENT JUNCTION BOX TERMINATION DIAGRAM
ABBREVIATION :
| 1- CU |  | : Conductor (Standard tinned copper)
| 2- XLPE |  | : Insulation (Cross-linked polyethylene, low smoke, zero halogen)
| 3- DW |  | : Drain Wire
| 4- ISC |  | : Individual Screen
| 5- DW |  | : Drain Wire
| 6- OSC |  | : Overall Screen
| 7- PVC |  | : Inner sheath (polyvinyl chloride insulation )
| 8- SWA |  | : Armoure (Steel wire Armord )
| 9- PVC |  | : Outer sheath (polyvinyl chloride insulation)
| 10- FRT |  | : Flame Retardant
| 11- FRS |  | : Fire Resistant

## SUMMARY
NISOC |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
INSTRUMENT CABLE LIST
شماره پیمان: |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 4 از 5
9184 – 073 - 053 |  | BK | PPL | PEDCO | 320 | IN | LI | 0007 | D01
SUMMARY
ITEM | TYPE | DESCRIPTION | [6 empty] | QUANTITY (m)(NOTE1)
[9 empty] | ACTUAL (m) |  | (PLUS 20%) (m)
1 | GY-1P-2-A | 1 PAIR * 1.5 mm² , CU/XLPE/DW/OSC/PVC/SWA/PVC, Flame Retardant (IEC-60332) , Gray | [6 empty] | 40 |  | 48
2 | GY-7P-1-A | 7 PAIR * 1 mm² , CU/XLPE/DW/OSC/PVC/LC/PVC/SWA/PVC, Flame Retardant (IEC-60332) , Gray | [6 empty] | 450 |  | 540
3 | GY-1P-3-A | 1 PAIR * 2.5 mm² , CU/XLPE/DW/OSC/PVC/SWA/PVC, Flame Retardant (IEC-60332) , Gray | [6 empty] | 450 |  | 540
4 | GR-1P-3-FA | 1 PAIR * 2.5 mm² , CU/Mica-tape/XLPE/DW/OSC/PVC/SWA/PVC, Fire resistant (IEC-60331)-Gray / Red Strip | [6 empty] | 450 |  | 540

## Cable list
NISOC |  |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
INSTRUMENT CABLE LIST
شماره پیمان: |  |  |  |  | پروژه | بسته کاری | صادرکننده |  | تسهیلات |  | رشته |  | نوع مدرک | سریال |  | نسخه | شماره صفحه:5 از 5
9184 – 073 - 053 |  |  |  |  | BK | PPL | PEDCO |  | 320 |  | IN |  | LI | 0007 |  | D01
ITEM | Cable Code | Tag No. | Description | Cable No. |  | From | To. | SYSTEM | FRT OR FRS | ARMOURE TYPE | IS OR NIS | Qty. OF PAIR/ TRIPLE/Core/QUAD | CONDUCTOR TYPE | CONDUCTOR SIZE ( mm2) | Lead Cover | SCREENING | OUTER SHEATH COLOR | DRUM No. | INSULATION RATED VOLTAG | CABLE LENGTH (M) | GLAND SIZE | Remark
1 | - | PSOV-3201 | Solenoid Valve | IC- | PSOV-3201 | PSOV-3201 | JBD-S-2104 | DCS NOTE 1 | FRT | YES | NIS | 1 | Pair | 2.5 | NO | Overall Screen | Gray | NOTE 4 | 600/1000 V | NOTE 3 | M20
2 | - | ESOV-3201 | Solenoid Valve | IC- | ESOV-3201 | ESOV-3201 | JBE-S-2106 | ESD NOTE 1 | FRS | YES | NIS | 1 | Pair | 2.5 | NO | Overall Screen | Gray / Red Strip | NOTE 4 | 600/1000 V | NOTE 3 | M20
3 | - | EZSC-3201 | Emergency shutdown Limit Switch Close | IC- | EZSC-3201 | EZSC-3201 | JBD-D-2106 | DCS NOTE 1 | FRT | YES | NIS | 1 | Pair | 1.5 | NO | Overall Screen | Gray | NOTE 4 | 300/500 V | NOTE 3 | M20
4 | - | EZSO-3201 | Emergency shutdown Limit Switch Open | IC- | EZSO-3201 | EZSO-3201 | JBD-D-2106 | DCS NOTE 1 | FRT | YES | NIS | 1 | Pair | 1.5 | NO | Overall Screen | Gray | NOTE 4 | 300/500 V | NOTE 3 | M20
5 | - | PIT-3201A | Pressure Indicator Transmitter | IC- | PIT-3201A | PIT-3201A | JBE-A-2105 | ESD NOTE 1 | FRS | YES | IS | 1 | Pair | 1.5 | NO | Overall Screen | LT. Blue / Red Strip | NOTE 4 | 300/500 V | NOTE 3 | M20
6 | - | PIT-3201B | Pressure Indicator Transmitter | IC- | PIT-3201B | PIT-3201B | JBE-A-2105 | ESD NOTE 1 | FRS | YES | IS | 1 | Pair | 1.5 | NO | Overall Screen | LT. Blue / Red Strip | NOTE 4 | 300/500 V | NOTE 3 | M20
7 | - | PIT-3201C | Pressure Indicator Transmitter | IC- | PIT-3201C | PIT-3201C | JBE-A-2105 | ESD NOTE 1 | FRS | YES | IS | 1 | Pair | 1.5 | NO | Overall Screen | LT. Blue / Red Strip | NOTE 4 | 300/500 V | NOTE 3 | M20
8 | GY-1P-3-A | PSOV-3202 | Solenoid Valve | IC- | PSOV-3201 | PSOV-3201 | DCS NOTE 2 | DCS NOTE 2 | FRT | YES | NIS | 1 | Pair | 2.5 | NO | Overall Screen | Gray | NOTE 4 | 600/1000 V | 450 | M20
9 | GR-1P-3-FA | ESOV-3202 | Solenoid Valve | IC- | ESOV-3201 | ESOV-3201 | ESD NOTE 2 | ESD NOTE 2 | FRS | YES | NIS | 1 | Pair | 2.5 | NO | Overall Screen | Gray / Red Strip | NOTE 4 | 600/1000 V | 450 | M20
10 | GY-1P-2-A | EZSC-3202 | Emergency shutdown Limit Switch Close | IC- | EZSC-3201 | EZSC-3201 | JBD-D-3201 | DCS NOTE 2 | FRT | YES | NIS | 1 | Pair | 1.5 | NO | Overall Screen | Gray | NOTE 4 | 300/500 V | 20 | M20
11 | GY-1P-2-A | EZSO-3202 | Emergency shutdown Limit Switch Open | IC- | EZSO-3201 | EZSO-3201 | JBD-D-3201 | DCS NOTE 2 | FRT | YES | NIS | 1 | Pair | 1.5 | NO | Overall Screen | Gray | NOTE 4 | 300/500 V | 20 | M20
12 | GY-7P-1-A | JBD-D-3201 | Junction Box | MC- | JBD-D-3201 | JBD-D-3201 | DCS NOTE 2 | DCS NOTE 2 | FRT | SWA | NIS | 7 | PAIR | 1 | Yes | Overall Screen | Gray | NOTE 4 | 300/500 V | 450 | M32
NOTE 1: NEW DCS/ESD SYSTEM OF GCS UNIT
NOTE 2: EXISTING DCS/ESD SYSTEM OF SIAHMAKAN
NOTE 3:ITENS 1~7 WILL BE PREPARED IN GCS WORK PACKAGE. THE CABLE LENGTH IS CONSIDERED IN GCS UNIT CABLE LIST.
D01
D01