## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-PPL-PEDCO-320-IN-LI-0007_D00 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-2401 |  |  | Transmital Date: 1 Oct 2023
Document Title: Instrument Cable List |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-IN-TR-2401 |  |  | Transmital Date:1 Oct 2023
[5 empty] | CRS No: NISOC-CRS-BK-PPL-PEDCO-320-IN-LI-0007_D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | چرا برای جعبه اتصال ESD کابل مولتی دیده نشده است؟ |  | 1402-2294-395986 | ۱۴۰۲/۰۷/۲۶ | مطابق مدرک تایید شده INSTRUMENT JUNCTION BOX TERMINATION DIAGRAM ، از انجا که تنها یک سیگنال برای قطع سولنویید شیر ESDV به فیلد ارسال میشودبرای آن JB دیده نشده است.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: S.Akbari | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: 14 Oct 2023 |  |  |  |  | Date: