## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-PR-CN-0003 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-2476 |  |  | Transmital Date: 11/11/2023
Document Title: Calculation Note For Flow Element Sizing |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-PR-TR-2476 |  |  | Transmital Date: 11/11/2023
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-PR-CN-0003_D03 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | لطلاعات فرآیندی در نظر گرفته شده برای FE-2101 و FE-2102 از جمله فشار با جدول HM مطابقت ندارد |  | 1402-2294-447402 | 1402/11/02 | در مدرک PFD مشخصات سیال بعد از FCV-2102 و FCV-2102 ارائه شده است. FE-2101,2102 قبل از شیرهای کنترلی ذکر شده قرار گرفته اند. بر اساس نامه شماره 1400/475/6953 مورخ 14100/01/14 فشار ورودی در Tie in ایستگاه 7.5 barg در نظر گرفته شده است. بر اساس مدارک طراحی پایه فشار ورودی به ایستگاه تقویت فشار بینک پس از شیر کنترلی 5.5barg در نظرگفته شده است. لذا بر اساس توافقات صورت گرفته مقرر گردید جهت حاشیه امنیت طراحی افت فشار شیرهای کنترلی برابر با 1bar و مجموع افت فشار خطوط و FE نیز برابر با 1 bar در نظر گرفته شود. با توجه به توضیحات فوق فشار ورودی به FE-2101,2102 برابر با 6.75 BARG در نظر گرفته شده است
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: |  |  |  |  | Date: