## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-PR-CN-0003 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-2476 |  |  | Transmital Date: 11/11/2023
Document Title: Calculation Note For Flow Element Sizing |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-PR-TR-2476 |  |  | Transmital Date: 11/11/2023
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-PR-CN-0003_D03 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | با توجه به اینکه فایل محاسبات پیوست به روز نشده و همانند فایل پیوست ویرایش قبل می باشد، می بایست فایل محاسباتی به روز شده در ویرایش بعد ارسال گردد. |  | BK-SUR-ENG-PCS-02-08859 | 2023-12-02 | اعمال گردید.
2 | میزان دبی RO-2162، با دبی پمپ 2103 مغایرت دارد. |  | BK-SUR-ENG-PCS-02-08859 | 2023-12-02 | اعمال گردید.
3 | با توجه به تامین FE-2121 و ّFE-2131،توسط سازنده کمپرسور و در نظر گرفتن افت فشار 100 میلی بار برای این FE ها، مغایرت این افت فشار با عدد 125 میلی بار در محاسبات پیمانکار، اصلاح گردد. |  | BK-SUR-ENG-PCS-02-08859 | 2023-12-02 | با توجه به تامین FE-2121 و ّFE-2131،توسط سازنده کمپرسور ،محاسبات ارائه شده در مدرک فوق حذف گردید.
4 | راهکار مناسب جهت اصلاح Beta Ratio های کم تر از 0.2 ( نظیر FE-2211) در نظر گرفته شود. |  | BK-SUR-ENG-PCS-02-08859 | 2023-12-02 | اصلاح گردید.
5 | ضروريست نقطه نظرات ذينفع اصلي در خصوص اين مدرك اعمال گردد. |  | BK-SUR-ENG-PCS-02-08859 | 2023-12-02 | اعمال گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: |  |  |  |  | Date: