## Cover
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
I/O LIST FOR F&G SYSTEMS
شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 14
9184 – 073 - 053 |  |  | BK |  | GCS | PEDCO | 120 |  | IN | LI | 0004 | D04
طرح نگهداشت و افزایش تولید 27 مخزن
I/O LIST FOR F&G SYSTEMS نگهداشت و افزایش تولید میدان نفتی بینک
D04 |  | FEB.2024 |  | AFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | S.Faramarzpour
D03 |  | NOV.2022 |  | AFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | S.Faramarzpour
D02 |  | OCT.2022 |  | IFA |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
D01 |  | MAY.2022 |  | IFA |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
D00 |  | FEB.2022 |  | IFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
Class: 1 |  |  |  | CLIENT Doc. Number:F0Z-708970
status: | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved

## REVISION
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
I/O LIST FOR F&G SYSTEMS
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 14
9184 – 073 - 053 |  |  | BK | GCS |  | PEDCO | 120 | IN | LI | 0004 |  | D04
REVISION RECORD SHEET
Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D01 |  | D02 | D03 | D04
1 | X | X | X |  | X |  | X |  | 65
2 | X | X | X |  | X |  | X |  | 66
3 | X | X | [6 empty] | 67
4 | X | X | X |  | X |  | X |  | 68
5 | X | X | X |  | X |  | X |  | 69
6 | X | X | X |  | X |  | X |  | 70
7 | X | X | X |  | X |  | X |  | 71
8 | X | X | X |  | X |  | X |  | 72
9 |  | X | X |  | X |  | X |  | 73
10 |  | X | X |  | X |  | X |  | 74
11 |  | X | X |  | X |  | X |  | 75
12 |  | X | X |  | X |  | X |  | 76
13 |  | X | X |  | X |  | X |  | 77
14 |  | X | X |  | X |  | X |  | 78
15 |  |  | X |  | X |  |  |  | 79
16 |  |  | X |  | X |  |  |  | 80
17 |  |  | X |  | X |  |  |  | 81
18 |  |  | X |  | X |  |  |  | 82
19 | [8 empty] | 83
20 | [8 empty] | 84
21 | [8 empty] | 85
22 | [8 empty] | 86
23 | [8 empty] | 87
24 | [8 empty] | 88
25 | [8 empty] | 89
26 | [8 empty] | 90
27 | [8 empty] | 91
28 | [8 empty] | 92
29 | [8 empty] | 93
30 | [8 empty] | 94
31 | [8 empty] | 95
32 | [8 empty] | 96
33 | [8 empty] | 97
34 | [8 empty] | 98
35 | [8 empty] | 99
36 | [8 empty] | 100
37 | [8 empty] | 101
38 | [8 empty] | 102
39 | [8 empty] | 103
40 | [8 empty] | 104
41 | [8 empty] | 105
42 | [8 empty] | 106
43 | [8 empty] | 107
44 | [8 empty] | 108
45 | [8 empty] | 109
46 | [8 empty] | 110
47 | [8 empty] | 111
48 | [8 empty] | 112
49 | [8 empty] | 113
50 | [8 empty] | 114
51 | [8 empty] | 115
52 | [8 empty] | 116
53 | [8 empty] | 117
54 | [8 empty] | 118
55 | [8 empty] | 119
56 | [8 empty] | 120
57 | [8 empty] | 121
58 | [8 empty] | 122
59 | [8 empty] | 123
60 | [8 empty] | 124
61 | [8 empty] | 125
62 | [8 empty] | 126
63 | [8 empty] | 127
64 | [8 empty] | 128

## NOTE
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
I/O LIST FOR F&G SYSTEMS
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 3 از 14
9184 – 073 - 053 |  |  | BK | GCS | PEDCO | 120 | IN | LI | 0004 | D04
REFERENCES(NOTE 2):
| F&G LOCATION LAYOUT FOR PROCESS Area | [7 empty] | BK-GCS-PEDCO-120-IN-PY-0005
| F&G LOCATION LAYOUT FOR BUILDINGS | [7 empty] | BK-GCS-PEDCO-120-IN-PY-0006
| DATA SHEET FOR MATRIX PANEL | [7 empty] | BK-GCS-PEDCO-120-IN-DT-0017
| ESD LEVEL HIERARCHY | [7 empty] | BK-GCS-PEDCO-120-IN-DG-0003
| FIRE & GAS DETECTION DESIGN CRITERIA | [7 empty] | BK-GCS-PEDCO-120-IN-DC-0001
GENERAL NOTE
| 1 | ALL LISTED FACP'S SIGNALS SHALL BE MONITORED IN F&G SYSTEM BY MODBUS CONNECTION.
| 2 | REFER TO LATEST VERSION OF REFERENCE DOCUMENTS.
| 3 | ALL RELAYS & I.S. BARRIERS INSTALLED IN F&G PANEL SHALL BE SIL CERTIFIED. ALL RELAYS SHALL BE LINE-MONITORED
| 4 | GALVANIC ISOLATION BARRIER SHALL BE CONSIDERED FOR INTRINSICALLY SAFE (EEXia) LOOPS.
| 5 | I/O CARDS & ACCESSORIES SHALL BE SELECTED IN ACCORDANCE WITH '' SPECIFICATION FOR CONTROL SYSTEM".

## SUMMARY
NISOC | [5 empty] | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
I/O LIST FOR F&G SYSTEMS
شماره پیمان: | [5 empty] | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 4 از 14
9184 – 073 - 053 | [5 empty] | BK | GCS |  | PEDCO | 120 | IN | LI | 0004 | D04
F&G I/O SUMMERY COUNT
| ITEM |  | I/O TYPE |  | IS/NIS | R/NR |  | DESCRIPTION | [6 empty] | QTY OF SIGNALS |  | QTY (+20% SPARE) | REMARKS
| 1 |  | AI-IS-R |  | IS | R |  | ANALOGUE INPUT HARDWARE SIGNAL (INTRINSICALLY SAFE, REDUNDANT) | [6 empty] | 86 |  | 104 | NOTES 4,5 | 103.2
| 2 |  | DI-NIS-R |  | NIS | R |  | DIGITAL INPUT HARDWARE SIGNAL (NON INTRINSICALLY SAFE, NON-REDUNDANT) | [6 empty] | 61 |  | 74 |  | 73.2
| 3 |  | DO-NIS-R |  | NIS | R |  | DIGITAL OUTPUT HARDWARE SIGNAL (NON INTRINSICALLY SAFE, REDUNDANT) | [6 empty] | 112 |  | 135 |  | 134.4
ABBREVIATIONS:
|  | I/O |  | INPUT / OUTPUT | [7 empty] | DCS: | DISTRIBUTED CONTROL SYSTEM
|  | DI: |  | DIGITAL INPUT SIGNAL | [7 empty] | ESD: | EMERGENCY SHUT DOWN SYSTEM
|  | DO: |  | DIGITAL OUTPUT SIGNAL | [7 empty] | F&G | FIRE AND GAS CONTROL SYSTEM
|  | AI: |  | ANALOGUE INPUT SIGNAL | [7 empty] | MCC: | MOTOR CONTROL CENTER
|  | AO: |  | ANALOGUE OUTPUT SIGNAL | [7 empty] | IRP: | INTERPOSING RELAY PANEL
|  | IND: |  | INDICATION | [7 empty] | CH: | CHANNEL
|  | STA: |  | STATUS | [7 empty] | ADD: | ADDRESS
|  | COM: |  | COMMAND | [7 empty] | TB: | TERMINAL BLOCK
|  | IS: |  | INTRINSICALLY SAFE | [7 empty] | R: | REDUNDANT
|  | NIS: |  | NON INTRINSICALLY SAFE | [7 empty] | NR: | NON-REDUNDANT
|  | MAC: |  | MANUAL CALL POINT | [7 empty] | BR: | BLUE BEACON
|  | HN: |  | HORN | [7 empty] | BB: | RED BEACON
|  | LHD: |  | LINEAER HEAT DETECTOR | [7 empty] | FGD: | FLAMMABLE GAS DETECTOR
|  | SD: |  | SMOKE DETECTOR | [7 empty] | TGD: | TOXIC GAS DETECTOR
|  | BL: |  | BELL | [7 empty] | FD: | FLAME DETECTOR
|  | FACP: |  | FIRE ALARM CONTROL PANEL | [7 empty] | IRP: | INTERFACE RELAY PANEL
D04

## IO List for F&G System
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
I/O LIST FOR F&G SYSTEMS
شماره پیمان: |  |  |  | پروژه |  | بسته کاری |  | صادرکننده |  | تسهیلات |  |  | رشته |  | نوع مدرک | سریال |  |  | نسخه
9184 – 073 - 053 |  |  |  | BK |  | GCS |  | PEDCO |  | 120 |  |  | IN |  | LI | 0004 |  |  | D04
SIGNALS TO F&G SYSTEM
ITEM | TAG | DESCRIPTION | LOCATION |  | P&ID |  | SIGNAL TYPE/ Area CLASSIFICATION | I/O TYPE |  | FROM |  | TO |  | JB NO. | POWER SUPPLY | Cable Type | SYSTEM CABINET |  |  |  |  | Marshalling Cabinet |  |  | ALARM |  |  |  | I/O TYPE (ADDRE./CONV.) | REMARK | REV.
[17 empty] | CABINET NO. | RACK | SLOT | CH. | ADD. | CABINET NO. | TB NO. | ADD. | HH | H | L | LL
FOR PROCESS AREA
1 | MAC-1001 | Manual Call Point | Area 1 - Pig Receiver Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
2 | MAC-1002 | Manual Call Point | Area 1 - Pig Receiver Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
3 | HN-1001 | Horn | Area 1 - Pig Receiver Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | 2X DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 5 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
4 | BR-1001 | Beacon - Red | Area 1 - Pig Receiver Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
5 | BB-1001 | Beacon - Blue | Area 1 - Pig Receiver Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
6 | BY-1001 | Beacon - Yellow | Area 1 - Pig Receiver Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
7 | MAC-2001 | Manual Call Point | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
8 | MAC-2002 | Manual Call Point | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
9 | MAC-2003 | Manual Call Point | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
10 | HN-2001 | Horn | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | 2X DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 5 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
11 | BR-2001 | Beacon - Red | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
12 | BB-2001 | Beacon - Blue | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
13 | BY-2001 | Beacon - Yellow | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
14 | MAC-3001 | Manual Call Point | Area 3 - Chemical Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
15 | HN-3001 | Horn | Area 3 - Chemical Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | 2X DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 5 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
16 | BR-3001 | Beacon - Red | Area 3 - Chemical Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
17 | BB-3001 | Beacon - Blue | Area 3 - Chemical Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
18 | BY-3001 | Beacon - Yellow | Area 3 - Chemical Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
19 | MAC-4001 | Manual Call Point | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
20 | MAC-4002 | Manual Call Point | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
21 | HN-4001 | Horn | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 OF 12) |  | Eexd Zone2, IIB T4 | 2X DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 5 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
22 | BR-4001 | Beacon - Red | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
23 | BB-4001 | Beacon - Blue | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
24 | BY-4001 | Beacon - Yellow | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
25 | HN-4002 | Horn | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | 2X DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 5 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
26 | BR-4002 | Beacon - Red | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
27 | BB-4002 | Beacon - Blue | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
28 | BY-4002 | Beacon - Yellow | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
29 | MAC-5001 | Manual Call Point | Area 5 - 1St. & 2nd Stage Air Cooler Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
30 | MAC-5002 | Manual Call Point | Area 5 - 1St. & 2nd Stage Air Cooler Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
31 | HN-5001 | Horn | Area 5 - 1St. & 2nd Stage Air Cooler Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | 2X DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 5 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
32 | BR-5001 | Beacon - Red | Area 5 - 1St. & 2nd Stage Air Cooler Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
33 | BB-5001 | Beacon - Blue | Area 5 - 1St. & 2nd Stage Air Cooler Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
34 | BY-5001 | Beacon - Yellow | Area 5 - 1St. & 2nd Stage Air Cooler Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
35 | MAC-6001 | Manual Call Point | Area 6 - Sump & Pig Launcher Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
36 | MAC-6002 | Manual Call Point | Area 6 - Sump & Pig Launcher Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
37 | HN-6001 | Horn | Area 6 - Sump & Pig Launcher Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | 2X DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 5 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
38 | BR-6001 | Beacon - Red | Area 6 - Sump & Pig Launcher Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
39 | BB-6001 | Beacon - Blue | Area 6 - Sump & Pig Launcher Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
40 | BY-6001 | Beacon - Yellow | Area 6 - Sump & Pig Launcher Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
41 | MAC-7001 | Manual Call Point | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
42 | MAC-7002 | Manual Call Point | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
43 | HN-7002 | Horn | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | 2X DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 5 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
44 | BR-7002 | Beacon - Red | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
45 | BB-7002 | Beacon - Blue | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
46 | BY-7002 | Beacon - Yellow | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
47 | MAC-8001 | Manual Call Point | Area 8 - Diesel Generator Area / Air Compressor /Air Dryer Packages Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D04
48 | MAC-8002 | Manual Call Point | Area 8 - Diesel Generator Area / Air Compressor /Air Dryer Packages Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D04
49 | HN-8001 | Horn | Area 8 - Diesel Generator Area / Air Compressor /Air Dryer Packages Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | 2X DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 5 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D04
50 | BR-8001 | Beacon - Red | Area 8 - Diesel Generator Area / Air Compressor /Air Dryer Packages Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D04
51 | BB-8001 | Beacon - Blue | Area 8 - Diesel Generator Area / Air Compressor /Air Dryer Packages Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D04
52 | BY-8001 | Beacon - Yellow | Area 8 - Diesel Generator Area / Air Compressor /Air Dryer Packages Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D04
53 | MAC-9001 | Manual Call Point | Area 9 - Diesel Generator Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D04
54 | MAC-9002 | Manual Call Point | Area 9 - Diesel Generator Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D04
55 | HN-9001 | Horn | Area 9 - Diesel Generator Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | 2X DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 5 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D04
56 | BR-9001 | Beacon - Red | Area 9 - Diesel Generator Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D04
57 | BB-9001 | Beacon - Blue | Area 9 - Diesel Generator Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D04
58 | BY-9001 | Beacon - Yellow | Area 9 - Diesel Generator Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D04
59 | FGD-1001 | Flammable Gas Detector | Area 1 - Pig Receiver Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (4 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
60 | TGD-1001 | Toxic Gas Detector | Area 1 - Pig Receiver Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (4 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
61 | FD-2001 | Flame Detector | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (5 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
62 | FD-2002 | Flame Detector | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (5 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
63 | FD-2003 | Flame Detector | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (5 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
64 | FGD-2001 | Flammable Gas Detector | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (5 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
65 | FGD-2002 | Flammable Gas Detector | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (5 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
66 | FGD-2003 | Flammable Gas Detector | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (5 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
67 | FGD-2004 | Flammable Gas Detector | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (5 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
68 | TGD-2001 | Toxic Gas Detector | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (5 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
69 | TGD-2002 | Toxic Gas Detector | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (5 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
70 | TGD-2003 | Toxic Gas Detector | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (5 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
71 | TGD-2004 | Toxic Gas Detector | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (5 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
72 | FD-3001 | Flame Detector | Area 3 - Chemical Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (6 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
75 | FD-4001A | Flame Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
76 | FD-4002A | Flame Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
77 | FD-4003A | Flame Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
78 | FD-4004A | Flame Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
79 | FGD-4001A | Flammable Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
80 | FGD-4002A | Flammable Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
81 | FGD-4003A | Flammable Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
82 | FGD-4004A | Flammable Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
83 | TGD-4001A | Toxic Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
84 | TGD-4002A | Toxic Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
85 | TGD-4003A | Toxic Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
86 | TGD-4004A | Toxic Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
87 | FD-4001B | Flame Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
88 | FD-4002B | Flame Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
89 | FD-4003B | Flame Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
90 | FD-4004B | Flame Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
91 | FGD-4001B | Flammable Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
92 | FGD-4002B | Flammable Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
93 | FGD-4003B | Flammable Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
94 | FGD-4004B | Flammable Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
95 | TGD-4001B | Toxic Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
96 | TGD-4002B | Toxic Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
97 | TGD-4003B | Toxic Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
98 | TGD-4004B | Toxic Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
99 | FD-4001C | Flame Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
100 | FD-4002C | Flame Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
101 | FD-4003C | Flame Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
102 | FD-4004C | Flame Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
103 | FGD-4001C | Flammable Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
104 | FGD-4002C | Flammable Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
105 | FGD-4003C | Flammable Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
106 | FGD-4004C | Flammable Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
107 | TGD-4001C | Toxic Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
108 | TGD-4002C | Toxic Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
109 | TGD-4003C | Toxic Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
110 | TGD-4004C | Toxic Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
111 | FGD-5001A | Flammable Gas Detector | Area 5 - 1St. & 2nd Stage Air Cooler Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (8 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
112 | FGD-5001B | Flammable Gas Detector | Area 5 - 1St. & 2nd Stage Air Cooler Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (8 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
113 | FGD-5001C | Flammable Gas Detector | Area 5 - 1St. & 2nd Stage Air Cooler Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (8 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
114 | TGD-5001A | Toxic Gas Detector | Area 5 - 1St. & 2nd Stage Air Cooler Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (8 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
115 | TGD-5001B | Toxic Gas Detector | Area 5 - 1St. & 2nd Stage Air Cooler Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (8 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
116 | TGD-5001C | Toxic Gas Detector | Area 5 - 1St. & 2nd Stage Air Cooler Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (8 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
117 | FD-6001 | Flame Detector | Area 6 - Sump & Pig Launcher Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (9 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
118 | FD-6002 | Flame Detector | Area 6 - Sump & Pig Launcher Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (9 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
119 | FGD-6001 | Flammable Gas Detector | Area 6 - Sump & Pig Launcher Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (9 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
120 | FGD-6002 | Flammable Gas Detector | Area 6 - Sump & Pig Launcher Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (9 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
121 | FGD-6003 | Flammable Gas Detector | Area 6 - Sump & Pig Launcher Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (9 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
122 | TGD-6001 | Toxic Gas Detector | Area 6 - Sump & Pig Launcher Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (9 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
123 | TGD-6002 | Toxic Gas Detector | Area 6 - Sump & Pig Launcher Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (9 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
124 | TGD-6003 | Toxic Gas Detector | Area 6 - Sump & Pig Launcher Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (9 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
125 | LHD-7001 | Linear Heat Detector | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (10 OF 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
126 | LHD-7002 | Linear Heat Detector | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (10 OF 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
129 | FGD-7001 | Flammable Gas Detector | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (10 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
130 | FGD-7002 | Flammable Gas Detector | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (10 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
131 | FGD-7003 | Flammable Gas Detector | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (10 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
132 | TGD-7001 | Toxic Gas Detector | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (10 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
133 | TGD-7002 | Toxic Gas Detector | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (10 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
134 | TGD-7003 | Toxic Gas Detector | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (10 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional
135 | FD-8001 | Flame Detector | Area 8 - Diesel Generator Area / Air Compressor /Air Dryer Packages Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (11 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D04
136 | FD-8002 | Flame Detector | Area 9 - Diesel Generator Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (12 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D04
137 | PT-2301 | Pressure Transmitter | Fire Water Pressure |  | BK-GCS-PEDCO-120-SA-PI-0001(2/2) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 2Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional | Deleted | D04
138 | HN-1011 | Horn | Guard House |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | 2X DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 5 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional | Deleted | D04
139 | BR-1011 | Beacon - Red | Guard House |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional | Deleted | D04
140 | BB-1011 | Beacon - Blue | Guard House |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional | Deleted | D04
141 | BY-1011 | Beacon - Yellow | Guard House |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional | Deleted | D04
FOR BUILDING
1 | FGD-1101 | Flammable Gas Detector | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D04
2 | FGD-1102 | Flammable Gas Detector | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * | * | √ | √ |  | Conventional |  | D04
3 | FGD-1103 | Flammable Gas Detector | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * | * | √ | √ |  | Conventional |  | D04
4 | TGD-1101 | Toxic Gas Detector | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * | * | √ | √ |  | Conventional |  | D04
5 | TGD-1102 | Toxic Gas Detector | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * | * | √ | √ |  | Conventional |  | D04
6 | TGD-1103 | Toxic Gas Detector | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * | * | √ | √ |  | Conventional |  | D04
7 | FGD-1201 | Flammable Gas Detector | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (3/6) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * | * | √ | √ |  | Conventional |  | D04
8 | FGD-1202 | Flammable Gas Detector | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (3/6) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * | * | √ | √ |  | Conventional |  | D04
9 | FGD-1203 | Flammable Gas Detector | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (3/6) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * | * | √ | √ |  | Conventional |  | D04
10 | TGD-1201 | Toxic Gas Detector | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (3/6) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * | * | √ | √ |  | Conventional |  | D04
11 | TGD-1202 | Toxic Gas Detector | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (3/6) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * | * | √ | √ |  | Conventional |  | D04
12 | TGD-1203 | Toxic Gas Detector | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (3/6) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * | * | √ | √ |  | Conventional |  | D04
13 | HGD-1101 | Hydrogen Gas Detector | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Eexia 'Zone1, IIC T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * | √ | √ |  | Conventional |  | D04
14 | HGD-1102 | Hydrogen Gas Detector | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Eexia 'Zone1, IIC T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * | √ | √ |  | Conventional |  | D04
16 | HD-1101 | Heat Detector | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Eexd 'Zone1, IIC T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D04
17 | HD-1102 | Heat Detector | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Eexd 'Zone1, IIC T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D04
18 | MAC-1101 | Manual Call Point | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Eexd 'Zone1, IIC T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D04
SIGNALS BETWEEN F&G AND ESD SYSTEM & OTHER SYSTEMS
1 | ESD0-FG-1101 | ESD 0 Request | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DG-0003 |  | Unclassified | DO-NIS-R |  | FGS |  | ESD |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D04
2 | ESD1A-FG-1101 | ESD 1A Request | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DG-0003 |  | Unclassified | DO-NIS-R |  | FGS |  | ESD |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D04
3 | ESD2A-FD-1101 | ESD 1A Request | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DG-0003 |  | Unclassified | DO-NIS-R |  | FGS |  | ESD |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D04
4 | FAN-FG-1101 | Battery Room Duty Fan Activation | Extension of Existing Control Building |  | - |  | Unclassified | DO-NIS-R |  | FGS |  | IRP |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional | ADDED | D04
5 | FAN-FG-1102 | Battery Room Standby Fan Activation | Extension of Existing Control Building |  | - |  | Unclassified | DO-NIS-R |  | FGS |  | IRP |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D04
6 | INB-FG-1101 | Inhibit to Boost for UPS Charger | Extension of Existing Control Building |  | - |  | Unclassified | DO-NIS-R |  | FGS |  | UPS |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D04
7 | EXT-FG-1101 | Extinguishing System Activation | Extension of Existing Control Building |  | - |  | Unclassified | DO-NIS-R |  | FGS |  | UPS |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional | ADDED | D04
8 | TOT-FG-1101 | Total Flooding System Activation | Extension of Existing Control Building |  | - |  | Unclassified | DO-NIS-R |  | FGS |  | UPS |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional | ADDED | D04
9 | Ex-FG-G-1101 | F&G System confirmed Gas Alarm to Existing F&G | Extension of Existing Control Building |  | - |  | Unclassified | DO-NIS-R |  | FGS |  | Existing F&G |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional | to be finalized based on existing f&g system | D04
10 | Ex-FG-F-1101 | F&G System confirmed Fire Alarm to Existing F&G System | Extension of Existing Control Building |  | - |  | Unclassified | DO-NIS-R |  | FGS |  | Existing F&G |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D04
11 | Ex-FG-G-1102 | Existing F&G confirmed Gas Alarm to F&G System | Extension of Existing Control Building |  | - |  | Unclassified | DI-NIS-R |  | Existing F&G |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D04
12 | Ex-FG-F-1102 | Existing F&G confirmed Fire Alarm to F&G System | Extension of Existing Control Building |  | - |  | Unclassified | DI-NIS-R |  | Existing F&G |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D04
13 | DAMP-FG-1101 | Battery Room Standby Damper closed | Extension of Existing Control Building |  | - |  | Unclassified | DO-NIS-R |  | FGS |  | Duty Damper |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D04
14 | DAMP-FG-1102 | Battery Room Duty Damper closed | Extension of Existing Control Building |  | - |  | Unclassified | DO-NIS-R |  | FGS |  | Stand by Damper |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D04
15 | LSLL-2301 | Low Low Level Alarm | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-SA-PI-0001(2/1) |  | Eexd 'Zone1, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D04
16 | LSLL-2302 | Low Low Level Alarm | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-SA-PI-0001(2/1) |  | Eexd 'Zone1, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D04
17 | HSS-2301A | Pump Start Command | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-SA-PI-0001(2/2) |  | Eexd 'Zone1, IIB T4 | DO-NIS-R | DO-NIS-R | FGS | FGS | IRP | Battery Room Fan |  | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D04
18 | XR-2301A | Pump Running/ Stopped Status | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-SA-PI-0001(2/2) |  | Eexd 'Zone1, IIB T4 | DI-NIS-R | DI-NIS-R | IRP | Battery Room Fan | FGS | FGS |  | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D04
19 | XF-2301A | Pump Fault Status | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-SA-PI-0001(2/2) |  | Eexd 'Zone1, IIB T4 | DI-NIS-R | DI-NIS-R | IRP | Battery Room Fan | FGS | FGS |  | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D04
20 | PAL-2301A | Low Pressure Alarm | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-SA-PI-0001(2/2) |  | Eexd 'Zone1, IIB T4 | DI-NIS-R | DI-NIS-R | P-2301A | Battery Room Fan | FGS | FGS |  | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional | ADDED | D04
21 | XM-2301A | Pump Auto/Manual Status | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-SA-PI-0001(2/2) |  | Eexd 'Zone1, IIB T4 | DI-NIS-R | DI-NIS-R | IRP | Battery Room Fan | FGS | FGS |  | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional | ADDED | D04
22 | HSS-2301B | Pump Start Command | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-SA-PI-0001(2/2) |  | Eexd 'Zone1, IIB T4 | DO-NIS-R | DO-NIS-R | FGS | FGS | P-2301B | Battery Room Fan |  | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D04
23 | XM-2301B | PumpAuto/ Manual Status | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-SA-PI-0001(2/2) |  | Eexd 'Zone1, IIB T4 | DI-NIS-R | DI-NIS-R | P-2301B | Battery Room Fan | FGS | FGS |  | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D04
24 | XR-2301B | Pump Running/ Stopped Status | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-SA-PI-0001(2/2) |  | Eexd 'Zone1, IIB T4 | DI-NIS-R | DI-NIS-R | P-2301B | Battery Room Fan | FGS | FGS |  | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D04
25 | XF-2301B | Pump Fault Status | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-SA-PI-0001(2/2) |  | Eexd 'Zone1, IIB T4 | DI-NIS-R | DI-NIS-R | P-2301B | Battery Room Fan | FGS | FGS |  | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D04
26 | PAL-2301B | Low Pressure Alarm | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-SA-PI-0001(2/2) |  | Eexd 'Zone1, IIB T4 | DI-NIS-R | DI-NIS-R | P-2301B | Battery Room Fan | FGS | FGS |  | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D04
27 | HSS-2302A | Pump Start Command | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-SA-PI-0001(2/2) |  | Eexd 'Zone1, IIB T4 | DO-NIS-R | DO-NIS-R | FGS | FGS | P-2302A | Battery Room Fan |  | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D04
28 | XM-2302A | PumpAuto/ Manual Status | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-SA-PI-0001(2/2) |  | Eexd 'Zone1, IIB T4 | DI-NIS-R | DI-NIS-R | P-2302A | Battery Room Fan | FGS | FGS |  | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D04
29 | XR-2302A | Pump Running/ Stopped Status | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-SA-PI-0001(2/2) |  | Eexd 'Zone1, IIB T4 | DI-NIS-R | DI-NIS-R | P-2302A | Battery Room Fan | FGS | FGS |  | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D04
30 | XF-2302A | Pump Fault Status | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-SA-PI-0001(2/2) |  | Eexd 'Zone1, IIB T4 | DI-NIS-R | DI-NIS-R | P-2302A | Battery Room Fan | FGS | FGS |  | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D04
31 | PAL-2302A | Low Pressure Alarm | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-SA-PI-0001(2/2) |  | Eexd 'Zone1, IIB T4 | DI-NIS-R | DI-NIS-R | P-2302A | Battery Room Fan | FGS | FGS |  | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D04
32 | HSS-2302B | Pump Start Command | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-SA-PI-0001(2/2) |  | Eexd 'Zone1, IIB T4 | DO-NIS-R | DO-NIS-R | FGS | FGS | P-2302B | Battery Room Fan |  | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D04
33 | XM-2302B | PumpAuto/ Manual Status | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-SA-PI-0001(2/2) |  | Eexd 'Zone1, IIB T4 | DI-NIS-R | DI-NIS-R | P-2302B | Battery Room Fan | FGS | FGS |  | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D04
34 | XR-2302B | Pump Running/ Stopped Status | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-SA-PI-0001(2/2) |  | Eexd 'Zone1, IIB T4 | DI-NIS-R | DI-NIS-R | P-2302B | Battery Room Fan | FGS | FGS |  | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D04
35 | XF-2302B | Pump Fault Status | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-SA-PI-0001(2/2) |  | Eexd 'Zone1, IIB T4 | DI-NIS-R | DI-NIS-R | P-2302B | Battery Room Fan | FGS | FGS |  | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D04
36 | PAL-2302B | Low Pressure Alarm | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-SA-PI-0001(2/2) |  | Eexd 'Zone1, IIB T4 | DI-NIS-R | DI-NIS-R | P-2302B | Battery Room Fan | FGS | FGS |  | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D04
37 | XA-CO2-1101 | MANUAL/AUTO SELECTOR SWITCH STATUS (FOR PROTECTED AREA) | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-SA-PI-0002 |  | - | DI-NIS-R |  | CO2 Control Panel |  | FGS | FGS |  | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D04
38 | XRE-CO2-1101 | RELEASED STATUS (FOR PROTECTED AREA) | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-SA-PI-0002 |  | - | DI-NIS-R |  | CO2 Control Panel |  | FGS | FGS |  | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D04
39 | XI-CO2-1101 | INHIBIT STATUS (FOR PROTECTED AREA) | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-SA-PI-0002 |  | - | DI-NIS-R |  | CO2 Control Panel |  | FGS | FGS |  | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D04
40 | XF-CO2-1101 | GENERAL FAULT | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-SA-PI-0002 |  | - | DI-NIS-R |  | CO2 Control Panel |  | FGS | FGS |  | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D04
41 | HS-CO2-1101 | AUTOMAT RELEASE COMMAND (FOR PROTECTED AREA) | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-SA-PI-0002 |  | - | DO-NIS-R |  | FGS | FGS | CO2 Control Panel |  |  | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D04
42 | PSH-2302 | Valve Status | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-SA-PI-0001 |  | Eexd 'Zone1, IIB T4 | DI-NIS-R | DI-NIS-R | DV-2302 |  | FGS | FGS |  | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D04
43 | DSOV-2302 | Valve Open Command | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-SA-PI-0001 |  | Eexd 'Zone1, IIB T4 | DO-NIS-R | DI-NIS-R | FGS | FGS | DV-2302 |  |  | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D04
44 | PSH-2303 | Valve Status | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-SA-PI-0001 |  | Eexd 'Zone1, IIB T4 | DI-NIS-R | DI-NIS-R | DV-2303 |  | FGS | FGS |  | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D04
45 | DSOV-2303 | Valve Open Command | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-SA-PI-0001 |  | Eexd 'Zone1, IIB T4 | DO-NIS-R | DI-NIS-R | FGS | FGS | DV-2303 |  |  | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D04
46 | PSH-2304 | Valve Status | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-SA-PI-0001 |  | Eexd 'Zone1, IIB T4 | DI-NIS-R | DI-NIS-R | DV-2304 |  | FGS | FGS |  | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D04
47 | DSOV-2304 | Valve Open Command | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-SA-PI-0001 |  | Eexd 'Zone1, IIB T4 | DO-NIS-R | DI-NIS-R | FGS | FGS | DV-2304 |  |  | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D04
48 | PSH-2301 | Valve Status | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-SA-PI-0001 |  | Eexd 'Zone1, IIB T4 | DI-NIS-R | DI-NIS-R | DV-2305 |  | FGS | FGS |  | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D04
49 | DSOV-2301 | Valve Open Command | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-SA-PI-0001 |  | Eexd 'Zone1, IIB T4 | DO-NIS-R | DI-NIS-R | FGS | FGS | DV-2305 |  |  | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D04
SIGNALS TO F&G Matrix PANEL
1 | LP-AR1-FD | Fire Alarm For Area 1 | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional | low frequency pulse for prealarm and high frequency pulse for alarm | D04
2 | LP-AR1-FGD | Felemmable Gas Alarm For Area 1 | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D04
3 | LP-AR1-TGD | Toxic Gas Alarm For Area 1 | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D04
4 | LP-AR2-FD | Fire Alarm For Area 2 | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D04
5 | LP-AR2-FGD | Felemmable Gas Alarm For Area 2 | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D04
6 | LP-AR2-TGD | Toxic Gas Alarm For Area 2 | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D04
7 | LP-AR3-FD | Fire Alarm For Area 3 | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D04
8 | LP-AR4A-FD | Fire Alarm For Area 4A | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D04
9 | LP-AR4A-FGD | Felemmable Gas Alarm For Area 4 A | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D04
10 | LP-AR4A-TGD | Toxic Gas Alarm For Area 4A | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D04
11 | LP-AR4B-FD | Fire Alarm For Area 4B | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D04
12 | LP-AR4B-FGD | Felemmable Gas Alarm For Area 4 B | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D04
13 | LP-AR4B-TGD | Toxic Gas Alarm For Area 4B | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D04
14 | LP-AR4C-FD | Fire Alarm For Area 4C | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D04
15 | LP-AR4C-FGD | Felemmable Gas Alarm For Area 4C | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D04
16 | LP-AR4C-TGD | Toxic Gas Alarm For Area 4C | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D04
17 | LP-AR5-FD | Fire Alarm For Area 5 | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D04
18 | LP-AR5-FGD | Felemmable Gas Alarm For Area 5 | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D04
19 | LP-AR5-TGD | Toxic Gas Alarm For Area 5 | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D04
20 | LP-AR6-FD | Fire Alarm For Area 6 | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D04
21 | LP-AR6-FGD | Felemmable Gas Alarm For Area 6 | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D04
22 | LP-AR6-TGD | Toxic Gas Alarm For Area 6 | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D04
23 | LP-AR7-FD | Fire Alarm For Area 7 | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D04
24 | LP-AR7-FGD | Felemmable Gas Alarm For Area 7 | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D04
25 | LP-AR7-TGD | Toxic Gas Alarm For Area 7 | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D04
26 | LP-AR8-FD | Fire Alarm For Area 8 | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D04
27 | LP-AR9-FD | Fire Alarm For Area 9 | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D04
28 | LP-CB-FD | Fire Alarm For Control Building | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D04
29 | LP-CB-FGD | Felemmable Gas Alarm For Control Building | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D04
30 | LP-CB-TGD | Toxic Gas Alarm For Control Building | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D04
31 | LP-EB-FD | Fire Alarm For Electrical Building | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D04
32 | LP-EB-FGD | Felemmable Gas Alarm For Electrical Building | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D04
33 | LP-EB-TGD | Toxic Gas Alarm For Electrical Building | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D04
34 | LP-PSH-2302 | Deluge Valve 2302 Opened | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D04
35 | LP-PSH-2303 | Deluge Valve 2303 Opened | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D04
36 | LP-PSH-2304 | Deluge Valve 2304 Opened | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D04
37 | LP-PSH-2301 | Deluge Valve 2301 Opened | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D04
38 | LP-P-2301B | Diesel Pump Status | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D04
39 | LP-P-2301A | Electrical Pump Status | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D04
40 | LP-CO2-RE | CO2 Release Status | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D04
41 | PB-DV-2302 | Deluge Valve 2302 Open Command | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DI-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D04
42 | PB-DV-2303 | Deluge Valve 2303 Open Command | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DI-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D04
43 | PB-DV-2304 | Deluge Valve 2304 Open Command | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DI-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D04
44 | PB-DV-2301 | Deluge Valve 2301 Open Command | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DI-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D04
45 | PB-P-2301B | Diesel Pump Start Command | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DI-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D04
46 | PB-P-2301A | Electrical Pump Start Command | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DI-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D04
47 | PB-CO2-CO | CO2 Release Command | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DI-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D04
48 | PB-RST | RESET-PB | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DI-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D04
49 | PB-ACK-HO | ACK HORN-PB | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DI-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D04
50 | PB-ACK | ACK-PB | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DI-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D04
51 | BUZZER | Audible Alarm | Extension of Existing Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D04
D04
D04
D04
D04
D04
D04
D04
D04
D04
D04
D04
D04
D04
D04
D04
D04
D04
D04
D04
D04
D04
D04
D04
D04
D04
D04
D04
D04
D04
D04
D04
D04

## IO List for FACP
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
I/O LIST FOR F&G SYSTEMS
شماره پیمان: |  |  |  | پروژه |  | بسته کاری |  | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه
9184 – 073 - 053 |  |  |  | BK |  | GCS |  | PEDCO | 120 |  | IN | LI | 0004 | D04
SIGNALS TO FACP
ITEM | TAG | DESCRIPTION | LOCATION |  | P&ID |  | SIGNAL TYPE/ Area CLASSIFICATION | I/O TYPE | FROM | TO |  | POWER SUPPLY | Cable Type | Marshalling Cabinet |  |  | ALARM |  |  |  | I/O TYPE (ADDRE./CONV.) | REMARK | REV.
[14 empty] | CABINET NO. | TB NO. | ADD. | HH | H | L | LL
FOR BUILDING
FACP LOOP 1
1 | FACP | Output Port of Loop 1 | Extension of Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | FACP | MAC-1103 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D04
2 | MAC-1103 | Manual Call Point | Extension of Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | MAC-1103 | MAC-1102 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D04
3 | MAC-1102 | Manual Call Point | Extension of Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | MAC-1102 | SD-1104 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D04
4 | SD-1104 | Smoke Detector | Extension of Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1104 | SD-1108 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D04
5 | SD-1108 | Smoke Detector | Extension of Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1108 | SD-1110 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D04
6 | SD-1110 | Smoke Detector | Extension of Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1110 | SD-1112 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D04
7 | SD-1112 | Smoke Detector | Extension of Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1112 | SD-1114 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D04
8 | SD-1114 | Smoke Detector | Extension of Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1114 | SD-1115 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D04
9 | SD-1115 | Smoke Detector | Extension of Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1115 | MAC-1104 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D04
10 | MAC-1104 | Manual Call Point | Extension of Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | MAC-1104 | BL-1101 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D04
11 | BL-1101 | Bell | Extension of Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | BL-1101 | BR-1103 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D04
12 | BR-1103 | Beacon - Red | Extension of Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | BR-1103 | MAC-1105 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D04
13 | MAC-1105 | Manual Call Point | Extension of Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | MAC-1105 | SD-1118 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D04
14 | SD-1118 | Smoke Detector | Extension of Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1118 | SD-1120 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D04
15 | SD-1120 | Smoke Detector | Extension of Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1120 | HN-1101 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D04
16 | HN-1101 | Horn | Extension of Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | HN-1101 | BR-1101 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D04
17 | BR-1101 | Beacon - Red | Extension of Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | BR-1101 | BB-1101 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D04
18 | BB-1101 | Beacon - Blue | Extension of Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | BB-1101 | BY-1101 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D04
19 | BY-1101 | Beacon - Yellow | Extension of Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | BY-1101 | FACP |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D04
FACP LOOP 2
1 | FACP | Output Port of Loop 3 | Extension of Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | FACP | SD-1105 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D04
2 | SD-1105 | Smoke Detector | Extension of Control Building-False Floor |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1105 | SD-1106 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D04
3 | SD-1106 | Smoke Detector | Extension of Control Building-False Floor |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1106 | FACP |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D04
FACP LOOP 3
1 | FACP | Output Port of Loop 3 | Extension of Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | FACP | SD-1103 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D04
2 | SD-1103 | Smoke Detector | Control Building-False Ceiling |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1103 | SD-1107 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D04
3 | SD-1107 | Smoke Detector | Control Building-False Ceiling |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1107 | SD-1109 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D04
4 | SD-1109 | Smoke Detector | Control Building-False Ceiling |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1109 | SD-1111 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D04
5 | SD-1111 | Smoke Detector | Control Building-False Ceiling |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1111 | SD-1113 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D04
6 | SD-1113 | Smoke Detector | Control Building-False Ceiling |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1113 | SD-1116 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D04
7 | SD-1116 | Smoke Detector | Control Building-False Ceiling |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1116 | SD-1117 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D04
8 | SD-1117 | Smoke Detector | Control Building-False Ceiling |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1117 | SD-1119 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D04
9 | SD-1119 | Smoke Detector | Control Building-False Ceiling |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1119 | FACP |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D04
FACP LOOP 4
1 | FACP | Output Port of Loop 4 | Extension of Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | FACP | HN-1201 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D04
2 | HN-1201 | Horn | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (4/6) |  | Note 1 | Note1 | HN-1201 | BR-1201 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D04
3 | BR-1201 | Beacon - Red | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (4/6) |  | Note 1 | Note1 | BR-1201 | BB-1201 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D04
4 | BB-1201 | Beacon - Blue | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (4/6) |  | Note 1 | Note1 | BB-1201 | BY-1201 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D04
5 | BY-1201 | Beacon - Yellow | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (4/6) |  | Note 1 | Note1 | BY-1201 | MAC-1201 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D04
6 | MAC-1201 | Manual Call Point | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (4/6) |  | Note 1 | Note1 | MAC-1201 | SD-1201 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D04
7 | SD-1201 | Smoke Detector | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (4/6) |  | Note 1 | Note1 | SD-1201 | SD-1202 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D04
8 | SD-1202 | Smoke Detector | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (4/6) |  | Note 1 | Note1 | SD-1202 | MAC-1202 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D04
9 | MAC-1202 | Manual Call Point | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (4/6) |  | Note 1 | Note1 | MAC-1202 | FACP |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D04
FACP LOOP 5
1 | SD-1203 | Smoke Detector | Extension of Existing Elect. Building-False Floor |  | BK-GCS-PEDCO-120-IN-PY-0006 (4/6) |  | Note 1 | Note1 | FACP | SD-1204 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D04
2 | SD-1204 | Smoke Detector | Extension of Existing Elect. Building-False Floor |  | BK-GCS-PEDCO-120-IN-PY-0006 (4/6) |  | Note 1 | Note1 | SD-1204 | FACP |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D04
FACP LOOP 6
1 | FACP | Output Port of Loop 5 | Extension of Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | FACP | HN-1202 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D04
2 | HN-1202 | Horn | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (5/6) |  | Note 1 | Note1 | HN-1202 | BR-1202 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
3 | BR-1202 | Beacon - Red | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (5/6) |  | Note 1 | Note1 | BR-1202 | BB-1202 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
4 | BB-1202 | Beacon - Blue | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (5/6) |  | Note 1 | Note1 | BB-1202 | BY-1202 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
5 | BY-1202 | Beacon - Yellow | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (5/6) |  | Note 1 | Note1 | BY-1202 | MAC-1203 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
6 | MAC-1203 | Manual Call Point | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (5/6) |  | Note 1 | Note1 | MAC-1203 | LHD-1201 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
7 | LHD-1201 | Linear Heat Detector | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (5/6) |  | Note 1 | Note1 | LHD-1201 | LHD-1202 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
8 | LHD-1202 | Linear Heat Detector | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (5/6) |  | Note 1 | Note1 | LHD-1202 | LHD-1203 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
9 | LHD-1203 | Linear Heat Detector | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (5/6) |  | Note 1 | Note1 | LHD-1203 | FACP |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE
FACP LOOP 7
1 | FACP | Output Port of Loop 6 | Extension of Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | FACP | SD-1301 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D04
2 | SD-1301 | Smoke Detector | CCTV Control Room |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1301 | SD-1302 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D04
3 | SD-1302 | Smoke Detector | CCTV Control Room |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1302 | MAC-1302 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D04
4 | MAC-1302 | Manual Call Point | CCTV Control Room |  | BK-GCS-PEDCO-120-IN-PY-0006 (4/6) |  | Note 1 | Note1 | MAC-1302 | SD-1304 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D04
5 | SD-1304 | Smoke Detector | CCTV Control Room |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1304 | SD-1303 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D04
6 | SD-1303 | Smoke Detector | CCTV Control Room |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1303 | HD-1303 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D04
7 | HD-1303 | Heat Detector | CCTV Control Room |  | BK-GCS-PEDCO-120-IN-PY-0006 (5/6) |  | Note 1 | Note1 | HD-1303 | #REF! |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D04
8 | MAC-1301 | Manual Call Point | CCTV Control Room |  | BK-GCS-PEDCO-120-IN-PY-0006 (4/6) |  | Note 1 | Note1 | MAC-1301 | HN-1301 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D04
9 | HN-1301 | Horn | CCTV Control Room |  | BK-GCS-PEDCO-120-IN-PY-0006 (4/6) |  | Note 1 | Note1 | HN-1301 | BR-1301 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D04
10 | BR-1301 | Beacon - Red | CCTV Control Room |  | BK-GCS-PEDCO-120-IN-PY-0006 (4/6) |  | Note 1 | Note1 | BR-1301 | BB-1301 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D04
11 | BB-1301 | Beacon - Blue | CCTV Control Room |  | BK-GCS-PEDCO-120-IN-PY-0006 (4/6) |  | Note 1 | Note1 | BB-1301 | BY-1301 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D04
12 | BY-1301 | Beacon - Yellow | CCTV Control Room |  | BK-GCS-PEDCO-120-IN-PY-0006 (4/6) |  | Note 1 | Note1 | BY-1301 | FACP |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D04
Notes:
1- Non-IS Detector is on the Loop. Level of Alarm is N.A. for such Loop-powered.
D04