## Cover
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
MTO FOR INSTRUMENT / F&G CABLE
شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 4
9184 – 073 - 053 |  |  | BK |  | GCS | PEDCO | 120 |  | IN | MT | 0002 | D01
طرح نگهداشت و افزایش تولید 27 مخزن
MTO FOR INSTRUMENT / F&G CABLE نگهداشت و افزایش تولید میدان نفتی بینک
D01 |  | FEB.2023 |  | IFI |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | S.Faramarzpour
D00 |  | JUNE.2022 |  | IFI |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
Class: 3 |  |  |  | CLIENT Doc. Number: 'F8Z-708979
status: | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved

## Revisions
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
MTO FOR INSTRUMENT / F&G CABLE
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 4
9184 – 073 - 053 |  |  | BK | GCS |  | PEDCO | 120 | IN | MT | 0002 |  | D01
REVISION RECORD SHEET
Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D01 |  | D02 | D03 | D04
1 | X | X | [6 empty] | 65
2 | X | X | [6 empty] | 66
3 | X | X | [6 empty] | 67
4 | X | X | [6 empty] | 68
5 | [8 empty] | 69
6 | [8 empty] | 70
7 | [8 empty] | 71
8 | [8 empty] | 72
9 | [8 empty] | 73
10 | [8 empty] | 74
11 | [8 empty] | 75
12 | [8 empty] | 76
13 | [8 empty] | 77
14 | [8 empty] | 78
15 | [8 empty] | 79
16 | [8 empty] | 80
17 | [8 empty] | 81
18 | [8 empty] | 82
19 | [8 empty] | 83
20 | [8 empty] | 84
21 | [8 empty] | 85
22 | [8 empty] | 86
23 | [8 empty] | 87
24 | [8 empty] | 88
25 | [8 empty] | 89
26 | [8 empty] | 90
27 | [8 empty] | 91
28 | [8 empty] | 92
29 | [8 empty] | 93
30 | [8 empty] | 94
31 | [8 empty] | 95
32 | [8 empty] | 96
33 | [8 empty] | 97
34 | [8 empty] | 98
35 | [8 empty] | 99
36 | [8 empty] | 100
37 | [8 empty] | 101
38 | [8 empty] | 102
39 | [8 empty] | 103
40 | [8 empty] | 104
41 | [8 empty] | 105
42 | [8 empty] | 106
43 | [8 empty] | 107
44 | [8 empty] | 108
45 | [8 empty] | 109
46 | [8 empty] | 110
47 | [8 empty] | 111
48 | [8 empty] | 112
49 | [8 empty] | 113
50 | [8 empty] | 114
51 | [8 empty] | 115
52 | [8 empty] | 116
53 | [8 empty] | 117
54 | [8 empty] | 118
55 | [8 empty] | 119
56 | [8 empty] | 120
57 | [8 empty] | 121
58 | [8 empty] | 122
59 | [8 empty] | 123
60 | [8 empty] | 124
61 | [8 empty] | 125
62 | [8 empty] | 126
63 | [8 empty] | 127
64 | [8 empty] | 128

## Notes & References
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
MTO FOR INSTRUMENT / F&G CABLE
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 3 از 4
9184 – 073 - 053 |  |  |  | BK | GCS | PEDCO | 120 | IN | MT | 0002 | D01
GENERAL NOTES:
1- Cable length will be finalized after approval of Instrument location.
2- Cutting column/Drum no. will be finalized after cable P.O.
3- All cables shall be accordance with Flame retardant standrad IEC 60332
4- Fire Resistant cables shall be accordance with standrad IEC 60331.
5- All conductors shall be accordance with standrad IEC 60228 and the material shall be Tinned cupper.
6- Estimated cables for control room such as F&G matrix ,… and internal/external instrument earth to be finalized later.
REFERENCES:
| 1 | BK-GCS-PEDCO-120-IN-LI-0009 INSTRUMENT/ F&G CABLE LIST
CABLE SPCIFICATION:
| 1- CU |  | : Conductor ( Standard tinned copper)
| 2- XLPE |  | : Insulation (Cross-linked polyethylene , low smoke,zero halogen)
| 3- DW |  | : Drain Wire
| 4- ISC |  | : Individual Screen
| 5- DW |  | : Drain Wire
| 6- OSC |  | : Overall Screen
| 7- PVC |  | : Inner sheath ( polyvinyl chloride insulation )
| 8- SWB |  | : Armoure ( Steel wire Braided )
| 9- PVC |  | : Outer sheath (polyvinyl chloride insulation)
D01

## SUMMARY
NISOC |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
MTO FOR INSTRUMENT / F&G CABLE
شماره پیمان: |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 4 از4
9184 – 073 - 053 |  | BK | GAS | PEDCO | 120 | IN | MT | 0002 | D01
ITEM | TYPE | DESCRIPTION | [6 empty] | QUANTITY (m)(NOTE1)
[9 empty] | ACTUAL (m) |  | (PLUS 20%) (m)
1 | BL-1P-2-A | 1 PAIR * 1.5 mm² , CU/XLPE/DW/OSC/PVC/SWA/PVC, Flame Retardant (IEC-60332) , L.T Blue | [6 empty] | 2190 |  | 2628
2 | BL-12P-1-A | 12 PAIR * 1 mm² , CU/XLPE/DW/ISC/DW/OSC/PVC/LC/PVC/SWA/PVC, Flame Retardant (IEC-60332) , L.T Blue | [6 empty] | 2820 |  | 3384
3 | BL-19P-1-A | 19 PAIR * 1 mm² , CU/XLPE/DW/ISC/DW/OSC/PVC/LC/PVC/SWA/PVC, Flame Retardant (IEC-60332) , L.T Blue | [6 empty] | 17250 |  | 20700
4 | GY-1P-2-A | 1 PAIR * 1.5 mm² , CU/XLPE/DW/OSC/PVC/SWA/PVC, Flame Retardant (IEC-60332) , Gray | [6 empty] | 1090 |  | 1308
5 | GY-7P-1 | 7 PAIR * 1 mm² , CU/XLPE/DW/OSC/PVC, Flame Retardant (IEC-60332) , Gray | [6 empty] | 350 |  | 420
6 | GY-7P-3-A | 7 PAIR * 2.5 mm² , CU/XLPE/DW/OSC/PVC/LC/PVC/SWA/PVC, Flame Retardant (IEC-60332) , Gray | [6 empty] | 2770 |  | 3324
7 | GY-12P-1-A | 12 PAIR * 1 mm² , CU/XLPE/DW/OSC/PVC/LC/PVC/SWA/PVC, Flame Retardant (IEC-60332) , Gray | [6 empty] | 1390 |  | 1668
8 | GY-19P-1-A | 19 PAIR * 1 mm² , CU/XLPE/DW/OSC/PVC/LC/PVC/SWA/PVC, Flame Retardant (IEC-60332) , Gray | [6 empty] | 12620 |  | 15144
9 | GY-19P-1-A | 19 PAIR * 1 mm² , CU/XLPE/DW/OSC/PVC/SWA/PVC, Flame Retardant (IEC-60332) , Gray | [6 empty] | 1120 |  | 1344
10 | GY-1P-3-A | 1 PAIR * 2.5 mm² , CU/XLPE/DW/OSC/PVC/SWA/PVC, Flame Retardant (IEC-60332) , Gray | [6 empty] | 425 |  | 510
11 | BR-1P-2-FA | 1 PAIR * 1.5 mm² , CU/Mica-tape/XLPE/DW/OSC/PVC/SWA/PVC, Fire resistant (IEC-60331)-LT. Blue / Red Strip | [6 empty] | 1180 |  | 1416
12 | BR-19P-1-FA | 19 PAIR * 1 mm² , CU/Mica-tape/XLPE/DW/ISC/DW/OSC/PVC/LC/PVC/SWA/PVC, Fire resistant (IEC-60331)-LT. Blue / Red Strip | [6 empty] | 1340 |  | 1608
13 | BR-12P-1-FA | 12 PAIR * 1 mm² , CU/Mica-tape/XLPE/DW/ISC/DW/OSC/PVC/LC/PVC/SWA/PVC, Fire resistant (IEC-60331)-LT. Blue / Red Strip | [6 empty] | 1190 |  | 1428
14 | GR-19P-1-FA | 19 PAIR * 1 mm² , CU/Mica-tape/XLPE/DW/OSC/PVC/SWA/PVC, Fire resistant (IEC-60331)-Gray / Red Strip | [6 empty] | 420 |  | 504
15 | GR-1P-2-FA | 1 PAIR * 1.5 mm² , CU/Mica-tape/XLPE/DW/OSC/PVC/SWA/PVC, Fire resistant (IEC-60331)-Gray / Red Strip | [6 empty] | 560 |  | 672
16 | GR-1P-3-FA | 1 PAIR * 2.5 mm² , CU/Mica-tape/XLPE/DW/OSC/PVC/SWA/PVC, Fire resistant (IEC-60331)-Gray / Red Strip | [6 empty] | 750 |  | 900
17 | GR-7P-1-FA | 7 PAIR * 1 mm² , CU/Mica-tape/XLPE/DW/OSC/PVC/SWA/PVC, Fire resistant (IEC-60331)-Gray / Red Strip | [6 empty] | 1310 |  | 1572
18 | GR-12P-1-F | 12 PAIR * 1 mm² , CU/Mica-tape/XLPE/DW/OSC/PVC, Fire resistant (IEC-60331)-Gray / Red Strip | [6 empty] | 400 |  | 480
19 | GR-12P-3-FA | 12 PAIR * 2.5 mm² , CU/Mica-tape/XLPE/DW/OSC/PVC/SWA/PVC, Fire resistant (IEC-60331)-Gray / Red Strip | [6 empty] | 2400 |  | 2880
20 | RD-1P-2-FA | 1 PAIR * 1.5 mm² , CU/Mica-tape/XLPE/DW/OSC/PVC/SWA/PVC, Fire resistant (IEC-60331)-RED | [6 empty] | 1090 |  | 1530
21 | RD-1P-2-F By Vendor | 1 PAIR * 1.5 mm² , CU/Mica-tape/XLPE/DW/OSC/PVC Fire resistant (IEC-60331)-RED- BY VENDOR ( FOR FACP ) | [6 empty] | 835 |  | 1002
22 | RD-1P-2-FA By Vendor | 1 PAIR * 1.5 mm² , CU/Mica-tape/XLPE/DW/OSC/PVC/SWA/PVC, Fire resistant (IEC-60331)-RED- BY VENDOR ( FOR FACP ) | [6 empty] | 300 |  | 360
23 | RD-7P-1-F | 7 PAIR * 1 mm² , CU/Mica-tape/XLPE/DW/OSC/PVC, Fire resistant (IEC-60331)-RED | [6 empty] | 100 |  | 120
24 | RD-7P-1-FA | 7 PAIR * 1 mm² , CU/Mica-tape/XLPE/DW/OSC/PVC/SWA/PVC, Fire resistant (IEC-60331)-RED | [6 empty] | 3120 |  | 3744
25 | RD-7P-3-FA | 7 PAIR * 2.5 mm² , CU/Mica-tape/XLPE/DW/OSC/PVC/SWA/PVC, Fire resistant (IEC-60331)-RED | [6 empty] | 3430 |  | 4116
26 | RD-19P-1-F | 19 PAIR * 1 mm² , CU/Mica-tape/XLPE/DW/OSC/PVC, Fire resistant (IEC-60331)-RED | [6 empty] | 250 |  | 300
27 | RD-1T-2-F | 1 Traid * 1.5 mm² , CU/Mica-tape/XLPE/DW/OSC/PVC, Fire resistant (IEC-60331)-RED | [6 empty] | 550 |  | 660
28 | RD-1T-2-FA | 1 Traid * 1.5 mm² , CU/Mica-tape/XLPE/DW/OSC/PVC/SWA/PVC, Fire resistant (IEC-60331)-RED | [6 empty] | 2200 |  | 2640
29 | RD-7T-1-F | 7 Traid * 1 mm² , CU/Mica-tape/XLPE/DW/ISC/DW/OSC//PVC Fire resistant (IEC-60331)-RED | [6 empty] | 50 |  | 60
30 | RD-12T-1-FA | 12 Traid * 1 mm² , CU/Mica-tape/XLPE/DW/ISC/DW/OSC/PVC/LC/PVC/SWA/PVC, Fire resistant (IEC-60331)-RED | [6 empty] | 4270 |  | 5124
31 | SERIAL LINK | BY VENDOR | [6 empty] | 100 |  | 120
D01