## Cover
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
ELECTRICAL LOAD LIST
شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 7
9184 – 073 - 053 |  |  | BK |  | GCS | PEDCO | 120 |  | EL | LI | 0001 | D05
طرح نگهداشت و افزایش تولید 27 مخزن
ELECTRICAL LOAD LIST نگهداشت و افزایش تولید میدان نفتی بینک
D05 |  | Feb.2023 |  | IFA |  |  |  | H.Shakiba |  |  | M.Fakharian |  | M.Mehrshad
D04 |  | Jul.2022 |  | IFA |  |  |  | H.Shakiba |  |  | M.Fakharian |  | M.Mehrshad
D03 |  | May.2022 |  | IFA |  |  |  | H.Shakiba |  |  | M.Fakharian |  | M.Mehrshad
D02 |  | Mar.2022 |  | IFA |  |  |  | H.Shakiba |  |  | M.Fakharian |  | M.Mehrshad
D01 |  | Jan.2022 |  | IFA |  |  |  | H.Shakiba |  |  | M.Fakharian |  | M.Mehrshad
D00 |  | Nov.2021 |  | IFC |  |  |  | H.Shakiba |  |  | M.Fakharian |  | M.Mehrshad
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
Class: 1 |  |  |  | CLIENT Doc. Number: F0Z-709066
status: | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved

## Revision
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
ELECTRICAL LOAD LIST
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 7
9184 – 073 - 053 |  |  | BK | GCS |  | PEDCO | 120 | EL | LI | 0001 |  | D05
REVISION RECORD SHEET
Page | D02 | D03 | D04 |  | D05 |  | D06 |  | Page |  | D02 |  | D03 |  | D04 | D05 | D06
1 | X | X | X |  | X |  |  |  | 51
2 | X | X | X |  | X |  |  |  | 52
3 | X | X | X | [5 empty] | 53
4 | X | X | X | [5 empty] | 54
5 | X | X | X |  | X |  |  |  | 55
6 | X | X | X |  | X |  |  |  | 56
7 | X | X | X |  | X |  |  |  | 57
8 | [8 empty] | 58
9 | [8 empty] | 59
10 | [8 empty] | 60
11 | [8 empty] | 61
12 | [8 empty] | 62
13 | [8 empty] | 63
14 | [8 empty] | 64
15 | [8 empty] | 65
16 | [8 empty] | 66
17 | [8 empty] | 67
18 | [8 empty] | 68
19 | [8 empty] | 69
20 | [8 empty] | 70
21 | [8 empty] | 71
22 | [8 empty] | 72
23 | [8 empty] | 73
24 | [8 empty] | 74
25 | [8 empty] | 75
26 | [8 empty] | 76
27 | [8 empty] | 77
28 | [8 empty] | 78
29 | [8 empty] | 79
30 | [8 empty] | 80
31 | [8 empty] | 81
32 | [8 empty] | 82
33 | [8 empty] | 83
34 | [8 empty] | 84
35 | [8 empty] | 85
36 | [8 empty] | 86
37 | [8 empty] | 87
38 | [8 empty] | 88
39 | [8 empty] | 89
40 | [8 empty] | 90
41 | [8 empty] | 91
42 | [8 empty] | 92
43 | [8 empty] | 93
44 | [8 empty] | 94
45 | [8 empty] | 95
46 | [8 empty] | 96
47 | [8 empty] | 97
48 | [8 empty] | 98
49 | [8 empty] | 99
50 | [8 empty] | 100

## Abb
Service Type:
N : Normal Load
E : Emergency Load
Load Duty:
C : Continuous Load
I : Intermitant Load
S : Stand By Load
LR/FL: Loacked Rotor / Full Load Current
Load Type:
M: Motor
F: Non-Motor
Definition of API Factor
1.25 for Motor Power < 22kW,
1.15 for Motor Power between, 22kW and 55kW
1.1 for Motor Power > 55kW
Height derating factor can be determined as follows if no manufacturer data is available:
Height Above Sea Level | Height Factor
< 1000 m | 1
1000 < Height < 1500 m | 0.97
1500 m > | 0.94
Coolant (Cooling) Factor is 0.88 according to basic document for motor feeder type.
LV Feeder Type:
F1: Simple 4-Pole MCCB Feeder with Thermal/Magnetic Trips, for I<63A Feeders
F2: Simple 4-Pole MCCB Feeder with Thermal/Magnetic Trips, for 63A=<I<100A Feeders
F3: Simple 4-Pole MCCB Feeder with Thermal/Magnetic Trips, for 100A=<I Feeders
F4: Simple 3-Pole MCCB Feeder with Thermal/Magnetic Trips, for I<63A Feeders
F5: Simple 3-Pole MCCB Feeder with Thermal/Magnetic Trips, for 63A=<I<100A Feeders
F6: Simple 3-Pole MCCB Feeder with Thermal/Magnetic Trips, for 100A=<I Feeders
F7: Simple 2-Pole MCCB Feeder for Feeding Single Phase Loads (Ph+N or 2-Ph)
M1: Direct on Line Motor Starter Feeders for 0.4 ≤ P < 4kW (Switch Fuse + Contactor + Bimetal + R/L Signaling)
M2: Direct on Line Motor Starter Feeders for 4kW ≤ P < 18.5kW (Switch Fuse + Contactor + Bimetal + R/L Signaling + R/L Ammeter)
M3: Direct on Line Motor Starter Feeders for 18.5kW ≤ P <30 (Switch Fuse + Contactor + Bimetal + R/L Signaling + R/L Ammeter (49, 50G, Phase Control))
M4: Direct on Line Motor Starter Feeders for 30kW ≤ P (Switch Fuse + Contactor + Overload CT + R/L Signaling + R/L Ammeter + Motor Protection Relay (49, 50G, Phase Control))
MV Feeder Type:
C1: 11 KV Incoming Feeder
C2: Outgoing Transformer 2000 KVA
C3: Outgoing Motor Starter <1000 KW
C4: Bus Coupler 11 KV
تسهیلات
ELECTRICAL LOAD LIST
شماره صفحه: 3 از 7
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
سطح‌الارض
احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
120
EL
LI
0001
D05
بسته کاری
GCS
پروژه
BK

## MV
Item NO | Rev | Bus | Equipment Number | Load Description | Service Type | Load Duty | Diversity Factor for Demand Load | NO Phases | Rated Voltage (V) | Load Type | Starting Method | BHP (Kw) | API Factor | Coolant Factor | Height Factor | Mechanical Power (Kw) | Rated Power (Kw) | Eff. (%) | Power Factor | Load Factor (%) | LR/FL | Current Normal Operation(A) | Starting Conditions Current (A) | Absorbed Peak Active Power (Kw) | Absorbed Peak Reactive Power (Kvar) | Absorbed Peak Apparent Power (Kva) | Feeder Type | Nameplate (KW) | Efficency | Power Factor | Is/In
1 | D02 | GCS-11-SWG-001A | C-2101A | First & Second Stage Gas Compressor A | N | C | 1 | 3 | 11 | M | DOL | 932 | 1.1 | 0.88 | 1 | 1165 | 1250 | 95 | 77 | 74.56 | 6 | 89.6897 | 538.138 | 981.0526 | 812.9281 | 1274.0943 | C3 | 160 | 92.8 | 82 | 6
2 | D02 | GCS-11-SWG-001B | C-2101B | First & Second Stage Gas Compressor B | N | C | 1 | 3 | 11 | M | DOL | 932 | 1.1 | 0.88 | 1 | 1165 | 1250 | 95 | 77 | 74.56 | 6 | 89.6897 | 538.138 | 981.0526 | 812.9281 | 1274.0943 | C3 | 200 | 92.8 | 82 | 6
3 | D02 | GCS-11-SWG-001A | C-2101C | First & Second Stage Gas Compressor C | N | S | 0.1 | 3 | 11 | M | DOL | 932 | 1.1 | 0.88 | 1 | 1165 | 1250 | 95 | 77 | 74.56 | 6 | 89.6897 | 538.138 | 98.1053 | 81.2928 | 127.4094 | C3 | 250 | 92.8 | 82 | 6
4 | D00 | GCS-11-SWG-001B | P-2301A | Fire Water Electric Pump | N | I | 0.75 | 3 | 3.3 | M | DOL | 220 | 1.1 | 0.88 | 1 | 275 | 300 | 92 | 82 | 73.3333 | 6 | 69.5737 | 417.4421 | 179.3478 | 125.1856 | 218.7169 | C3 | 315 | 92.8 | 82.5 | 6
5 | D03 | GCS-11-SWG-001A | GCS-TR-001 | Transformer-001 11/.42 KV | N | C | 1 | 3 | 11 | F | - | - | - | - | - | - | 1000 | 100 | 80 | 100 | 1 | 65.608 | - | 1000 | 750 | 1250 | C2 | 375 | 94 | 84 | 6
6 | D03 | GCS-11-SWG-001B | GCS-TR-002 | Transformer-002 11/.42 KV | N | C | 1 | 3 | 11 | F | - | - | - | - | - | - | 1000 | 100 | 80 | 100 | 1 | 65.608 | - | 1000 | 750 | 1250 | C2 | 400 | 94 | 84 | 6
[28 empty] | 450 | 94 | 84 | 6
[28 empty] | 500 | 94 | 84 | 6
[28 empty] | 560 | 94 | 84 | 6
[19 empty] | GCS-11-SWG-001A | [8 empty] | 630 | 94 | 86 | 6
[19 empty] | Continuous |  | Intermittent |  | Standby |  |  |  |  | 710 | 94.5 | 86 | 6
[19 empty] | Avtive Power (Kw) | Reactive Power (Kvar) | Avtive Power (Kw) | Reactive Power (Kvar) | Avtive Power (Kw) | Reactive Power (Kvar) |  |  |  | 800 | 94.5 | 86 | 6
[19 empty] | 1981.0526 | 1562.9281 | 0 | 0 | 98.1053 | 81.2928 |  |  |  | 900 | 95.5 | 87 | 6
[19 empty] | Power Calculation |  | Avtive Power (Kw) | Reactive Power (Kvar) | Apparent power (KVA) | Power Factor
[19 empty] | Maximum Normal Running Load |  | 1981.0526 | 1562.9281 | 2523.3537 | 0.78509
[19 empty] | Peak Load |  | 2079.1579 | 1644.2209 | 2650.7282 | 0.78437
[19 empty] | Peak Load |  |  |  | 2650.7282
GCS-11-SWG-001B
[19 empty] | Continuous |  | Intermittent |  | Standby
[19 empty] | Avtive Power (Kw) | Reactive Power (Kvar) | Avtive Power (Kw) | Reactive Power (Kvar) | Avtive Power (Kw) | Reactive Power (Kvar)
[19 empty] | 1981.0526 | 1562.9281 | 179.3478 | 125.1856 | 0 | 0
[19 empty] | Power Calculation |  | Avtive Power (Kw) | Reactive Power (Kvar) | Apparent power (KVA) | Power Factor
[19 empty] | Maximum Normal Running Load |  | 2160.4005 | 1688.1136 | 2741.7253 | 0.78797
[19 empty] | Peak Load |  | 2160.4005 | 1688.1136 | 2741.7253 | 0.78797
[19 empty] | Peak Load |  |  |  | 2741.7253
The Peak load on 11 Kv switchgear "GCS-11-SWG-001A" is 2650 KVA while demand load on "GCS-11-SWG-001B" is aboat 2742 KVA.
Fire water Pump will fed from 800 kVA trnasformer 11/3.3 KV, which will be finalized after power flow calculation.
تسهیلات
ELECTRICAL LOAD LIST
شماره صفحه: 4 از 7
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
سطح‌الارض
احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
120
EL
LI
0001
D05
بسته کاری
GCS
پروژه
BK

## LV
Item NO | Rev | Bus | Equipment Number | Load Description | Service Type | Load Duty | Diversity Factor for Demand Load | NO Phases | Rated Voltage (V) | Load Type | Starting Method | BHP (Kw) | API Factor | Coolant Factor | Height Factor | Mechanical Power (Kw) | Rated Power (Kw) | Eff. (%) | Power Factor | Load Factor (%) | LR/FL | Current Normal Operation(A) | Absorbed Peak Active Power (Kw) | Absorbed Peak Reactive Power (Kvar) | Feeder Type | Nameplate (KW) | Efficency | Power Factor | Is/In
[26 empty] | 0.55 | 75.3 | 76 | 4.6
1 | D05 | GCS-400-NSWG-001A | AC-2121A | First Stage Air Cooler 21A | N | C | 1 | 3 | 0.4 | M | DOL | 8.5 | 1.25 | 0.88 | 1 | 12.0739 | 15 | 91.8 | 82 | 56.6667 | 7 | 28.7617 | 9.2593 | 6.463 | M3 | 0.75 | 78.2 | 74 | 4.7
2 | D05 | GCS-400-NSWG-001A | AC-2122A | First Stage Air Cooler 22A | N | C | 1 | 3 | 0.4 | M | DOL | 8.5 | 1.25 | 0.88 | 1 | 12.0739 | 15 | 91.8 | 82 | 56.6667 | 7 | 28.7617 | 9.2593 | 6.463 | M3 | 1.1 | 83.9 | 80 | 4.7
3 | D05 | GCS-400-NSWG-001B | AC-2121B | First Stage Air Cooler 21B | N | C | 1 | 3 | 0.4 | M | DOL | 8.5 | 1.25 | 0.88 | 1 | 12.0739 | 15 | 91.8 | 82 | 56.6667 | 7 | 28.7617 | 9.2593 | 6.463 | M3 | 1.5 | 85.6 | 82 | 5
4 | D05 | GCS-400-NSWG-001B | AC-2122B | First Stage Air Cooler 22B | N | C | 1 | 3 | 0.4 | M | DOL | 8.5 | 1.25 | 0.88 | 1 | 12.0739 | 15 | 91.8 | 82 | 56.6667 | 7 | 28.7617 | 9.2593 | 6.463 | M3 | 2.2 | 86.8 | 77 | 5.2
5 | D05 | GCS-400-NSWG-001A | AC-2121C | First Stage Air Cooler 21C | N | S | 0.1 | 3 | 0.4 | M | DOL | 8.5 | 1.25 | 0.88 | 1 | 12.0739 | 15 | 91.8 | 82 | 56.6667 | 7 | 28.7617 | 0.92593 | 0.6463 | M3 | 3 | 87.5 | 81 | 6
6 | D05 | GCS-400-NSWG-001A | AC-2122C | First Stage Air Cooler 22C | N | S | 0.1 | 3 | 0.4 | M | DOL | 8.5 | 1.25 | 0.88 | 1 | 12.0739 | 15 | 91.8 | 82 | 56.6667 | 7 | 28.7617 | 0.92593 | 0.6463 | M3 | 4 | 88.3 | 76 | 6.3
7 | D05 | GCS-400-NSWG-001A | AC-2131A | Second Stage Air Cooler 31A | N | C | 1 | 3 | 0.4 | M | DOL | 19 | 1.15 | 0.88 | 1 | 24.8295 | 30 | 92 | 80 | 63.3333 | 7 | 58.8332 | 20.6522 | 15.4891 | M3 | 5.5 | 89.3 | 84 | 6.5
8 | D05 | GCS-400-NSWG-001A | AC-2132A | Second Stage Air Cooler 32A | N | C | 1 | 3 | 0.4 | M | DOL | 19 | 1.15 | 0.88 | 1 | 24.8295 | 30 | 92 | 80 | 63.3333 | 7 | 58.8332 | 20.6522 | 15.4891 | M3 | 7.5 | 90.3 | 87 | 6.5
9 | D05 | GCS-400-NSWG-001B | AC-2131B | Second Stage Air Cooler 31B | N | C | 1 | 3 | 0.4 | M | DOL | 19 | 1.15 | 0.88 | 1 | 24.8295 | 30 | 92 | 80 | 63.3333 | 7 | 58.8332 | 20.6522 | 15.4891 | M3 | 9 | 90.7 | 81 | 6.5
10 | D05 | GCS-400-NSWG-001B | AC-2132B | Second Stage Air Cooler 32B | N | C | 1 | 3 | 0.4 | M | DOL | 19 | 1.15 | 0.88 | 1 | 24.8295 | 30 | 92 | 80 | 63.3333 | 7 | 58.8332 | 20.6522 | 15.4891 | M3 | 11 | 92 | 81 | 6.5
11 | D05 | GCS-400-NSWG-001A | AC-2131C | Second Stage Air Cooler 31C | N | S | 0.1 | 3 | 0.4 | M | DOL | 19 | 1.15 | 0.88 | 1 | 24.8295 | 30 | 92 | 80 | 63.3333 | 7 | 58.8332 | 2.0652 | 1.5489 | M3 | 15 | 91.8 | 82 | 7
12 | D05 | GCS-400-NSWG-001A | AC-2132C | Second Stage Air Cooler 32C | N | S | 0.1 | 3 | 0.4 | M | DOL | 19 | 1.15 | 0.88 | 1 | 24.8295 | 30 | 92 | 80 | 63.3333 | 7 | 58.8332 | 2.0652 | 1.5489 | M3 | 18.5 | 92.3 | 84 | 7
13 | D04 | GCS-400-NSWG-001E | PK-C-2203A | Instrument & Plant Air Package A | E | C | 1 | 3 | 0.4 | F | - | - | - | - | - | - | 50 | 100 | 85 | 100 | 1 | 84.9045 | 50 | 30.9872 | F3 | 22 | 90 | 79 | 7
14 | D04 | GCS-400-NSWG-001E | PK-C-2203B | Instrument & Plant Air Package B | E | S | 0.1 | 3 | 0.4 | F | - | - | - | - | - | - | 50 | 100 | 85 | 100 | 1 | 84.9045 | 5 | 3.0987 | F3 | 25 | 93.8 | 86 | 7
15 | D05 | GCS-400-NSWG-001A | PK-Dr-2203A | Air Dryer Package A | N | C | 1 | 3 | 0.4 | F | - | - | - | - | - | - | 2 | 100 | 85 | 100 | 1 | 3.3962 | 2 | 1.2395 | F1 | 30 | 92 | 80 | 7
16 | D05 | GCS-400-NSWG-001B | PK-Dr-2203B | Air Dryer Package B | N | S | 0.1 | 3 | 0.4 | F | - | - | - | - | - | - | 2 | 100 | 85 | 100 | 1 | 3.3962 | 0.2 | 0.12395 | F1 | 37 | 93.8 | 82 | 7
17 | D03 | GCS-400-NSWG-001A | PK-C-2204 | Air Compressor for N2 Package | N | C | 1 | 3 | 0.4 | F | - | - | - | - | - | - | 30 | 100 | 85 | 100 | 1 | 50.9427 | 30 | 18.5923 | F2 | 45 | 91 | 82 | 7
18 | D02 | GCS-400-NSWG-001A | PK-2204 | Nitrogen Package | N | C | 1 | 3 | 0.4 | F | - | - | - | - | - | - | 2 | 100 | 85 | 100 | 1 | 3.3962 | 2 | 1.2395 | F1 | 75 | 93 | 83 | 7
19 | D05 | GCS-400-NSWG-001A | PK-2201 | LP Flare Package | N | C | 1 | 3 | 0.4 | F | - | - | - | - | - | - | 22.5 | 100 | 95 | 100 | 1 | 34.1852 | 22.5 | 7.3954 | F1
20 | D00 | GCS-400-NSWG-001E | IG-2201 | LP Flare Ignition Package | E | I | 0.75 | 3 | 0.4 | F | - | - | - | - | - | - | 2 | 100 | 95 | 100 | 1 | 3.0387 | 1.5 | 0.49303 | F1
21 | D04 | GCS-400-NSWG-001B | PK-2207 | Corrosion Inhibitor Package | N | C | 1 | 3 | 0.4 | F | - | - | - | - | - | - | 2 | 100 | 95 | 100 | 1 | 3.0387 | 2 | 0.65737 | F1
22 | D04 | GCS-400-NSWG-001B | PK-2208 | Methanol Injection Package | N | I | 0.75 | 3 | 0.4 | F | - | - | - | - | - | - | 0 | 100 | 95 | 100 | 1 | 0 | 0 | 0 | F1
23 | D00 | GCS-400-NSWG-001B | PK-2101 | Dehydration Package | N | C | 1 | 3 | 0.4 | F | - | - | - | - | - | - | 20 | 100 | 95 | 100 | 1 | 30.3869 | 20 | 6.5737 | F1
24 | D04 | GCS-400-NSWG-001E | P-2203A | Sump Pump A | E | I | 0.75 | 3 | 0.4 | M | DOL | 1 | 1.25 | 0.88 | 1 | 1.4205 | 2.2 | 86.8 | 77 | 45.4545 | 5.2 | 4.7511 | 0.86406 | 0.71598 | M1
25 | D04 | GCS-400-NSWG-001E | P-2203B | Sump Pump B | E | I | 0.75 | 3 | 0.4 | M | DOL | 1 | 1.25 | 0.88 | 1 | 1.4205 | 2.2 | 86.8 | 77 | 45.4545 | 5.2 | 4.7511 | 0.86406 | 0.71598 | M1
26 | D04 | GCS-400-NSWG-001E | P-2202A | Closed Drain Pump A | E | I | 0.75 | 3 | 0.4 | M | DOL | 2.9 | 1.25 | 0.88 | 1 | 4.1193 | 5.5 | 89.3 | 84 | 52.7273 | 6.5 | 10.5831 | 2.4356 | 1.5732 | M1
27 | D04 | GCS-400-NSWG-001E | P-2202B | Closed Drain Pump B | E | I | 0.75 | 3 | 0.4 | M | DOL | 2.9 | 1.25 | 0.88 | 1 | 4.1193 | 5.5 | 89.3 | 84 | 52.7273 | 6.5 | 10.5831 | 2.4356 | 1.5732 | M1
28 | D05 | GCS-400-NSWG-001E | P-2101A | Slug Pump A | E | I | 0.75 | 3 | 0.4 | M | DOL | 7 | 1.25 | 0.88 | 1 | 9.9432 | 11 | 92 | 81 | 63.6364 | 6.5 | 21.3059 | 5.7065 | 4.1315 | M4
29 | D05 | GCS-400-NSWG-001E | P-2101B | Slug Pump B | E | I | 0.75 | 3 | 0.4 | M | DOL | 7 | 1.25 | 0.88 | 1 | 9.9432 | 11 | 92 | 81 | 63.6364 | 6.5 | 21.3059 | 5.7065 | 4.1315 | M4
30 | D05 | GCS-400-NSWG-001E | P-2302A | Fire Water Jockey Pump A | E | I | 0.75 | 3 | 0.4 | F | - | 12 | 1.25 | 0.88 | 1 | - | 20 | 100 | 95 | 60 | 1 | 30.3869 | 15 | 4.9303 | F2
31 | D05 | GCS-400-NSWG-001E | P-2302B | Fire Water Jockey Pump B | E | I | 0.75 | 3 | 0.4 | F | - | 12 | 1.25 | 0.88 | 1 | - | 20 | 100 | 95 | 60 | 1 | 30.3869 | 15 | 4.9303 | F2
32 | D04 | GCS-400-NSWG-001B | P-2209 | Potable Water Pump | N | I | 0.75 | 3 | 0.4 | M | DOL | 1 | 1.25 | 0.88 | 1 | 1.4205 | 2.2 | 86.8 | 77 | 45.4545 | 5.2 | 4.7511 | 0.86406 | 0.71598 | M1
33 | D05 | GCS-400-NSWG-001B | P-2206 | Diesel Oil Pump | N | I | 0.75 | 3 | 0.4 | M | DOL | 0.3 | 1.25 | 0.88 | 1 | 0.42614 | 1.1 | 83.9 | 80 | 27.2727 | 4.7 | 2.3655 | 0.26818 | 0.20113 | M1
34 | D04 | GCS-400-NSWG-001E | P-2201A | LP Flare K.O. Drum Pump A | E | I | 0.75 | 3 | 0.4 | M | DOL | 0.6 | 1.25 | 0.88 | 1 | 0.85227 | 1.1 | 83.9 | 80 | 54.5455 | 4.7 | 2.3655 | 0.53635 | 0.40226 | M1
35 | D04 | GCS-400-NSWG-001E | P-2201B | LP Flare K.O. Drum Pump B | E | I | 0.75 | 3 | 0.4 | M | DOL | 0.6 | 1.25 | 0.88 | 1 | 0.85227 | 1.1 | 83.9 | 80 | 54.5455 | 4.7 | 2.3655 | 0.53635 | 0.40226 | M1
36 | D04 | GCS-400-NSWG-001A | P-2103A | Glycol Transfer Pump A | N | I | 0.75 | 3 | 0.4 | M | DOL | 1 | 1.25 | 0.88 | 1 | 1.4205 | 1.5 | 85.6 | 82 | 66.6667 | 5 | 3.0845 | 0.87617 | 0.61157 | M1
37 | D04 | GCS-400-NSWG-001B | P-2103B | Glycol Transfer Pump B | N | I | 0.75 | 3 | 0.4 | M | DOL | 1 | 1.25 | 0.88 | 1 | 1.4205 | 1.5 | 85.6 | 82 | 66.6667 | 5 | 3.0845 | 0.87617 | 0.61157 | M1
38 | D00 | GCS-400-NSWG-001B | P-2102 | Glycol Manual Pump | N | I | 0.75 | 3 | 0.4 | M | DOL | 0.5 | 1.25 | 0.88 | 1 | 0.71023 | 1.1 | 83.9 | 80 | 45.4545 | 4.7 | 2.3655 | 0.44696 | 0.33522 | M1
39 | D04 | GCS-400-NSWG-001B | P-2104 | Glycol Drain Pump | N | I | 0.75 | 3 | 0.4 | M | DOL | 0.8 | 1.25 | 0.88 | 1 | 1.1364 | 1.1 | 83.9 | 80 | 72.7273 | 4.7 | 2.3655 | 0.71514 | 0.53635 | M1
40 | D01 | GCS-400-NSWG-001A | P-2105A | Glycol Sump Pump A | N | I | 0.75 | 3 | 0.4 | M | DOL | 0 | 1.25 | 0.88 | 1 | 0 | 0.75 | 78.2 | 74 | 0 | 4.7 | 1.8707 | 0 | 0 | M1
41 | D01 | GCS-400-NSWG-001B | P-2105B | Glycol Sump Pump B | N | I | 0.75 | 3 | 0.4 | M | DOL | 0 | 1.25 | 0.88 | 1 | 0 | 0.75 | 78.2 | 74 | 0 | 4.7 | 1.8707 | 0 | 0 | M1
42 | D04 | GCS-400-NSWG-001B | GCS-400-CR-01 | Main Compressor Crane | N | I | 0.75 | 3 | 0.4 | F | - | - | - | - | - | - | 10 | 100 | 90 | 100 | 1 | 16.0375 | 7.5 | 3.6324 | F1
43 | D04 | GCS-400-NSWG-001A | GCS-400-CR-02 | Fire Water Pumps Crane | N | I | 0.75 | 3 | 0.4 | F | - | - | - | - | - | - | 5 | 100 | 90 | 100 | 1 | 8.0188 | 3.75 | 1.8162 | F1
44 | D04 | GCS-400-NSWG-001B | GCS-400-NDP-01 | Process Area Normal Distribution Panel | N | C | 1 | 3 | 0.4 | F | - | - | - | - | - | - | 20 | 100 | 85 | 100 | 1 | 33.9618 | 20 | 12.3949 | F1
45 | D04 | GCS-400-NSWG-001E | GCS-400-EDP-01 | Process Area Emergency Distribution Panel | E | C | 1 | 3 | 0.4 | F | - | - | - | - | - | - | 10 | 100 | 85 | 100 | 1 | 16.9809 | 10 | 6.1974 | F1
46 | D04 | GCS-400-NSWG-001A | GCS-400-NDP-02 | Utility Area Normal Distribution Panel | N | C | 1 | 3 | 0.4 | F | - | - | - | - | - | - | 10 | 100 | 85 | 100 | 1 | 16.9809 | 10 | 6.1974 | F1
47 | D04 | GCS-400-NSWG-001E | GCS-400-EDP-02 | Utility Area Emergency Distribution Panel | E | C | 1 | 3 | 0.4 | F | - | - | - | - | - | - | 5 | 100 | 85 | 100 | 1 | 8.4904 | 5 | 3.0987 | F1
48 | D03 | GCS-400-NSWG-001B | GCS-400-WS-01 | Welding Receptacle (3Phase)(Process Area) | N | I | 0.75 | 3 | 0.4 | F | - | - | - | - | - | - | 35 | 100 | 85 | 100 | 1 | 59.4331 | 26.25 | 16.2683 | F2
49 | D03 | GCS-400-NSWG-001A | GCS-400-WS-02 | Welding Receptacle (3Phase)(Utility Area) | N | I | 0.75 | 3 | 0.4 | F | - | - | - | - | - | - | 35 | 100 | 85 | 100 | 1 | 59.4331 | 26.25 | 16.2683 | F2
50 | D02 | GCS-400-NSWG-001A | GCS-400-CP01 | Cathodic Protection Transformer Rectifier1 | N | C | 1 | 3 | 0.4 | F | - | - | - | - | - | - | 5 | 90 | 100 | 100 | 1 | 8.0188 | 5.5556 | 0 | F1
51 | D01 | GCS-400-NSWG-001B | GCS-400-CP02 | Cathodic Protection Transformer Rectifier2 | N | C | 1 | 3 | 0.4 | F | - | - | - | - | - | - | 10 | 90 | 100 | 100 | 1 | 16.0375 | 11.1111 | 0 | F1
52 | D05 | GCS-400-NSWG-001E | CTRL- HVAC | HVAC Panel for Control Room | E | C | 1 | 3 | 0.4 | F | - | - | - | - | - | - | 140 | 100 | 85 | 100 | 1 | 237.7325 | 140 | 86.7642 | F3
53 | D01 | GCS-400-NSWG-001A | GCS-110-CHG-001 | 110VDC Charger 1 | N | S | 0.1 | 3 | 0.4 | F | - | - | - | - | - | - | 20 | 90 | 85 | 100 | 1 | 37.7353 | 2.2222 | 1.3772 | F1
54 | D04 | GCS-400-NSWG-001E | GCS-110-CHG-002 | 110VDC Charger 2 | E | C | 1 | 3 | 0.4 | F | - | - | - | - | - | - | 20 | 90 | 85 | 100 | 1 | 37.7353 | 22.2222 | 13.7721 | F1
55 | D01 | GCS-400-NSWG-001A | GCS-24-CHG-001 | 24VDC Charger 1 | N | S | 0.1 | 3 | 0.4 | F | - | - | - | - | - | - | 18.5 | 90 | 85 | 100 | 1 | 34.9052 | 2.0556 | 1.2739 | F1
56 | D04 | GCS-400-NSWG-001E | GCS-24-CHG-002 | 24VDC Charger 2 | E | C | 1 | 3 | 0.4 | F | - | - | - | - | - | - | 18.5 | 90 | 85 | 100 | 1 | 34.9052 | 20.5556 | 12.7392 | F1
57 | D05 | GCS-400-NSWG-001B | GCS-110-UPS-001 | 110VAC UPS 1 | N | S | 0.1 | 3 | 0.4 | F | - | - | - | - | - | - | 36 | 90 | 85 | 100 | 1 | 67.9236 | 4 | 2.479 | F2
58 | D05 | GCS-400-NSWG-001E | GCS-110-UPS-002 | 110VAC UPS 2 | E | C | 1 | 3 | 0.4 | F | - | - | - | - | - | - | 36 | 90 | 85 | 100 | 1 | 67.9236 | 40 | 24.7898 | F2
59 | D01 | GCS-400-NSWG-001E | GCS-110-UPS-Bypass | 110VAC UPS By Pass | E | S | 0.1 | 3 | 0.4 | F | - | - | - | - | - | - | 20 | 90 | 85 | 100 | 1 | 37.7353 | 2.2222 | 1.3772 | F1
60 | D04 | GCS-400-NSWG-001E | GCS-400-Non UPS | Non-UPS Load for Instrument | E | C | 1 | 3 | 0.4 | F | - | - | - | - | - | - | 0 | 100 | 85 | 100 | 1 | 0 | 0 | 0 | F1
61 | D04 | GCS-400-NSWG-001B | GCS-400-NDB-CAP | Capacitor Room Normal Lighting Panel | N | C | 1 | 3 | 0.4 | F | - | - | - | - | - | - | 0 | 100 | 85 | 100 | 1 | 0 | 0 | 0 | F1
62 | D02 | GCS-400-NSWG-001E | ELP-105 | Capacitor Room Emergency Lighting Panel | E | C | 1 | 3 | 0.4 | F | - | - | - | - | - | - | 0 | 100 | 80 | 100 | 1 | 0 | 0 | 0 | F1
63 | D04 | GCS-400-NSWG-001A |  | MOV 1 | N | C | 1 | 3 | 0.4 | F | - | - | - | - | - | - | 2 | 100 | 85 | 100 | 1 | 3.3962 | 2 | 1.2395 | F1
64 | D04 | GCS-400-NSWG-001B |  | MOV 2 | N | S | 0.1 | 3 | 0.4 | F | - | - | - | - | - | - | 2 | 100 | 85 | 100 | 1 | 3.3962 | 0.2 | 0.12395 | F1
65 | D01 | GCS-400-NSWG-001B |  | MOV 3 | N | C | 1 | 3 | 0.4 | F | - | - | - | - | - | - | 0 | 100 | 85 | 100 | 1 | 0 | 0 | 0 | F1
66 | D01 | GCS-400-NSWG-001B |  | MOV 4 | N | C | 1 | 3 | 0.4 | F | - | - | - | - | - | - | 0 | 100 | 85 | 100 | 1 | 0 | 0 | 0 | F1
67 | D04 | GCS-400-NSWG-001E | GCS-230-FDP 01 | Fire Diesel Panel 01 (Electrical Main Motor) | E | C | 1 | 1 | 0.23 | F | - | - | - | - | - | - | 1 | 100 | 85 | 100 | 1 | 2.9532 | 1 | 0.61974 | F7
68 | D04 | GCS-400-NSWG-001E | GCS-230-FDP 02 | Fire Diesel Panel 02 (Diesel Engine) | E | C | 1 | 1 | 0.23 | F | - | - | - | - | - | - | 1 | 100 | 85 | 100 | 1 | 2.9532 | 1 | 0.61974 | F7
69 | D05 | GCS-400-NSWG-001A | MCC-2101A | Auxiliary Panel for Gas Compressor C-2101A | N | C | 1 | 3 | 0.4 | F | - | - | - | - | - | - | 50 | 100 | 85 | 100 | 1 | 84.9045 | 50 | 30.9872 | F1
70 | D05 | GCS-400-NSWG-001B | MCC-2101B | Auxiliary Panel for Gas Compressor C-2101B | N | C | 1 | 3 | 0.4 | F | - | - | - | - | - | - | 50 | 100 | 85 | 100 | 1 | 84.9045 | 50 | 30.9872 | F1
71 | D05 | GCS-400-NSWG-001B | MCC-2101C | Auxiliary Panel for Gas Compressor C-2101C | N | S | 0.1 | 3 | 0.4 | F | - | - | - | - | - | - | 50 | 100 | 85 | 100 | 1 | 84.9045 | 5 | 3.0987 | F1
72 | D01 | GCS-400-NSWG-001E | SPH-01 | Space Heater & Lighting for New LV Switchgear | E | C | 1 | 1 | 0.23 | F | - | - | - | - | - | - | 2 | 100 | 85 | 100 | 1 | 5.9064 | 2 | 1.2395 | F7
73 | D01 | GCS-400-NSWG-001E | SPH-02 | Space Heater & Lighting for MV Switchgear | E | C | 1 | 1 | 0.23 | F | - | - | - | - | - | - | 2 | 100 | 85 | 100 | 1 | 5.9064 | 2 | 1.2395 | F7
74 | D04 | GCS-400-NSWG-001B | GCS-400-NDP-CRM | Control Room Normal Distribution Panel | N | C | 1 | 3 | 0.4 | F | - | - | - | - | - | - | 30 | 100 | 85 | 100 | 1 | 50.9427 | 30 | 18.5923 | F2
75 | D04 | GCS-400-NSWG-001E | GCS-400-EDP-CRM | Control Room Emergency Distribution Panel | E | C | 1 | 3 | 0.4 | F | - | - | - | - | - | - | 23 | 100 | 85 | 100 | 1 | 39.056 | 23 | 14.2541 | F1
76 | D04 | GCS-400-NSWG-001E | GCS-400-EDB-CAP | Capacitor Room Emergency Lighting Panel | E | C | 1 | 3 | 0.4 | F | - | - | - | - | - | - | 0 | 100 | 85 | 100 | 1 | 0 | 0 | 0 | F1
77 | D05 | GCS-400-NSWG-001A | GCS-400-NDP-SWHVAC | Switchgear HVAC Panel | N | C | 1 | 3 | 0.4 | F | - | - | - | - | - | - | 30 | 100 | 85 | 100 | 1 | 50.9427 | 30 | 18.5923 | F2
78 | D04 | GCS-400-NSWG-001A | LV-HVAC01 | Split Feeder (HVAC Feeder-01 for LV Room) | N | C | 1 | 3 | 0.4 | F | - | - | - | - | - | - | 0 | 100 | 90 | 100 | 1 | 0 | 0 | 0 | F1
79 | D04 | GCS-400-NSWG-001B | LV-HVAC02 | Split Feeder (HVAC Feeder-02 for LV Room) | N | C | 1 | 3 | 0.4 | F | - | - | - | - | - | - | 0 | 100 | 90 | 100 | 1 | 0 | 0 | 0 | F1
80 | D04 | GCS-400-NSWG-001A | MV-HVAC01 | Split Feeder (HVAC Feeder-01 for MV Room) | N | C | 1 | 3 | 0.4 | F | - | - | - | - | - | - | 0 | 100 | 90 | 100 | 1 | 0 | 0 | 0 | F1
81 | D04 | GCS-400-NSWG-001B | MV-HVAC02 | Split Feeder (HVAC Feeder-02 for MV Room) | N | C | 1 | 3 | 0.4 | F | - | - | - | - | - | - | 0 | 100 | 90 | 100 | 1 | 0 | 0 | 0 | F1
82 | D04 | GCS-400-NSWG-001A | CAP-HVAC01 | Split Feeder (HVAC Feeder-01 for Capacitor Room) | N | C | 1 | 3 | 0.4 | F | - | - | - | - | - | - | 0 | 100 | 90 | 100 | 1 | 0 | 0 | 0 | F1
83 | D04 | GCS-400-NSWG-001B | CAP-HVAC02 | Split Feeder (HVAC Feeder-02 for Capacitor Room) | N | C | 1 | 3 | 0.4 | F | - | - | - | - | - | - | 0 | 100 | 90 | 100 | 1 | 0 | 0 | 0 | F1
84 | D05 | GCS-400-NSWG-001E | EHTC | Electrical Heat Tracing Panel | E | C | 1 | 3 | 0.4 | F | - | - | - | - | - | - | 10 | 100 | 90 | 100 | 1 | 16.0375 | 10 | 4.8432 | F1
85 | D03 | GCS-400-NSWG-001A | CAP-01 | Capacitor Bank 1 | N | C | 1 | 3 | 0.4 | F | - | - | - | - | - | - | - | 100 | 100 | 100 | 1 | 216.5064 | - | 150 | F3
86 | D03 | GCS-400-NSWG-001B | CAP-02 | Capacitor Bank 2 | N | C | 1 | 3 | 0.4 | F | - | - | - | - | - | - | - | 100 | 100 | 100 | 1 | 216.5064 | - | 150 | F3
GCS-400-NSWG-001A
[19 empty] | Continuous |  | Intermittent |  | Standby
[19 empty] | Avtive Power (Kw) | Reactive Power (Kvar) | Avtive Power (Kw) | Reactive Power (Kvar) | Avtive Power (Kw) | Reactive Power (Kvar)
[19 empty] | 213.8784 | 129.3874 | 30.8762 | 18.6961 | 10.2601 | 7.0416
[13 empty] | GCS-400-NSWG-001A | [5 empty] | Power Calculation |  | Avtive Power (Kw) | Reactive Power (Kvar) | Apparent power (KVA) | Power Factor
[13 empty] | Max Intermittent (KW) | Max Standby (KW) | Max Intermittent (KVAR) | Max Standby (KVAR) |  |  | Maximum Normal Running Load (Demand) |  | 244.7546 | 148.0835 | 286.0656 | 0.85559
[19 empty] | Peak Load |  | 255.0147 | 155.1251 | 298.49 | 0.85435
[13 empty] | 35 | 22.2222 | 21.6911 | 15.4891 |  |  | Peak Load With 15% Spare (KVA) |  |  |  | 343.2635
GCS-400-NSWG-001B
[19 empty] | Continuous |  | Intermittent |  | Standby
[19 empty] | Avtive Power (Kw) | Reactive Power (Kvar) | Avtive Power (Kw) | Reactive Power (Kvar) | Avtive Power (Kw) | Reactive Power (Kvar)
[19 empty] | 192.934 | 113.1098 | 36.9205 | 22.301 | 9.4 | 5.8256
[13 empty] | GCS-400-NSWG-001B | [5 empty] | Power Calculation |  | Avtive Power (Kw) | Reactive Power (Kvar) | Apparent power (KVA) | Power Factor
[13 empty] | Max Intermittent (KW) | Max Standby (KW) | Max Intermittent (KVAR) | Max Standby (KVAR) |  |  | Maximum Normal Running Load (Demand) |  | 229.8545 | 135.4107 | 266.7754 | 0.8616
[19 empty] | Peak Load |  | 239.2545 | 141.2363 | 277.8316 | 0.86115
[13 empty] | 35 | 50 | 21.6911 | 30.9872 |  |  | Peak Load With 15% Spare (KVA) |  |  |  | 319.5063
GCS-400-NSWG-001E
[19 empty] | Continuous |  | Intermittent |  | Standby
[19 empty] | Avtive Power (Kw) | Reactive Power (Kvar) | Avtive Power (Kw) | Reactive Power (Kvar) | Avtive Power (Kw) | Reactive Power (Kvar)
[19 empty] | 326.7778 | 201.1645 | 50.5851 | 23.9994 | 7.2222 | 4.4759
[13 empty] | GCS-400-NSWG-001E | [5 empty] | Power Calculation |  | Avtive Power (Kw) | Reactive Power (Kvar) | Apparent power (KVA) | Power Factor
[13 empty] | Max Intermittent (KW) | Max Standby (KW) | Max Intermittent (KVAR) | Max Standby (KVAR) |  |  | Maximum Normal Running Load |  | 377.3629 | 225.1639 | 439.4332 | 0.85875
[19 empty] | Peak Load |  | 384.5851 | 229.6398 | 447.9287 | 0.85859
[13 empty] | 20 | 50 | 6.5737 | 30.9872 |  |  | Peak Load With 15% Spare (KVA) |  |  |  | 515.118
[8 empty] | 1. For each LV switchgear A & B, a separate transformer is needed to supply normal & emergency power. So the sum of apparent power will be about 1189KVA, which 2 transformers 1250 KVA are required. | [10 empty] | Total Peak Load on LV Switchgear
[21 empty] | Avtive Power (Kw) | Reactive Power (Kvar) | Apparent power (KVA) | Power Factor
[8 empty] | 2. Size of transformers shall be finalized in load flow and motor starting study. | [10 empty] | Peak Load |  | 878.8542 | 526.0012 | 1024.2373 | 0.85806
[8 empty] | 3. Power factor has been calculated while all capacitor banks are out of service. | [10 empty] | Peak Load With 15% Spare (KVA) |  |  |  | 1177.8729
تسهیلات
ELECTRICAL LOAD LIST
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
سطح‌الارض
احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
120
EL
LI
0001
D05
بسته کاری
GCS
پروژه
BK

## Calculation
NISOC |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
ELECTRICAL LOAD LIST
شماره پیمان: |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 7 از 7
9184 – 073 - 053 |  | BK | GCS | PEDCO | 120 | EL | LI | 0001 | D05
| 1. Mechanical Power (KW): | Mechanical Power for Motors = BHP(KW) x API Factor / (Cooling Factor x Height Factor)
| 2. Rated Power(KW): | Rated Power = The Nearest Size of The Equipment to Mechanical Power of Motors
| 3. Load Factor(%): | Load Factor = (BHP/Rated Power) x 100
| 4. Normal Operation(A): | Normal Operation (A) = Rated Power / (Sqrt(3) x Nominal Voltage x cosØ)
| 5. Starting Current(A): | Starting Current(A) = (LR/LF) x Normal Current
6. Electrical Power Demand (KW):
Electrical Absorbed Power Demand (KW) = BHP(KW) x Diversity Factor / Efficiency
Electrical Absorbed Power Demand (KW) = Rated Power(KW) x Diversity Factor / Efficiency
7. Electrical Reactive Power Demand (KVAR):
Electrical Reactive Power Demand (KVAR) = Electrical Absorbed Power Demand (KW) x Tangent(Ø
For "Electrical Demand" calculation, following "Diversity Factors" has been considered (based on peak loads):
Continous: 100% Diversity factor.
Intermittent: Normally less than 12 hours/day, As generaly 75%
Standby: Spare/Backup drives or systems, As generaly 10% or biggest standby load (which is bigger)
Notes
1- Electrical heat tracing for compressor will be supplied from Auxiliary MCC of each one