## Sheet2
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض
خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03)
I/O LIST
شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 9
9184 – 073 - 053 |  |  | BK |  | GCS | HY | 120 |  | IN | LI | 005 | V01
طرح نگهداشت و افزایش تولید 27 مخزن
I/O LIST نگهداشت و افزایش تولید میدان نفتی بینک
V01 |  | Aug.2023 |  | IFR |  |  |  | Havayar Co. |  |  | M.Fakharian |  | M.Mehrshad
V00 |  | MAY.2023 |  | IFR |  |  |  | Havayar Co. |  |  | M.Fakharian |  | M.Mehrshad
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
Class: 2 |  |  |  | CLIENT Doc. Number:
status:
IFR: Issued For Review
IFR: Issued For Review
IFI: Issued For Information
AFC: Approved For Construction

## Sheet1
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض
خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03)
I/O LIST
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 9
9184 – 073 - 053 |  |  | BK | GCS |  | HY | 120 | PM | LI | 0005 |  | V01
REVISION RECORD SHEET
Page | V00 | V01 | V02 |  | V03 |  | V04 |  | Page |  | V00 |  | V01 |  | V02 | V03 | V04
1 | X | X | [6 empty] | 65
2 | X | X | [6 empty] | 66
3 | X | X | [6 empty] | 67
4 | X | X | [6 empty] | 68
5 | X | X | [6 empty] | 69
6 | X | X | [6 empty] | 70
7 | X | X | [6 empty] | 71
8 | X | X | [6 empty] | 72
9 | X | X | [6 empty] | 73
10 | [8 empty] | 74
11 | [8 empty] | 75
12 | [8 empty] | 76
13 | [8 empty] | 77
14 | [8 empty] | 78
15 | [8 empty] | 79
16 | [8 empty] | 80
17 | [8 empty] | 81
18 | [8 empty] | 82
19 | [8 empty] | 83
20 | [8 empty] | 84
21 | [8 empty] | 85
22 | [8 empty] | 86
23 | [8 empty] | 87
24 | [8 empty] | 88
25 | [8 empty] | 89
26 | [8 empty] | 90
27 | [8 empty] | 91
28 | [8 empty] | 92
29 | [8 empty] | 93
30 | [8 empty] | 94
31 | [8 empty] | 95
32 | [8 empty] | 96
33 | [8 empty] | 97
34 | [8 empty] | 98
35 | [8 empty] | 99
36 | [8 empty] | 100
37 | [8 empty] | 101
38 | [8 empty] | 102
39 | [8 empty] | 103
40 | [8 empty] | 104
41 | [8 empty] | 105
42 | [8 empty] | 106
43 | [8 empty] | 107
44 | [8 empty] | 108
45 | [8 empty] | 109
46 | [8 empty] | 110
47 | [8 empty] | 111
48 | [8 empty] | 112
49 | [8 empty] | 113
50 | [8 empty] | 114
51 | [8 empty] | 115
52 | [8 empty] | 116
53 | [8 empty] | 117
54 | [8 empty] | 118
55 | [8 empty] | 119
56 | [8 empty] | 120
57 | [8 empty] | 121
58 | [8 empty] | 122
59 | [8 empty] | 123
60 | [8 empty] | 124
61 | [8 empty] | 125
62 | [8 empty] | 126
63 | [8 empty] | 127
64 | [8 empty] | 128

## LEGEND
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض
خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03)
I/O LIST
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 3 از 9
9184 – 073 - 053 |  |  |  | BK | GCS | HY | 120 | PM | LI | 5 | V01
ABBREVIATIONS
| Location: |  | (Geographical location of the instrument) | [6 empty] | Valve Action :
| FIELD | : | Local | [6 empty] | FC | : | Fail Close
| LCP | : | Local Panel | [6 empty] | FO | : | Fail Open
| SS | : | Electrical Substation | [6 empty] | FL | : | Fail Lock
| ITR | : | Instrument Technical Room | [6 empty] | FLC | : | Fail Lock Close
| CCR | : | Central Control Room | [6 empty] | FLO | : | Fail Lock Open
| MCC | : | Motor Control Center
| DCS | : | Distributed Control System
| ESD | : | Emergency Shutdown System | [6 empty] | W/D :
| UCP | : | Unit Control Panel | [6 empty] | D | : | Dry Contact
[10 empty] | W | : | Wet Contact
| I/O type | [8 empty] | Power Supply :
| AI | : | Analog Input | [6 empty] | AC110V
| AO | : | Analog Output | [6 empty] | DC24V
| DI | : | Digital Input
| DO | : | Digital Output
| DOR | : | Digital Output redundant
| AIR | : | Analog Input redundant
| AOR | : | Analog Output redundant
| DIR | : | Digital Input redundant
| SAI | : | Software Analog Input
| SAO | : | Software Analog Output
| SDI | : | Software Digital Input
| SDO | : | Software Digital Output
| F |  | fail safe
System:
| ESD | : | Emergency Shut Down System
| UCP | : | Unit Control Panel
| DCS | : | Distributed Control System (PCS)
| FGS | : | Fire and Gas System
| MCC | : | Motor Control Center
Signal Type :
4-20mA
DC24V
| NC |  | Contact (Normal Close)
| NO |  | Contact (Normal Open)
| SOV |  | Digital Output Solenoid Valve
| SL |  | Serial Link

## LIST-A
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض
خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03)
I/O LIST
شماره پیمان: | [5 empty] | پروژه | بسته کاری | صادرکننده |  |  | تسهیلات |  | رشته | نوع مدرک |  | سریال | نسخه |  | از |  |  |  |  | شماره صفحه:
9184 – 073 - 053 | [5 empty] | BK | GCS | HY |  |  | 120 |  | IN | LI |  | 0005 | V01
Item No. |  |  |  | Description | Service 1 | Service 2 | P&ID No. | line Size | Connection |  | I/O Type |  | Location, Signal (To) | Power Supply | W/D | Signal Type | IS/NIS | Valve Action | Range/ Alarm Set point | Eng. Units | Engineering Documents |  |  |  | Hazardous Area | Manufacturer | Model Number | Remark
|  | Tag Number | Unit Number | [5 empty] | Size | Rating |  | Location, Signal ( From) | [8 empty] | Loop Diagram No. | Inst. Location Layout | Hook-Up Drawing | Data Sheet
1 | SV-2201 | SV-2201A | A | SOLENOID VALVE | INST. AIR SUPPLY | PACKAGE COMPRESSOR C-2101,2A | BK-GCS-HY-120-PR-PI-0001-SHEET 2A |  |  |  | DOR | UCP-A | FIELD | 24VDC | W | 24VDC | NIS | [7 empty] | ZONE2, IIB, T3
2 | SV-2202 | SV-2202A | A | SOLENOID VALVE | INST. AIR SUPPLY | PACKAGE COMPRESSOR C-2101,2A | BK-GCS-HY-120-PR-PI-0001-SHEET 2A |  |  |  | DOR | UCP-A | FIELD | 24VDC | W | 24VDC | NIS | [7 empty] | ZONE2, IIB, T3
3 | SV-2203 | SV-2203A | A | SOLENOID VALVE | INST. AIR SUPPLY | PACKAGE COMPRESSOR C-2101,2A | BK-GCS-HY-120-PR-PI-0001-SHEET 2A |  |  |  | DOR | UCP-A | FIELD | 24VDC | W | 24VDC | NIS | [7 empty] | ZONE2, IIB, T3
4
5 | PT-2123 | PT-2123A | A | PRESSURE TRANSMITTER | ON SUCTION SNUBBER 1S STAGE | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 1A | 8" |  |  | AI | FIELD | UCP-A | 24VDC | - | 4-20mA Hart | IS |  | 0-16 | BARG |  |  |  |  | ZONE2, IIB, T3
6 | PI-2123 | PI-2123A | A | PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 1A |  |  |  | - | UCP-A | CCR
7 | PAH-2123 | PAH-2123A | A | PRESSURE ALARM HIGH |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 1A |  |  |  | - | UCP-A | CCR
8
9 | FT-2121 | FT-2121A | A | FLOW TRANSMITTER | ON SUCTION SNUBBER 1S STAGE | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 1A | 8" |  |  | AI | FIELD | UCP-A | 24VDC | - | 4-20mA Hart | IS |  | 0-14000 | NM3/H |  |  |  |  | ZONE2, IIB, T3
10 | FE-2121 | FE-2121 A | A | FLOW ELEMENT |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 1A |  |  |  | - | FIELD | -
11 | FI-2121 | FI-2121 A | A | FLOW INDICATING |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 1A |  |  |  | - | UCP-A | CCR
12
13 | TT-2122 | TT-2122 A | A | TEMPERATURE TRANSMITTER | ON SUCTION SNUBBER 1S STAGE | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 1A | 8" |  |  | AI | FIELD | UCP-A | 24VDC | - | 4-20mA Hart | IS |  | 0-100 | °C |  |  |  |  | ZONE2, IIB, T3
14 | TI-2122 | TI-2122 A | A | TEMPERATURE INDICATING |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 1A |  |  |  | - | UCP-A | CCR
15 | TE-2122 | TE-2122A | A | THERMO ELEMENT |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 1A |  |  |  | -
16 | TW-2122 | TW-2122 A | A | THERMOWELL |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 1A |  |  |  | -
17
18 | PDT-2122 | PDT-2122 A | A | DIFF. PRESSURE TRANSMITTER | STRAINER FILTER | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 1A | 1" |  |  | AI | FIELD | UCP-A | 24VDC | - | 4-20mA Hart | IS |  | 0-1 | BARG |  |  |  |  | ZONE2, IIB, T3
19 | PDI-2122 | PDI-2122 A | A | DIFF. PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 1A |  |  |  | - | UCP-A | CCR
20 | PDAH-2122 | PDAH-2122 A | A | DIFF. PRESSURE ALARM HIGH |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 1A |  |  |  | - | UCP-A | CCR
21
22 | PT-2192 A/B | PT-2192 A/BA | A | PRESSURE TRANSMITTER | ON DISCHARGE SNUBBER 1ST STAGE | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 1A | 6" |  |  | AI | FIELD | UCP-A | 24VDC | - | 4-20mA Hart | IS |  | 0-40 | BARG |  |  |  |  | ZONE2, IIB, T3
23 | PI-2192 A/B | PI-2192 A/BA | A | PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 1A |  |  |  | - | UCP-A | CCR
24 | PAH-2192 A/B | PAH-2192 A/BA | A | PRESSURE ALARM HIGH |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 1A |  |  |  | - | UCP-A | CCR
25
26 | TT-2192 | TT-2192 A | A | TEMPERATURE TRANSMITTER | ON DISCHARGE SNUBBER 1ST STAGE | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 1A | 6" |  |  | AI | FIELD | UCP-A | 24VDC | - | 4-20mA Hart | IS |  | 0-200 | °C |  |  |  |  | ZONE2, IIB, T3
27 | TE-2191 | TE-2191 A | A | THERMO ELEMENT |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 1A |  |  |  |  | FIELD | -
28 | TW-2191 | TW-2191 A | A | THERMOWELL |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 1A |  |  |  |  | FIELD | -
29 | TI-2192 | TI-2192 A | A | TEMPERATURE INDICATING |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 1A |  |  |  | - | UCP-A | CCR
30
31 | TT-2191 | TT-2191 A | A | TEMPERATURE TRANSMITTER | ON DISCHARGE SNUBBER 1ST STAGE | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 1A |  |  |  | AI | FIELD | UCP-A | 24VDC | - | 4-20mA Hart | IS |  | 0-200 | °C |  |  |  |  | ZONE2, IIB, T3
32 | TI-2191 | TI-2191A | A | TEMPERATURE INDICATING |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 1A |  |  |  | - | UCP-A | CCR
33 | TAH-2191 | TAH-2191A | A | TEMPERATURE ALARM HIGH |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 1A |  |  |  | - | UCP-A | CCR
34
35 | TS-2191 | TS-2191A | A | TEMPERATURE SWITCH | ON DISCHARGE SNUBBER 1ST STAGE | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 1A |  |  |  | DI | FIELD | Trip Relay UCP A | 24VDC |  | NC | NIS |  | 0-200/160 | °C
36 | TAHH-2191 | TAHH-2191A | A | TEMPERATURE ALARM HIGH HIGH |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 1A | - | - | - |  | FIELD | UCP-A | 24VDC
37
38 | TT-2194 | TT-2194 A | A | TEMPERATURE TRANSMITTER | ON DISCHARGE SNUBBER 2ND STAGE | PACKAGE COMPRESSOR C-2102A | AK-GCS-HY-120-PR-PI-0001-SHEET 1A |  |  |  | AI | FIELD | CCR | 24VDC | - | 4-20mA Hart | IS |  | 0-200 | °C |  |  |  |  | ZONE2, IIB, T3
39 | TE-2194 | TE-2194 A | A | THERMO ELEMENT |  | PACKAGE COMPRESSOR C-2102A | AK-GCS-HY-120-PR-PI-0001-SHEET 1A |  |  |  |  | FIELD | -
40 | TW-2194 | TW-2194 A | A | THERMOWELL |  | PACKAGE COMPRESSOR C-2102A | AK-GCS-HY-120-PR-PI-0001-SHEET 1A |  |  |  |  | FIELD | -
41 | TI-2194 | TI-2194 A | A | TEMPERATURE INDICATING |  | PACKAGE COMPRESSOR C-2102A | AK-GCS-HY-120-PR-PI-0001-SHEET 1A |  |  |  | - | UCP-A | CCR
42 | TAH-2194 | TAH-2194 A | A | TEMPERATURE ALARM HIGH |  | PACKAGE COMPRESSOR C-2102A | AK-GCS-HY-120-PR-PI-0001-SHEET 1A |  |  |  | - | UCP-A | CCR
43
44 | TS-2194 | TS-2194 A | A | TEMPERATURE SWITCH | ON DISCHARGE SNUBBER 2ND STAGE | PACKAGE COMPRESSOR C-2102A | AK-GCS-HY-120-PR-PI-0001-SHEET 1A |  |  |  | DI | FIELD | USD |  |  |  | NIS
45 | TAHH-2194 | TAHH-2194 A | A | TEMPERATURE ALARAM HIGH HIGH |  | PACKAGE COMPRESSOR C-2102A | AK-GCS-HY-120-PR-PI-0001-SHEET 1A |  |  |  | - | FIELD | UCP
46
47 | PT-2124 | PT-2124 A | A | PRESSURE TRANSMITTER | ON DISCHARGE LINE SNUBBER 2ND STAGE | PACKAGE COMPRESSOR C-2102A | AK-GCS-HY-120-PR-PI-0001-SHEET 1A | 6" |  |  | AI | FIELD | UCP-A | 24VDC | - | 4-20mA Hart | IS |  | 0-80 | BARG |  |  |  |  | ZONE2, IIB, T3
48 | PI-2124 | PI-2124 A | A | PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2102A | AK-GCS-HY-120-PR-PI-0001-SHEET 1A |  |  |  | - | UCP-A | CCR
49 | PAHH-2124 | PAHH-2124 A | A | PRESSURE ALARM HIGH HIGH |  | PACKAGE COMPRESSOR C-2102A | AK-GCS-HY-120-PR-PI-0001-SHEET 1A |  |  |  | - | UCP-A | CCR
50
51 | PS-2195 | PS-2195 A | A | PRESSURE SWITCH | ON DISCHARGE LINE SNUBBER 2ND STAGE | PACKAGE COMPRESSOR C-2102A | AK-GCS-HY-120-PR-PI-0001-SHEET 1A | 6" |  |  | DI | FIELD | Trip Relay UCP A |  |  |  | NIS
52 | PAHH-2195 | PAHH-2195 A | A | PRESSURE Trip HIGH HIGH |  | PACKAGE COMPRESSOR C-2102A | AK-GCS-HY-120-PR-PI-0001-SHEET 1A |  |  |  | - | FIELD | UCP-A
53
54 | TT-2123 | TT-2123 A | A | TEMPERATURE TRANSMITTER | ON DISCHARGE LINE SNUBBER 2ND STAGE | PACKAGE COMPRESSOR C-2102A | AK-GCS-HY-120-PR-PI-0001-SHEET 1A | 6" |  |  | AI | FIELD | UCP-A | 24VDC | - | 4-20mA Hart | IS |  | 0-200 | °C |  |  |  |  | ZONE2, IIB, T3
55 | TE-2123 | TE-2123 A | A | THERMO ELEMENT |  | PACKAGE COMPRESSOR C-2102A | AK-GCS-HY-120-PR-PI-0001-SHEET 1A |  |  |  |  | - | FIELD
56 | TW2123 | TW2123 A | A | THERMOWELL |  | PACKAGE COMPRESSOR C-2102A | AK-GCS-HY-120-PR-PI-0001-SHEET 1A |  |  |  |  | - | FIELD
57 | TI-2123 | TI-2123 A | A | TEMPERATURE INDICATING |  | PACKAGE COMPRESSOR C-2102A | AK-GCS-HY-120-PR-PI-0001-SHEET 1A |  |  |  | - | UCP-A | CCR
58
59 | PT-2197 | PT-2197A | A | PRESSURE TRANSMITTER | ON SUCTION SNUBBER 2ND STAGE | PACKAGE COMPRESSOR C-2102A | AK-GCS-HY-120-PR-PI-0001-SHEET 1A | 6" |  |  | AI | FIELD | UCP-A | 24VDC | - | 4-20mA Hart | IS |  | 0-40 | BARG |  |  |  |  | ZONE2, IIB, T3
60 | PI-2197 | PI-2197 A | A | PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2102A | AK-GCS-HY-120-PR-PI-0001-SHEET 1A |  |  |  | - | UCP-A | CCR
61
62 | FT-2197 | FT-2197A | A | FLOW TRANSMITTER | ON SUCTION SNUBBER 2ND STAGE | PACKAGE COMPRESSOR C-2102A | AK-GCS-HY-120-PR-PI-0001-SHEET 1A | 6" |  |  | AI | FIELD | UCP-A | 24VDC | - | 4-20mA Hart | IS |  | 0-14000 | NM3/H |  |  |  |  | ZONE2, IIB, T3
63 | FE-2197 | FE-2197A | A | FLOW ELEMENT |  | PACKAGE COMPRESSOR C-2102A | AK-GCS-HY-120-PR-PI-0001-SHEET 1A |  |  |  | - | FIELD | -
64 | FI-2197 | FI-2197A | A | FLOW INDICATING |  | PACKAGE COMPRESSOR C-2102A | AK-GCS-HY-120-PR-PI-0001-SHEET 1A |  |  |  | - | UCP-A | CCR
65
66 | TT-2197 | TT-2197A | A | TEMPERATURE TRANSMITTER | ON SUCTION SNUBBER 2ND STAGE | PACKAGE COMPRESSOR C-2102A | AK-GCS-HY-120-PR-PI-0001-SHEET 1A | 6" |  |  | AI | FIELD | UCP-A | 24VDC | - | 4-20mA Hart | IS |  | 0-100 | °C |  |  |  |  | ZONE2, IIB, T3
67 | TE-2197 | TE-2197A | A | THERMO ELEMENT |  | PACKAGE COMPRESSOR C-2102A | AK-GCS-HY-120-PR-PI-0001-SHEET 1A |  |  |  | - | - | FIELD
68 | TW-2197 | TW-2197A | A | THERMOWELL |  | PACKAGE COMPRESSOR C-2102A | AK-GCS-HY-120-PR-PI-0001-SHEET 1A |  |  |  |  | - | FIELD
69 | TI-2197 | TI-2197A | A | TEMPERATURE INDICATING |  | PACKAGE COMPRESSOR C-2102A | AK-GCS-HY-120-PR-PI-0001-SHEET 1A |  |  |  |  | UCP-A | CCR
70
71 | PDT-2197 | PDT-2197A | A | DIFF. PRESSURE TRANSMITTER | STRAINER FILTER 2ND STAGE | PACKAGE COMPRESSOR C-2102A | AK-GCS-HY-120-PR-PI-0001-SHEET 1A | 1" |  |  | AI | FIELD | UCP-A | 24VDC | - | 4-20mA Hart | IS |  | 0-6 | BARG |  |  |  |  | ZONE2, IIB, T3
72 | PDI-2197 | PDI-2197A | A | DIFF. PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2102A | AK-GCS-HY-120-PR-PI-0001-SHEET 1A |  |  |  | - | UCP-A | CCR
73 | PDAH-2197 | PDAH-2197A | A | DIFF. PRESSURE ALARM HIGH |  | PACKAGE COMPRESSOR C-2102A | AK-GCS-HY-120-PR-PI-0001-SHEET 1A |  |  |  | - | UCP-A | CCR
74
75 | PT-2201 | PT-2201A | A | PRESSURE TRANSMITTER | ON INSTRUMENT LINE | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 2A | 2" |  |  | AI | FIELD | UCP-A | 24VDC | - | 4-20mA Hart | IS |  | HOLD | HOLD |  |  |  |  | ZONE2, IIB, T3
76 | PI-2201 | PI-2201A | A | PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 2A |  |  |  | - | UCP-A | CCR
77 | PAL-2201 | PAL-2201A | A | PRESSURE ALARM LOW |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 2A |  |  |  | - | UCP-A | CCR
78
79 | PT-2200 | PT-2200 A | A | PRESSURE TRANSMITTER | ON LUBRICATOR | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | AI | FIELD | UCP-A | 24VDC | - | 4-20mA Hart | IS |  | HOLD | HOLD |  |  |  |  | ZONE2, IIB, T3
80 | PI-2200 | PI-2200 A | A | PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | - | UCP-A | CCR
81 | PAL-2200 | PAL-2200 A | A | PRESSURE ALARM LOW |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | - | UCP-A | CCR
82
83 | LT-2200 | LT-2200 A | A | LEVEL TRANSMITTER | ON CRANK CASE | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | AI | FIELD | UCP-A | 24VDC | - | 4-20mA Hart | IS |  | HOLD | HOLD |  |  |  |  | ZONE2, IIB, T3
84 | LI-2200 | LI-2200 A | A | LEVEL INDICATING |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | - | UCP-A | CCR
85 | LAL-2200 | LAL-2200 A | A | LEVEL ALARM LOW |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | - | UCP-A | CCR
86
87 | LT-2213 | LT-2213 A | A | LEVEL TRANSMITTER | WATER RESERVOIR | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | AI | FIELD | Trip Relay UCP A | 24VDC | - | 4-20mA Hart | IS |  | HOLD | HOLD |  |  |  |  | ZONE2, IIB, T3
88 | LI-2213 | LI-2213 A | A | LEVEL INDICATING |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | - | UCP-A | CCR
89 | LAL-2213 | LAL-2213 A | A | LEVEL ALARM LOW |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | - | UCP-A | CCR
90 | LALL-2213 | LALL-2213 A | A | LEVEL ALARM LOW LOW |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | - | UCP-A | CCR
91
92 | TT-2203 | TT-2203 A | A | TEMPERATURE TRANSMITTER | ON CRANK CASE | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | AIR | FIELD | UCP-A | 24VDC | - | 4-20mA Hart | IS |  | 0-200 | °C |  |  |  |  | ZONE2, IIB, T3
93 | TE-2203 | TE-2203 A | A | THERMO ELEMENT |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  |  | FIELD | -
94 | TW-2203 | TW-2203 A | A | THERMOWELL |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  |  | FIELD | -
95 | TI-2203 | TI-2203 A | A | THERMO ELEMENT |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  |  | UCP-A | CCR
96
97 | HSP-2203 | HSP-2203 A | A | START COMMAND HEATER CRANK CASE | HEATER CRANK CASE | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | DOR | UCP-A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
98 | HST-2203 | HST-2203 A | A | STOP COMMAND HEATER CRANK CASE | HEATER CRANK CASE | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | DOR | UCP-A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
99 | XL-2203 | XL-2203 A | A | RUNNING STATUS HEATER CRANK CASE | HEATER CRANK CASE | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | DI | MCC | UCP-A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
100 | XA-2203 | XA-2203 A | A | FAILURE STATUS HEATER CRANK CASE | HEATER CRANK CASE | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | DI | MCC | UCP-A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
101
102 | HST-2200 | HST-2200 A | A | START COMMAND HEATER LUBRICATOR | HEATER ON LUBRICATOR | PACKAGE COMPRESSOR C-1401A | AK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | DOR | UCP-A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
103 | HSP-2200 | HSP-2200 A | A | STOP COMMAND HEATER LUBRICATOR | HEATER ON LUBRICATOR | PACKAGE COMPRESSOR C-1401A | AK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | DOR | UCP-A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
104 | XL-2200 | XL-2200 A | A | RUNNING STATUS HEATER LUBRICATOR | HEATER ON LUBRICATOR | PACKAGE COMPRESSOR C-1401A | AK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | DI | MCC | UCP-A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
105 | XA-2200 | XA-2200 A | A | FAILURE STATUS HEATER LUBRICATOR | HEATER ON LUBRICATOR | PACKAGE COMPRESSOR C-1401A | AK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | DI | MCC | UCP-A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
106
107 | TT-2204 | TT-2204A | A | TEMPERATURE TRANSMITTER | LUBE OIL FILTER DOWNSTREAM | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 3A | 4" |  |  | AI | FIELD | UCP-A | 24VDC | - | 4-20mA Hart | IS |  | 0-100 | °C |  |  |  |  | ZONE2, IIB, T3
108 | TI-2204 | TI-2204A | A | TEMPERATURE INDICATING |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | - | UCP-A | CCR
109 | TW-2204 | TW-2204A | A | THERMOWELL | LUBE OIL FILTER DOWNSTREAM | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  |  | FIELD | -
110 | TAH-2204 | TAH-2204A | A | TEMPERATURE ALARM HIGH |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | - | UCP-A | CCR
111 | TAL-2204 | TAL-2204A | A | TEMPERATURE ALARM LOW |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | - | UCP-A | CCR
112
113 | PT-2204 | PT-2204A | A | PRESSURE TRANSMITTER | LUBE OIL FILTER DOWNSTREAM | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 3A | 2" |  |  | AIR | FIELD | UCP-A | 24VDC | - | 4-20mA Hart | IS |  | 0-16 | BARG |  |  |  |  | ZONE2, IIB, T3
114 | PI-2204 | PI-2204A | A | PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | - | UCP-A | CCR
115 | PAL-2204 | PAL-2204A | A | PRESSURE ALARM LOW |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | - | UCP-A | CCR
116 | PAH-2204 | PAH-2204A | A | PRESSURE ALARM HIGH |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | - | UCP-A | CCR
117 | PAH2-2204 | PAH2-2204A | A | PRESSURE ALARM HIGH2 |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | - | UCP-A | CCR
118
119 | PS-2204 | PS-2204A | A | PRESSURE SWITCH | LUBE OIL FILTER DOWNSTREAM | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | DI | Field | Trip Relay UCP A |  |  |  | N'IS |  | 0-16/6 | BARG |  |  |  |  | ZONE2, IIB, T3
120 | PALL-2204 | PALL-2204A | A | PRESSURE ALARM LOW LOW |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | - | Field | UCP-A
121
122 | PDT-2204 | PDT-2204 A | A | DIFF. PRESSURE TRANSMITTER | LUBE OIL FILTER | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 3A | 1" |  |  | AIR | FIELD | UCP-A | 24VDC | - | 4-20mA Hart | IS |  | 0-6 | BARG |  |  |  |  | ZONE2, IIB, T3
123 | PDI-2204 | PDI-2204 A | A | DIFF. PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | - | UCP-A | CCR
124 | PDAH-2204 | PDAH-2204 A | A | DIFF. PRESSURE ALARM HIGH |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | - | UCP-A | CCR
125
126 | HST-2202 | HST-2202 A | A | START COMMAND AUX. OIL PUMP | AUX. OIL PUMP (P-2101-AP A) | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | DOR | UCP-A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
127 | HSP-2202 | HSP-2202 A | A | STOP COMMAND AUX. OIL PUMP | AUX. OIL PUMP (P-2101-AP A) | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | DOR | UCP-A | MCC | 24VDC | D | NC | NIS | [7 empty] | ZONE2, IIB, T3
128 | XL-2202 | XL-2202 A | A | RUNNING STATUSAUX. OIL PUMP | AUX. OIL PUMP (P-2101-AP A) | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | DI | MCC | UCP-A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
129 | XA-2202 | XA-2202 A | A | FAILURE STATUS AUX. OIL PUMP | AUX. OIL PUMP (P-2101-AP A) | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | DI | MCC | UCP-A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
130
131 | HST-2201 | HST-2201 A | A | START COMMAND LUBRICATOR. OIL PUMP | LUBRICATOR. OIL PUMP (2101-LP A) | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | DOR | UCP-A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
132 | HSP-2201 | HSP-2201 A | A | STOP COMMAND LUBRICATOR. OIL PUMP | LUBRICATOR. OIL PUMP (2101-LP A) | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | DOR | UCP-A | MCC | 24VDC | D | NC | NIS | [7 empty] | ZONE2, IIB, T3
133 | XL-2201 | XL-2201 A | A | RUNNING STATUS LUBRICATOR. OIL PUMP | LUBRICATOR. OIL PUMP (2101-LP A) | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | DI | MCC | UCP-A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
134 | XA-2201 | XA-2201 A | A | FAILURE STATUS LUBRICATOR. OIL PUMP | LUBRICATOR. OIL PUMP (2101-LP A) | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | DI | MCC | UCP-A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
135
136 | HST-2205 | HST-2205 A | A | START COMMAND LUB OIL COOLER | LUB OIL COOLER (AE-2101-OC A) | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | DOR | UCP-A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
137 | HSP-2205 | HSP-2205 A | A | STOP COMMAND LUB OIL COOLER | LUB OIL COOLER (AE-2101-OC A) | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | DOR | UCP-A | MCC | 24VDC | D | NC | NIS | [7 empty] | ZONE2, IIB, T3
138 | XL-2205 | XL-2205 A | A | RUNNING STATUS LUB OIL COOLER | LUB OIL COOLER (AE-2101-OC A) | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | DI | MCC | UCP-A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
139 | XA-2205 | XA-2205 A | A | FAILURE STATUS LUB OIL COOLER | LUB OIL COOLER (AE-2101-OC A) | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | DI | MCC | UCP-A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
140
141 | PT-2210 | PT-2210A | A | PRESSURE TRANSMITTER | N2 TO CYLINDER PACKING INLET | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 4A | 1" |  |  | AI | FIELD | UCP-A | 24VDC | - | 4-20mA Hart | IS |  | 0-6 | BARG |  |  |  |  | ZONE2, IIB, T3
142 | PI-2210 | PI-2210A | A | PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 4A |  |  |  | - | UCP-A | CCR
143 | PAL-2210 | PAL-2210A | A | PRESSURE ALARM LOW |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 4A |  |  |  | - | UCP-A | CCR
144
145 | PT-2211 | PT-2211A | A | PRESSURE TRANSMITTER | N2 TO CYLINDER PACKING INLET | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 4A | 1" |  |  | AI | FIELD | UCP-A | 24VDC | - | 4-20mA Hart | IS |  | 0-6 | BARG |  |  |  |  | ZONE2, IIB, T3
146 | PI-2211 | PI-2211A | A | PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 4A |  |  |  | - | UCP-A | CCR
147 | PAL-2211 | PAL-2211A | A | PRESSURE ALARM LOW |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 4A |  |  |  | - | UCP-A | CCR
148
149 | HST-2220 | HST-2220 A | A | START COMMAND WATER CONSULE COOLER | WATER CONSULE COOLER (AE-2101-WC A) | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  | DOR | UCP-A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
150 | HSP-2220 | HSP-2220 A | A | STOP COMMAND WATER CONSULE COOLER | WATER CONSULE COOLER (AE-2101-WC A) | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  | DOR | UCP-A | MCC | 24VDC | D | NC | NIS | [7 empty] | ZONE2, IIB, T3
151 | XL-2220 | XL-2220 A | A | RUNNING STATUS WATER CONSULE COOLER | WATER CONSULE COOLER (AE-2101-WC A) | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  | DI | MCC | UCP-A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
152 | XA-2220 | XA-2220 A | A | FAILURE STATUS WATER CONSULE COOLER | WATER CONSULE COOLER (AE-2101-WC A) | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  | DI | MCC | UCP-A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
153
154 | HST-2221 | HST-2221 A | A | START COMMAND AUX WATER PUMP | AUX WATER PUMP (P-2101-AX A) | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  | DOR | UCP-A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
155 | HSP-2221 | HSP-2221 A | A | STOP COMMAND AUX WATER PUMP | AUX WATER PUMP (P-2101-AX A) | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  | DOR | UCP-A | MCC | 24VDC | D | NC | NIS | [7 empty] | ZONE2, IIB, T3
156 | XL-2221 | XL-2221A | A | RUNNING STATUS AUX WATER PUMP | AUX WATER PUMP (P-2101-AX A) | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  | DI | MCC | UCP-A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
157 | XA-2221 | XA-2221 A | A | FAILURE STATUS AUX WATER PUMP | AUX WATER PUMP (P-2101-AX A) | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  | DI | MCC | UCP-A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
158
159 | HST-2222 | HST-2222 A | A | START COMMAND MAIN WATER PUMP | MAIN WATER PUMP (P-2101-WP A) | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  | DOR | UCP-A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
160 | HSP-2222 | HSP-2222 A | A | STOP COMMAND MAIN WATER PUMP | MAIN WATER PUMP (P-2101-WP A) | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  | DOR | UCP-A | MCC | 24VDC | D | NC | NIS | [7 empty] | ZONE2, IIB, T3
161 | XL-2222 | XL-2222A | A | RUNNING STATUS MAIN WATER PUMP | MAIN WATER PUMP (P-2101-WP A) | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  | DI | MCC | UCP-A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
162 | XA-2222 | XA-2222 A | A | FAILURE STATUS MAIN WATER PUMP | MAIN WATER PUMP (P-2101-WP A) | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  | DI | MCC | UCP-A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
163
164 | HST-2223 | HST-2223 A | A | START COMMAND HEATER WATER CONSULE | WATER CONSULE COOLER HEATER (AE-2101-WC A) | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  | DOR | UCP-A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
165 | HSP-2223 | HSP-2223 A | A | STOP COMMAND HEATER WATER CONSULE | WATER CONSULE COOLER HEATER (AE-2101-WC A) | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  | DOR | UCP-A | MCC | 24VDC | D | NC | NIS | [7 empty] | ZONE2, IIB, T3
166 | XL-2223 | XL-2223A | A | RUNNING STATUS HEATER WATER CONSULE | WATER CONSULE COOLER HEATER (AE-2101-WC A) | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  | DI | MCC | UCP-A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
167 | XA-2223 | XA-2223 A | A | FAILURE STATUS HEATER WATER CONSULE | WATER CONSULE COOLER HEATER (AE-2101-WC A) | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  | DI | MCC | UCP-A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
168
169 | PT-2220 | PT-2220A | A | PRESSURE TRANSMITTER | WATER TO CYLINDERS | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 5A | 2" |  |  | AIR | FIELD | FIELD | 24VDC | - | 4-20mA Hart | IS |  | 0-16 | BARG |  |  |  |  | ZONE2, IIB, T3
170 | PI-2220 | PI-2220A | A | PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  | - | UCP-A | CCR
171 | PAL-2220 | PAL-2220A | A | PRESSURE ALARM LOW |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  | - | UCP-A | CCR
172 | PAH-2220 | PAH-2220A | A | PRESSURE ALARM HIGH |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  | - | UCP-A | CCR
173
174 | PT-2221 | PT-2221A | A | PRESSURE TRANSMITTER | WATER TO CYLINDERS | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 5A | 2" |  |  | AI | FIELD | FIELD | 24VDC | - | 4-20mA Hart | IS |  | 0-16 | BARG |  |  |  |  | ZONE2, IIB, T3
175 | PI-2221 | PI-2221A | A | PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  | - | UCP-A | CCR
176 | PAL-2221 | PAL-2221A | A | PRESSURE ALARM LOW |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  | - | UCP-A | CCR
177
178 | PS-2220 | PS-2220A | A | PRESSURE SWITCH | WATER TO CYLINDERS | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 5A | 2" |  |  | DI | Field | Trip Relay UCP A |  |  |  | NIS |  | 0-16 | BARG
179 | PALL-2220 | PALL-2220A | A | PRESSURE ALARM LOW LOW |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  | - | Field | UCP-A
180
181 | TT-2213 | TT-2213A | A | TEMPERATURE TRANSMITTER | WATER RESERVOIR | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  | AIR | FIELD | UCP-A | 24VDC | - | 4-20mA Hart | IS |  | 0-100 | °C |  |  |  |  | ZONE2, IIB, T3
182 | TE-2213 | TE-2213A | A | THERMO ELEMENT |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 5A | [5 empty] | FIELD
183 | TW-2213 | TW-2213A | A | THERMOWELL |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 5A | [5 empty] | FIELD
184 | TI-2213 | TI-2213A | A | TEMPERATURE INDICATING |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  | - | UCP-A | CCR
185 | TAH-2213 | TAH-2213A | A | TEMPERATURE ALARM HIGH |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  | - | UCP-A | CCR
186 | TAL-2213 | TAL-2213A | A | TEMPERATURE ALARM LOW |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  | - | UCP-A | CCR
187
188 | FT-2206 | FT-2206A | A | FLOW TRANSMITTER | WATER TO CYLINDERS | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 5A | 2" |  |  | AI | FIELD | UCP-A | 24VDC | - | 4-20mA Hart | IS |  | 0-16 | BARG |  |  |  |  | ZONE2, IIB, T3
189 | FE-2221 | FE-2221A | A | FLOW ELEMENT |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  | - | FIELD | -
190 | FI-2221 | FI-2221A | A | FLOW INDICATING |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  | - | UCP-A | CCR
191
192 | HS-2239-L | HS-2239-LA | A | SELECTOR SWITCH | LOCAL MODE SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 8A | - | - | - | DI | LCP-A | UCP-A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
193 | HS-2239-R | HS-2239-RA | A | SELECTOR SWITCH | REMOTE MODE SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 8A | - | - | - | DI | LCP-A | UCP-A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
194 | HS-2230-M | HS-2230-MA | A | SELECTOR SWITCH | AUX. LUBE OIL PUMP MANU. SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 8A | - | - | - | DI | LCP-A | UCP-A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
195 | HS-2230-U | HS-2230-UA | A | SELECTOR SWITCH | AUX. LUBE OIL PUMP AUTO. SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 8A | - | - | - | DI | LCP-A | UCP-A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
196 | HS-2231-M | HS-2231-MA | A | SELECTOR SWITCH | OIL COOLER . SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 8A | - | - | - | DI | LCP-A | UCP-A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
197 | HS-2231-U | HS-2231-UA | A | SELECTOR SWITCH | OIL COOLER . SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 8A | - | - | - | DI | LCP-A | UCP-A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
198 | HS-2233-M | HS-2233-MA | A | SELECTOR SWITCH | MAIN WATER PUMP MANU SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 8A | - | - | - | DI | LCP-A | UCP-A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
199 | HS-2233-U | HS-2233-UA | A | SELECTOR SWITCH | MAIN WATER PUMP AUTO SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 8A | - | - | - | DI | LCP-A | UCP-A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
200 | HS-2234-M | HS-2234-MA | A | SELECTOR SWITCH | AUX WATER PUMP MANU SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 8A | - | - | - | DI | LCP-A | UCP-A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
201 | HS-2234-U | HS-2234-UA | A | SELECTOR SWITCH | AUX WATER PUMP AUTO SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 8A | - | - | - | DI | LCP-A | UCP-A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
202 | HS-2235-M | HS-2235-MA | A | SELECTOR SWITCH | WATER COOLER MANU SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 8A | - | - | - | DI | LCP-A | UCP-A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
203 | HS-2235-U | HS-2235-UA | A | SELECTOR SWITCH | WATER COOLER AUTO SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 8A | - | - | - | DI | LCP-A | UCP-A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
204 | HS-2236 | HS-2236A | A | PUSH BUTTON | LAMP TEST PUSHBUTTON SWITCH | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 8A | - | - | - | DI | LCP-A | UCP-A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
205 | HS-2237-T | HS-2237-TA | A | PUSH BUTTON | MAIN MOTOR START PUSHBUTTON | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 8A |  |  |  | DI | LCP-A | UCP-A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
206 | HS-2237-P | HS-2237-PA | A | PUSH BUTTON | MAIN MOTOR STOP PUSHBUTTON | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 8A |  |  |  | DI | LCP-A | UCP-A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
207 | HS-2238-T | HS-2238-TA | A | PUSH BUTTON | OIL HEATER ON PUSHBUTTON | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 8A |  |  |  | DI | LCP-A | UCP-A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
208 | HS-2238-P | HS-2238-PA | A | PUSH BUTTON | OIL HEATER OFF PUSHBUTTON | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 8A |  |  |  | DI | LCP-A | UCP-A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
209 | HS-2239-T | HS-2239-TA | A | PUSH BUTTON | AUX. LUBE OIL PUMP START PUSHBUTTON | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 8A |  |  |  | DI | LCP-A | UCP-A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
210 | HS-2239-P | HS-2239-PA | A | PUSH BUTTON | AUX. LUBE OIL PUMP STOP PUSHBUTTON | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 8A |  |  |  | DI | LCP-A | UCP-A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
211 | HS-2240-T | HS-2240-TA | A | PUSH BUTTON | OIL COOLER MOTOR A START PUSHBUTTON | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 8A |  |  |  | DI | LCP-A | UCP-A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
212 | HS-2240-P | HS-2240-PA | A | PUSH BUTTON | OIL COOLER MOTOR A STOP PUSHBUTTON | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 8A |  |  |  | DI | LCP-A | UCP-A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
213 | HS-2241-T | HS-2241-TA | A | PUSH BUTTON | OIL COOLER MOTOR B START PUSHBUTTON | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 8A |  |  |  | DI | LCP-A | UCP-A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
214 | HS-2241-P | HS-2241-PA | A | PUSH BUTTON | OIL COOLER MOTOR B STOP PUSHBUTTON | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 8A |  |  |  | DI | LCP-A | UCP-A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
215 | HS-2242-T | HS-2242-TA | A | PUSH BUTTON | LUB L HEATER ON PUSHBUTTON | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 8A |  |  |  | DI | LCP-A | UCP-A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
216 | HS-2242-P | HS-2242-PA | A | PUSH BUTTON | LUB HEATER OFF PUSHBUTTON | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 8A |  |  |  | DI | LCP-A | UCP-A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
217 | HS-2243-T | HS-2243-TA | A | PUSH BUTTON | LUB MOTOR START PUSHBUTTON | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 8A |  |  |  | DI | LCP-A | UCP-A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
218 | HS-2243-P | HS-2243-PA | A | PUSH BUTTON | LUB MOTOR STOP PUSHBUTTON | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 8A |  |  |  | DI | LCP-A | UCP-A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
219 | HS-2244-T | HS-2244-TA | A | PUSH BUTTON | MAIN WATER PUMP MOTOR START PUSHBUTTON | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 8A |  |  |  | DI | LCP-A | UCP-A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
220 | HS-2244-P | HS-2244-PA | A | PUSH BUTTON | MAIN WATER PUMP MOTOR STOP PUSHBUTTON | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 8A |  |  |  | DI | LCP-A | UCP-A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
221 | HS-2245-T | HS-2245-TA | A | PUSH BUTTON | AUX WATER PUMP MOTOR START PUSHBUTTON | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 8A |  |  |  | DI | LCP-A | UCP-A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
222 | HS-2245-P | HS-2245-PA | A | PUSH BUTTON | AUX WATER PUMP MOTOR STOP PUSHBUTTON | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 8A |  |  |  | DI | LCP-A | UCP-A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
223 | HS-2246-T | HS-2246-TA | A | PUSH BUTTON | WATER HEATER ON PUSHBUTTON | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 8A |  |  |  | DI | LCP-A | UCP-A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
224 | HS-2246-P | HS-2246-PA | A | PUSH BUTTON | WATER HEATER OFF PUSHBUTTON | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 8A |  |  |  | DI | LCP-A | UCP-A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
225 | HS-2247-T | HS-2247-TA | A | PUSH BUTTON | WATER COOLER MOTOR START PUSHBUTTON | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 8A |  |  |  | DI | LCP-A | UCP-A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
226 | HS-2247-P | HS-2247-PA | A | PUSH BUTTON | WATER COOLER MOTOR STOP PUSHBUTTON | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 8A |  |  |  | DI | LCP-A | UCP-A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
227 | HS-2248-T | HS-2248-TA | A | PUSH BUTTON | BEARING MOTOR START PUSHBUTTON | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 8A |  |  |  | DI | LCP-A | UCP-A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
228 | HS-2248-P | HS-2248-PA | A | PUSH BUTTON | BEARING MOTOR STOP PUSHBUTTON | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 8A |  |  |  | DI | LCP-A | UCP-A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
229 | HS-2250 | HS-2250A | A | PUSH BUTTON | RESET PUSH BUTTON | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 8A |  |  |  | DI | LCP-A | UCP-A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
230 | HS-2238-U | HS-2238-UA | A | SELECTOR SWITCH | OIL COOLER AUTO SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 8A | - | - | - | DI | LCP-A | UCP-A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
231 | HS-2240 | HS-2240A | A | EMERGENCY SHUT DOWN | RESET PUSH BUTTON | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 8A |  |  |  | DI | LCP-A | UCP-A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
232 | XL-2230 | XL-2230A | A | SIGNAL LAMP | OIL HEATER ACTIVE LAMP | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 8A | - | - | - | DO | UCP-A | LCP | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T3
233 | XL-2231 | XL-2231A | A | SIGNAL LAMP | AUX LUBE OILPUMP MOTOR START LAMP | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 8A | - | - | - | DO | UCP-A | LCP-A | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T3
234 | XL-2184 | XL-2184A | A | SIGNAL LAMP | COMMON ALARM LAMP | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 8A | - | - | - | DO | UCP-A | LCP-A | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T3
235 | XL-2185 | XL-2185A | A | SIGNAL LAMP | COMMON SHUTDOWN LAMP | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 8A | - | - | - | DO | UCP-A | LCP-A | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T3
236 | XL-2232 | XL-2232A | A | SIGNAL LAMP | LUBRICATOR OIL HEATER ON LAMP | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 8A | - | - | - | DO | UCP-A | LCP-A | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T3
237 | XL-2233 | XL-2233A | A | SIGNAL LAMP | LUBRICATOR OIL MOTOR START LAMP | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 8A | - | - | - | DO | UCP-A | LCP-A | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T3
238 | XL-2234 | XL-2234A | A | SIGNAL LAMP | MAIN MOTOR RUNNING LAMP | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 8A | - | - | - | DO | UCP-A | LCP-A | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T3
239 | XL-2235 | XL-2235A | A | SIGNAL LAMP | OIL COOLER MOTOR A RUNNING LAMP | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 8A | - | - | - | DO | UCP-A | LCP-A | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T3
240 | XL-2236 | XL-2236A | A | SIGNAL LAMP | OIL COOLER MOTOR B RUNNING LAMP | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 8A |  |  |  | DO | UCP-A | LCP-A | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T3
241 | XL-2237 | XL-2237A | A | SIGNAL LAMP | MAIN WATER PUMP MOTOR RUNNING LAMP | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 8A |  |  |  | DO | UCP-A | LCP-A | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T3
242 | XL-2238 | XL-2238A | A | SIGNAL LAMP | AUX WATER PUMP MOTOR RUNNING LAMP | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 8A |  |  |  | DO | UCP-A | LCP-A | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T3
243 | XL-2239 | XL-2239A | A | SIGNAL LAMP | WATER HEATER ACTIVE LAMP | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 8A |  |  |  | DO | UCP-A | LCP-A | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T3
244 | XL-2240 | XL-2240A | A | SIGNAL LAMP | WATER COOLER RUNNING LAMP | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 8A |  |  |  | DO | UCP-A | LCP-A | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T3
245 | XL-2241 | XL-2241A | A | SIGNAL LAMP | BEARRING MOTOR RUNNING LAMP | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 8A |  |  |  | DO | UCP-A | LCP-A | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T3
246 | XL-2242 | XL-2242A | A | SIGNAL LAMP | READY TO START LAMP | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 8A |  |  |  | DO | UCP-A | LCP-A | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T3
247 | XL-2243 | XL-2243A | A | SIGNAL LAMP | COMMON ALARM LAMP | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 8A |  |  |  | DO | UCP-A | LCP-A | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T3
248 | XL-2244 | XL-2244A | A | SIGNAL LAMP | COMMON SHUT DOWN LAMP | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 8A |  |  |  | DO | UCP-A | LCP-A | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T3
249
250 | VT-2202 | VT-2202A | A | VIBRATION TRANSMITTER | FRAME VIBRATION | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | AI | FIELD | Trip Relay UCP | 24VDC | - | 4-20mA | IS |  | HOLD | HOLD |  |  |  |  | ZONE2, IIB, T3
251 | VE--2202 | VE--2202A | A | VIBRATION ELEMENT |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | - | FIELD | -
252 | VI--2202 | VI--2202A | A | VIBRATION INDICATING |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | - | UCP-A | CCR
253 | VAH-2202 | VAH-2202A | A | VIBRATION ALARM HIGH |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | - | UCP-A | CCR
254 | VAHH-2202 | VAHH-2202A | A | VIBRATION ALARM HIGH HIGH |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | - | UCP-A | CCR
255
256 | VT--2200 | VT--2200A | A | VIBRATION TRANSMITTER | FRAME VIBRATION | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | AI | FIELD | Trip Relay UCP A | 24VDC | - | 4-20mA | IS |  | HOLD | HOLD |  |  |  |  | ZONE2, IIB, T3
257 | VE--2200 | VE--2200A | A | VIBRATION ELEMENT |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | - | FIELD | -
258 | VI--2200 | VI--2200A | A | VIBRATION INDICATING |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | - | UCP-A | CCR
259 | VAH-2200 | VAH-2200A | A | VIBRATION ALARM HIGH |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | - | UCP-A | CCR
260 | VAHH-2200 | VAHH-2200A | A | VIBRATION ALARM HIGH HIGH |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | - | UCP-A | CCR
261
262 | VT-2201 | VT-2201A | A | VIBRATION TRANSMITTER | FRAME VIBRATION | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | AI | FIELD | Trip Relay UCP A | 24VDC | - | 4-20mA | IS |  | HOLD | HOLD |  |  |  |  | ZONE2, IIB, T3
263 | VE-2201 | VE-2201A | A | VIBRATION ELEMENT |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | - | FIELD | -
264 | VI-2201 | VI-2201A | A | VIBRATION INDICATING |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | - | UCP-A | CCR
265 | VAH-2201 | VAH-2201A | A | VIBRATION ALARM HIGH |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | - | UCP-A | CCR
266 | VAHH-2201 | VAHH-2201A | A | VIBRATION ALARM HIGH HIGH |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | - | UCP-A | CCR
267
268
269 | TE-2214 | TE-2214A | A | RTD THERMO ELEMENT | Comp. Frame Temp. Measurment | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  |  | FIELD |  |  | - | RTD |  |  | HOLD | [5 empty] | ZONE2, IIB, T3
270 | TT-2214 | TT-2214A | A | TEMPERATURE TRAMSMITTER |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | AI | FIELD | UCP-A | 24VDC |  | 4-20mA Hart | IS |  | HOLD
271 | TI-2214 | TI-2214A | A | TEMPERATURE INDICATION |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | - | UCP-A | CCR
272 | TAH-2214 | TAH-2214A | A | TEMPERATURE ALARM HIGH |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | - | UCP-A | CCR
273
274 | TE-2215 | TE-2215A | A | RTD THERMO ELEMENT | Comp. Frame Temp. Measurment | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  |  | FIELD |  |  | - | RTD |  |  | HOLD | [5 empty] | ZONE2, IIB, T3
275 | TT-2215 | TT-2215A | A | TEMPERATURE TRAMSMITTER |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | AI | FIELD | UCP-A | 24VDC |  | 4-20mA Hart | IS
276 | TI-2215 | TI-2215A | A | TEMPERATURE INDICATION |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | - | UCP-A | CCR
277 | TAH-2215 | TAH-2215A | A | TEMPERATURE ALARM HIGH |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | - | UCP-A | CCR
278
279 | TE-2216 | TE-2216A | A | RTD THERMO ELEMENT | Comp. Frame Temp. Measurment | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  |  | FIELD |  |  | - | RTD |  |  | HOLD | [5 empty] | ZONE2, IIB, T3
280 | TT-2216 | TT-2216A | A | TEMPERATURE TRANSMITTER |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | AI | FIELD | Trip Relay UCP A | 24VDC | - | 4-20mA Hart | IS |  | HOLD | HOLD |  |  |  |  | ZONE2, IIB, T3
281 | TI-2216 | TI-2216A | A | RTD THERMO ELEMENT |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  |  | UCP-A | CCR
282 | TAH-2216 | TAH-2216A | A | TEMPERATURE ALARM HIGH |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | - | UCP-A | CCR
283 | TAHH-2216 | TAHH-2216A | A | TEMPERATURE ALARM HIGH HIGH |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  |  | UCP-A | CCR
284
285 | TE-2217 | TE-2217A | A | RTD THERMO ELEMENT | Comp. Power Bearing Temp. Measurment | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  |  | FIELD |  |  | - | RTD |  |  | HOLD | [5 empty] | ZONE2, IIB, T3
286 | TT-2217 | TT-2217A | A | TEMPERATURET RAMSMITTER |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | AI | UCP-A | Trip Relay UCP A | 24VDC |  | 4-20mA Hart | IS
287 | TI-2217 | TI-2217A | A | RTD THERMO ELEMENT |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  |  | UCP-A | CCR
288 | TAH-2217 | TAH-2217A | A | TEMPERATURE ALARM HIGH |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | - | UCP-A | CCR
289 | TAHH-2217 | TAHH-2217A | A | TEMPERATURE ALARM HIGH HIGH |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | - | UCP-A | CCR
290
291 | TE-2218 | TE-2218A | A | RTD THERMO ELEMENT | Comp. Power Bearing Temp. Measurment | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  |  | FIELD |  |  | - | RTD |  |  | HOLD | [5 empty] | ZONE2, IIB, T3
292 | TT-2218 | TT-2218A | A | TEMPERATURE TRANSMITTER |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | AI | FIELD | Trip Relay UCP A | 24VDC | - | 4-20mA Hart | IS |  | HOLD | HOLD |  |  |  |  | ZONE2, IIB, T3
293 | TI-2218 | TI-2218A | A | RTD THERMO ELEMENT |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | - | UCP-A | CCR
294 | TAH-2218 | TAH-2218A | A | TEMPERATURE ALARM HIGH |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | - | UCP-A | CCR
295 | TAHH-2218 | TAHH-2218A | A | TEMPERATURE ALARM HIGH HIGH |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | - | UCP-A | CCR
296
297 | TE-2219 | TE-2219A | A | RTD THERMO ELEMENT | Comp. Power Bearing Temp. Measurment | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  |  | FIELD |  |  | - | RTD |  |  | HOLD | [5 empty] | ZONE2, IIB, T3
298 | TT-2219 | TT-2219A | A | TEMPERATURE TRANSMITTER |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | AI | FIELD | Trip Relay UCP A | 24VDC | - | 4-20mA Hart | IS |  | HOLD | HOLD |  |  |  |  | ZONE2, IIB, T3
299 | TI-2219 | TI-2219A | A | TEMPERATURE TRAMSMITTER |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | - | UCP-A | CCR
300 | TAH-2219 | TAH-2219A | A | TEMPERATURE ALARM HIGH |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | - | UCP-A | CCR
301 | TAHH-2219 | TAHH-2219A | A | TEMPERATURE ALARM HIGH HIGH |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | - | UCP-A | CCR
302
303 | ZT-2201 | ZT-2201A | A | ROD DROP TRANSMITTER | Cylinder Rod Drop Detector | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | AI | FIELD | UCP-A | 24VDC | - | 4-20mA | IS |  | HOLD | HOLD |  |  |  |  | ZONE2, IIB, T3
304 | ZE-2201 | ZE-2201A | A | ROD DROP ELEMENT |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  |  | FIELD
305 | ZI-2201 | ZI-2201A | A | ROD DROP INDICATOR |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  |  | UCP-A | CCR
306 | ZAH-2201 | ZAH-2201A | A | ROD DROP ALARM HIGH |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | - | UCP-A | CCR
307
308 | ZT-2200 | ZT-2200A | A | ROD DROP TRANSMITTER | LEFT Cylinder Rod Drop Detector | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | AI | FIELD | UCP-A | 24VDC | - | 4-20mA | IS |  | HOLD | HOLD |  |  |  |  | ZONE2, IIB, T3
309 | ZE-2200 | ZE-2200A | A | ROD DROP ELEMENT |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  |  | FIELD
310 | ZI-2200 | ZI-2200A | A | ROD DROP INDICATOR |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  |  | UCP-A | CCR
311 | ZAH-2200 | ZAH-2200A | A | ROD DROP ALARM HIGH |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | - | UCP-A | CCR
312
313 | TE-2222 | TE-2222A | A | RTD THERMO ELEMENT | MAIN MOTOR R-PHASE WINDING TEMP. | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | AI | Motor | MCC |  | - | RTD | NIS |  | 0-100 | °C |  |  |  |  | ZONE2, IIB, T3
314 | TE-2228 | XL-2222A | A | RTD R TRIP FEEDBACK | MAIN MOTOR R-PHASE WINDING TEMPTRIP FEEDBACK. | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | DI | MCC | UCP-A | 24VDC | - | N.O | NIS
315
316 | TE-2225 | TE-2225A | A | RTD THERMO ELEMENT | MAIN MOTOR S-PHASE WINDING TEMP. | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | AI | Motor | MCC |  | - | RTD | NIS |  | 0-100 | °C |  |  |  |  | ZONE2, IIB, T3
317 | TE-2228 | XL-2225A | A | RTD S TRIP FEEDBACK | MAIN MOTOR S-PHASE WINDING TEMPTRIP FEEDBACK. | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | DI | MCC | UCP-A | 24VDC | - | N.O | NIS
318
319 | TE-2228 | TE-2228A | A | RTD THERMO ELEMENT | MAIN MOTOR T-PHASE WINDING TEMP. | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | AI | Motor | MCC |  | - | RTD | NIS |  | 0-100 | °C |  |  |  |  | ZONE2, IIB, T3
320 | TE-2228 | XL-2228A | A | RTD T TRIP FEEDBACK | MAIN MOTOR T-PHASE WINDING TEMPTRIP FEEDBACK. | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | DI | MCC | UCP-A | 24VDC | - | N.O | NIS
321
322 | HST-2205 | HST-2205 A | A | START COMMAND | LOOB OIL COOLER (AE-2101-OC A/B/C) | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | DOR | UCP-A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
323 | HSP-2205 | HSP-2205 A | A | STOP COMMAND |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | DOR | UCP-A | MCC | 24VDC | D | NC | NIS | [7 empty] | ZONE2, IIB, T3
324 | XL-2205 | XL-2205 A | A | RUNNING STATUS |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | DI | MCC | UCP-A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
325 | XA-2205 | XA-2205 A | A | FAILURE STATUS |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | DI | MCC | UCP-A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
326 | [7 empty] | - | - | -
327 | HST-2225 | HST-2225 A | A | START COMMAND | MOTOR BEARING DEVICE MOTOR | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 7A | - | - | - | DOR | UCP-A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
328 | HSP-2225 | HSP-2225 A | A | STOP COMMAND |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 7A | - | - | - | DOR | UCP-A | MCC | 24VDC | D | NC | NIS | [7 empty] | ZONE2, IIB, T3
329 | XL-2225 | XL-2225 A | A | RUNNING STATUS |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 7A | - | - | - | DI | MCC | UCP-A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
330 | XA-2225 | XA-2225 A | A | FAULT STATUS |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 7A | - | - | - | DI | MCC | UCP-A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
331
332 | HST-2224 | HST-2224 A | A | START COMMAND | MAKE UP GAS COMPRESSOR MAIN MOTOR | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 7A | - | - | - | DOR | UCP-A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
333 | HSP-2224 | HSP-2224 A | A | STOP COMMAND |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 7A | - | - | - | DOR | UCP-A | MCC | 24VDC | D | NC | NIS | [7 empty] | ZONE2, IIB, T3
334 | XL-2224 | XL-2224 A | A | RUNNING STATUS |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 7A | - | - | - | DI | MCC | UCP-A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
335 | XA-2224 | XA-2224 A | A | FAULT STATUS |  | PACKAGE COMPRESSOR C-2101A |  | - | - | - | DI | MCC | UCP-A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
336
337 | PCV-2123 | PCV-2123A | A | CONTROL VALVE | SPILL BACK VALVE | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 1A |  |  |  | - | UCP-A | FIELD |  | - |  |  | FO
338 | PCY-2123 | PCY-2123 A | A | CONTROLLER |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 1A |  |  |  | AOR | UCP-A | FIELD |  |  | 4-20mA | IS
339 | PCVY-2123 | PCYZ-2123A | A | Feed back |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 1A |  |  |  | AI | UCP-A | FIELD |  |  | 4-20mA | IS
340 | CZSO-2123 | CZSO-2123 A | A | LIMIT SWITCH |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 1A |  |  |  | DI | FIELD | UCP-A | 24VDC |  |  | NIS
341 | CZSC-2123 | CZSC-2123 A | A | LIMIT SWITCH |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 1A |  |  |  | DI | FIELD | UCP-A | 24VDC |  |  | NIS
342 | PY-2123 | PY-2123 A | A | SOLENOID VALVE |  | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 1A |  |  |  | DOR | UCP-A | FIELD | 24VDC |  |  | NIS
343
344
345 | XV-2121 | XV-2121A | A | INPUT ON OFF VALVE | INPUT ON OFF VALVE(CLINET SIDE) | PACKAGE COMPRESSOR C-2101 A | BK-GCS-PEDCO-120-PR-PI-0006-SHEET 1A |  |  |  | - | FIELD
346 | PSOV-2121 | PSOV-2121A | A | ON OFF VALVE SOLENOID |  | PACKAGE COMPRESSOR C-2101 A | BK-GCS-PEDCO-120-PR-PI-0006-SHEET 1A |  |  |  | DOR | UCP-A | FIELD | 24VDC | W | 24VDC | NIS | FO | [9 empty] | Valve is in client scope of supply
347 | XZIC-2121 | XZIC-2121A | A | LIMIT SWITCH |  | PACKAGE COMPRESSOR C-2101 A | BK-GCS-PEDCO-120-PR-PI-0006-SHEET 1A |  |  |  | DI | FIELD | UCP-B | 24VDC | W | 24VDC | NIS
348 | XZIO-2121 | XZIO-2121A | A | LIMIT SWITCH |  | PACKAGE COMPRESSOR C-2101 A | BK-GCS-PEDCO-120-PR-PI-0006-SHEET 1A |  |  |  | DI | FIELD | UCP-B | 24VDC | W | 24VDC | NIS
349
350 | XV-2133 | XV-2133A | A | OUTPUT OFF VALVE | OUTPUT OFF VALVE(CLINET SIDE) | PACKAGE COMPRESSOR C-2101 A | BK-GCS-PEDCO-120-PR-PI-0011-SHEET 1A |  |  |  | - | FIELD | [15 empty] | Valve is in client scope of supply
351 | PSOV-2233 | PSOV-2233A | A | ON OFF VALVE SOLENOID |  | PACKAGE COMPRESSOR C-2101 A | BK-GCS-PEDCO-120-PR-PI-0011-SHEET 1A |  |  |  | DOR | UCP-A | FIELD | 24VDC | W | 24VDC | NIS | FO
352 | XZIC-2133 | XZIC-2133A | A | LIMIT SWITCH |  | PACKAGE COMPRESSOR C-2101 A | BK-GCS-PEDCO-120-PR-PI-0011-SHEET 1A |  |  |  | DI | FIELD | UCP-B | 24VDC | W | 24VDC | NIS
353 | XZIO-2133 | XZIO-2133A | A | LIMIT SWITCH |  | PACKAGE COMPRESSOR C-2101 A | BK-GCS-PEDCO-120-PR-PI-0011-SHEET 1A |  |  |  | DI | FIELD | UCP-B | 24VDC | W | 24VDC | NIS
Note on B108: Forouzandeh Fatemeh: ALARM L,H چک شود

## LIST-B
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض
خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03)
I/O LIST
شماره پیمان: | [5 empty] | پروژه | بسته کاری | صادرکننده |  |  | تسهیلات |  | رشته | نوع مدرک |  | سریال | نسخه |  | از |  |  |  |  | شماره صفحه:
9184 – 073 - 053 | [5 empty] | BK | GCS | HY |  |  | 120 |  | IN | LI |  | 0005 | V01
Item No. |  |  |  | Description | Service 1 | Service 2 | P&ID No. | line Size | Connection |  | I/O Type |  | Location, Signal (To) | Power Supply | W/D | Signal Type | IS/NIS | Valve Action | Range/ Alarm Set point | Eng. Units | Engineering Documents |  |  |  | Hazardous Area | Manufacturer | Model Number | Remark
|  | Tag Number | Unit Number | [5 empty] | Size | Rating |  | Location, Signal ( From) | [8 empty] | Loop Diagram No. | Inst. Location Layout | Hook-Up Drawing | Data Sheet
1 | SV-2201 | SV-2201B | B | SOLENOID VALVE | INST. AIR SUPPLY | PACKAGE COMPRESSOR C-2101,2B | BK-GCS-HY-120-PR-PI-0001-SHEET 2B |  |  |  | DOR | UCP-B | FIELD | 24VDC | W | 24VDC | NIS | [7 empty] | ZONE2, IIB, T3
2 | SV-2202 | SV-2202B | B | SOLENOID VALVE | INST. AIR SUPPLY | PACKAGE COMPRESSOR C-2101,2B | BK-GCS-HY-120-PR-PI-0001-SHEET 2B |  |  |  | DOR | UCP-B | FIELD | 24VDC | W | 24VDC | NIS | [7 empty] | ZONE2, IIB, T3
3 | SV-2203 | SV-2203B | B | SOLENOID VALVE | INST. AIR SUPPLY | PACKAGE COMPRESSOR C-2101,2B | BK-GCS-HY-120-PR-PI-0001-SHEET 2B |  |  |  | DOR | UCP-B | FIELD | 24VDC | W | 24VDC | NIS | [7 empty] | ZONE2, IIB, T3
4
5 | PT-2123 | PT-2123B | B | PRESSURE TRANSMITTER | ON SUCTION SNUBBER 1S STAGE | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B | 8" |  |  | AI | FIELD | UCP-B | 24VDC | - | 4-20mA Hart | IS |  | 0-16 | BARG |  |  |  |  | ZONE2, IIB, T3
6 | PI-2123 | PI-2123B | B | PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  | - | UCP-B | CCR
7 | PAH-2123 | PAH-2123B | B | PRESSURE ALARM HIGH |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  | - | UCP-B | CCR
8
9 | FT-2121 | FT-2121B | B | FLOW TRANSMITTER | ON SUCTION SNUBBER 1S STAGE | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B | 8" |  |  | AI | FIELD | UCP-B | 24VDC | - | 4-20mA Hart | IS |  | 0-14000 | NM3/H |  |  |  |  | ZONE2, IIB, T3
10 | FE-2121 | FE-2121 B | B | FLOW ELEMENT |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  | - | FIELD | -
11 | FI-2121 | FI-2121 B | B | FLOW INDICATING |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  | - | UCP-B | CCR
12
13 | TT-2122 | TT-2122 B | B | TEMPERATURE TRANSMITTER | ON SUCTION SNUBBER 1S STAGE | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B | 8" |  |  | AI | FIELD | UCP-B | 24VDC | - | 4-20mA Hart | IS |  | 0-100 | °C |  |  |  |  | ZONE2, IIB, T3
14 | TI-2122 | TI-2122 B | B | TEMPERATURE INDICATING |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  | - | UCP-B | CCR
15 | TE-2122 | TE-2122B | B | THERMO ELEMENT |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  | -
16 | TW-2122 | TW-2122 B | B | THERMOWELL |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  | -
17
18 | PDT-2122 | PDT-2122 B | B | DIFF. PRESSURE TRANSMITTER | STRAINER FILTER | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B | 1" |  |  | AI | FIELD | UCP-B | 24VDC | - | 4-20mA Hart | IS |  | 0-1 | BARG |  |  |  |  | ZONE2, IIB, T3
19 | PDI-2122 | PDI-2122 B | B | DIFF. PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  | - | UCP-B | CCR
20 | PDAH-2122 | PDAH-2122 B | B | DIFF. PRESSURE ALARM HIGH |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  | - | UCP-B | CCR
21
22 | PT-2192 A/B | PT-2192 A/BB | B | PRESSURE TRANSMITTER | ON DISCHARGE SNUBBER 1ST STAGE | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B | 6" |  |  | AI | FIELD | UCP-B | 24VDC | - | 4-20mA Hart | IS |  | 0-40 | BARG |  |  |  |  | ZONE2, IIB, T3
23 | PI-2192 A/B | PI-2192 A/BB | B | PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  | - | UCP-B | CCR
24 | PAH-2192 A/B | PAH-2192 A/BB | B | PRESSURE ALARM HIGH |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  | - | UCP-B | CCR
25
26 | TT-2192 | TT-2192 B | B | TEMPERATURE TRANSMITTER | ON DISCHARGE SNUBBER 1ST STAGE | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B | 6" |  |  | AI | FIELD | UCP-B | 24VDC | - | 4-20mA Hart | IS |  | 0-200 | °C |  |  |  |  | ZONE2, IIB, T3
27 | TE-2191 | TE-2191 B | B | THERMO ELEMENT |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  |  | FIELD | -
28 | TW-2191 | TW-2191 B | B | THERMOWELL |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  |  | FIELD | -
29 | TI-2192 | TI-2192 B | B | TEMPERATURE INDICATING |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  | - | UCP-B | CCR
30
31 | TT-2191 | TT-2191 B | B | TEMPERATURE TRANSMITTER | ON DISCHARGE SNUBBER 1ST STAGE | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  | AI | FIELD | UCP-B | 24VDC | - | 4-20mA Hart | IS |  | 0-200 | °C |  |  |  |  | ZONE2, IIB, T3
32 | TI-2191 | TI-2191B | B | TEMPERATURE INDICATING |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  | - | UCP-B | CCR
33 | TAH-2191 | TAH-2191B | B | TEMPERATURE ALARM HIGH |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  | - | UCP-B | CCR
34 |  |  | B
35 | TS-2191 | TS-2191B | B | TEMPERATURE SWITCH | ON DISCHARGE SNUBBER 1ST STAGE | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  | DI | FIELD | Trip Relay UCP B | 24VDC |  | NC | N'IS |  | 0-200/160 | °C
36 | TAHH-2191 | TAHH-2191B | B | TEMPERATURE ALARM HIGH HIGH |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B | - | - | - |  | FIELD | UCP-B | 24VDC
37
38 | TT-2194 | TT-2194 B | B | TEMPERATURE TRANSMITTER | ON DISCHARGE SNUBBER 2ND STAGE | PACKAGE COMPRESSOR C-2102B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  | AI | FIELD | CCR | 24VDC | - | 4-20mA Hart | IS |  | 0-200 | °C |  |  |  |  | ZONE2, IIB, T3
39 | TE-2194 | TE-2194 B | B | THERMO ELEMENT |  | PACKAGE COMPRESSOR C-2102B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  |  | FIELD | -
40 | TW-2194 | TW-2194 B | B | THERMOWELL |  | PACKAGE COMPRESSOR C-2102B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  |  | FIELD | -
41 | TI-2194 | TI-2194 B | B | TEMPERATURE INDICATING |  | PACKAGE COMPRESSOR C-2102B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  | - | UCP-B | CCR
42 | TAH-2194 | TAH-2194 B | B | TEMPERATURE ALARM HIGH |  | PACKAGE COMPRESSOR C-2102B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  | - | UCP-B | CCR
43 |  |  | B
44 | TS-2194 | TS-2194 B | B | TEMPERATURE SWITCH | ON DISCHARGE SNUBBER 2ND STAGE | PACKAGE COMPRESSOR C-2102B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  | DI | FIELD | Trip Relay UCP B |  |  |  | N'IS
45 | TAHH-2194 | TAHH-2194 B | B | TEMPERATURE ALARAM HIGH HIGH |  | PACKAGE COMPRESSOR C-2102B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  | - | FIELD | UCP
46
47 | PT-2124 | PT-2124 B | B | PRESSURE TRANSMITTER | ON DISCHARGE LINE SNUBBER 2ND STAGE | PACKAGE COMPRESSOR C-2102B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B | 6" |  |  | AI | FIELD | UCP-B | 24VDC | - | 4-20mA Hart | IS |  | 0-80 | BARG |  |  |  |  | ZONE2, IIB, T3
48 | PI-2124 | PI-2124 B | B | PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2102B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  | - | UCP-B | CCR
49 | PAHH-2124 | PAHH-2124 B | B | PRESSURE ALARM HIGH HIGH |  | PACKAGE COMPRESSOR C-2102B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  | - | UCP-B | CCR
50 |  |  | B
51 | PS-2195 | PS-2195 B | B | PRESSURE SWITCH | ON DISCHARGE LINE SNUBBER 2ND STAGE | PACKAGE COMPRESSOR C-2102B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B | 6" |  |  | DI | FIELD | Trip Relay UCP B |  |  |  | N'IS
52 | PAHH-2195 | PAHH-2195 B | B | PRESSURE Trip HIGH HIGH |  | PACKAGE COMPRESSOR C-2102B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  | - | FIELD | UCP-B
53
54 | TT-2123 | TT-2123 B | B | TEMPERATURE TRANSMITTER | ON DISCHARGE LINE SNUBBER 2ND STAGE | PACKAGE COMPRESSOR C-2102B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B | 6" |  |  | AI | FIELD | UCP-B | 24VDC | - | 4-20mA Hart | IS |  | 0-200 | °C |  |  |  |  | ZONE2, IIB, T3
55 | TE-2123 | TE-2123 B | B | THERMO ELEMENT |  | PACKAGE COMPRESSOR C-2102B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  |  | - | FIELD
56 | TW2123 | TW2123 B | B | THERMOWELL |  | PACKAGE COMPRESSOR C-2102B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  |  | - | FIELD
57 | TI-2123 | TI-2123 B | B | TEMPERATURE INDICATING |  | PACKAGE COMPRESSOR C-2102B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  | - | UCP-B | CCR
58 |  |  | B
59 | PT-2197 | PT-2197B | B | PRESSURE TRANSMITTER | ON SUCTION SNUBBER 2ND STAGE | PACKAGE COMPRESSOR C-2102B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B | 6" |  |  | AI | FIELD | UCP-B | 24VDC | - | 4-20mA Hart | IS |  | 0-40 | BARG |  |  |  |  | ZONE2, IIB, T3
60 | PI-2197 | PI-2197 B | B | PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2102B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  | - | UCP-B | CCR
61
62 | FT-2197 | FT-2197B | B | FLOW TRANSMITTER | ON SUCTION SNUBBER 2ND STAGE | PACKAGE COMPRESSOR C-2102B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B | 6" |  |  | AI | FIELD | UCP-B | 24VDC | - | 4-20mA Hart | IS |  | 0-14000 | NM3/H |  |  |  |  | ZONE2, IIB, T3
63 | FE-2197 | FE-2197B | B | FLOW ELEMENT |  | PACKAGE COMPRESSOR C-2102B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  | - | FIELD | -
64 | FI-2197 | FI-2197B | B | FLOW INDICATING |  | PACKAGE COMPRESSOR C-2102B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  | - | UCP-B | CCR
65
66 | TT-2197 | TT-2197B | B | TEMPERATURE TRANSMITTER | ON SUCTION SNUBBER 2ND STAGE | PACKAGE COMPRESSOR C-2102B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B | 6" |  |  | AI | FIELD | UCP-B | 24VDC | - | 4-20mA Hart | IS |  | 0-100 | °C |  |  |  |  | ZONE2, IIB, T3
67 | TE-2197 | TE-2197B | B | THERMO ELEMENT |  | PACKAGE COMPRESSOR C-2102B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  | - | - | FIELD
68 | TW-2197 | TW-2197B | B | THERMOWELL |  | PACKAGE COMPRESSOR C-2102B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  |  | - | FIELD
69 | TI-2197 | TI-2197B | B | TEMPERATURE INDICATING |  | PACKAGE COMPRESSOR C-2102B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  |  | UCP-B | CCR
70
71 | PDT-2197 | PDT-2197B | B | DIFF. PRESSURE TRANSMITTER | STRAINER FILTER 2ND STAGE | PACKAGE COMPRESSOR C-2102B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B | 1" |  |  | AI | FIELD | UCP-B | 24VDC | - | 4-20mA Hart | IS |  | 0-6 | BARG |  |  |  |  | ZONE2, IIB, T3
72 | PDI-2197 | PDI-2197B | B | DIFF. PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2102B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  | - | UCP-B | CCR
73 | PDAH-2197 | PDAH-2197B | B | DIFF. PRESSURE ALARM HIGH |  | PACKAGE COMPRESSOR C-2102B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  | - | UCP-B | CCR
74
75 | PT-2201 | PT-2201B | B | PRESSURE TRANSMITTER | ON INSTRUMENT LINE | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 2B | 2" |  |  | AI | FIELD | UCP-B | 24VDC | - | 4-20mA Hart | IS |  | HOLD | HOLD |  |  |  |  | ZONE2, IIB, T3
76 | PI-2201 | PI-2201B | B | PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 2B |  |  |  | - | UCP-B | CCR
77 | PAL-2201 | PAL-2201B | B | PRESSURE ALARM LOW |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 2B |  |  |  | - | UCP-B | CCR
78
79 | PT-2200 | PT-2200 B | B | PRESSURE TRANSMITTER | ON LUBRICATOR | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | AI | FIELD | UCP-B | 24VDC | - | 4-20mA Hart | IS |  | HOLD | HOLD |  |  |  |  | ZONE2, IIB, T3
80 | PI-2200 | PI-2200 B | B | PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | - | UCP-B | CCR
81 | PAL-2200 | PAL-2200 B | B | PRESSURE ALARM LOW |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | - | UCP-B | CCR
82 |  |  | B
83 | LT-2200 | LT-2200 B | B | LEVEL TRANSMITTER | ON CRANK CASE | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | AI | FIELD | UCP-B | 24VDC | - | 4-20mA Hart | IS |  | HOLD | HOLD |  |  |  |  | ZONE2, IIB, T3
84 | LI-2200 | LI-2200 B | B | LEVEL INDICATING |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | - | UCP-B | CCR
85 | LAL-2200 | LAL-2200 B | B | LEVEL ALARM LOW |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | - | UCP-B | CCR
86
87 | LT-2213 | LT-2213 B | B | LEVEL TRANSMITTER | WATER RESERVOIR | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | AI | FIELD | Trip Relay UCP B | 24VDC | - | 4-20mA Hart | IS |  | HOLD | HOLD |  |  |  |  | ZONE2, IIB, T3
88 | LI-2213 | LI-2213 B | B | LEVEL INDICATING |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | - | UCP-B | CCR
89 | LAL-2213 | LAL-2213 B | B | LEVEL ALARM LOW |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | - | UCP-B | CCR
90 | LALL-2213 | LALL-2213 B | B | LEVEL ALARM LOW LOW |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | - | UCP-B | CCR
91
92 | TT-2203 | TT-2203 B | B | TEMPERATURE TRANSMITTER | ON CRANK CASE | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | AIR | FIELD | UCP-B | 24VDC | - | 4-20mA Hart | IS |  | 0-200 | °C |  |  |  |  | ZONE2, IIB, T3
93 | TE-2203 | TE-2203 B | B | THERMO ELEMENT |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  |  | FIELD | -
94 | TW-2203 | TW-2203 B | B | THERMOWELL |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  |  | FIELD | -
95 | TI-2203 | TI-2203 B | B | THERMO ELEMENT |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  |  | UCP-B | CCR
96
97 | HSP-2203 | HSP-2203 B | B | START COMMAND HEATER CRANK CASE | START COMMAND HEATER CRANK CASE | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | DOR | UCP-B | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
98 | HST-2203 | HST-2203 B | B | STOP COMMAND HEATER CRANK CASE | STOP COMMAND HEATER CRANK CASE | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | DOR | UCP-B | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
99 | XL-2203 | XL-2203 B | B | RUNNING STATUS HEATER CRANK CASE | RUNNING STATUS HEATER CRANK CASE | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | DI | MCC | UCP-B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
100 | XA-2203 | XA-2203 B | B | FAILURE STATUS HEATER CRANK CASE | FAILURE STATUS HEATER CRANK CASE | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | DI | MCC | UCP-B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
101
102 | HST-2200 | HST-2200 B | B | START COMMAND HEATER LUBRICATOR | HEATER ON LUBRICATOR | PACKAGE COMPRESSOR C-1401B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | DOR | UCP-B | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
103 | HSP-2200 | HSP-2200 B | B | STOP COMMAND HEATER LUBRICATOR | HEATER ON LUBRICATOR | PACKAGE COMPRESSOR C-1401B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | DOR | UCP-B | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
104 | XL-2200 | XL-2200 B | B | RUNNING STATUS HEATER LUBRICATOR | HEATER ON LUBRICATOR | PACKAGE COMPRESSOR C-1401B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | DI | MCC | UCP-B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
105 | XA-2200 | XA-2200 B | B | FAILURE STATUS HEATER LUBRICATOR | HEATER ON LUBRICATOR | PACKAGE COMPRESSOR C-1401B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | DI | MCC | UCP-B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
106
107 | TT-2204 | TT-2204B | B | TEMPERATURE TRANSMITTER | LUBE OIL FILTER DOWNSTREAM | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B | 4" |  |  | AI | FIELD | UCP-B | 24VDC | - | 4-20mA Hart | IS |  | 0-100 | °C |  |  |  |  | ZONE2, IIB, T3
108 | TI-2204 | TI-2204B | B | TEMPERATURE INDICATING |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | - | UCP-B | CCR
109 | TW-2204 | TW-2204B | B | THERMOWELL | LUBE OIL FILTER DOWNSTREAM | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  |  | FIELD | -
110 | TAH-2204 | TAH-2204B | B | TEMPERATURE ALARM HIGH |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | - | UCP-B | CCR
111 | TAL-2204 | TAL-2204B | B | TEMPERATURE ALARM LOW |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | - | UCP-B | CCR
112
113 | PT-2204 | PT-2204B | B | PRESSURE TRANSMITTER | LUBE OIL FILTER DOWNSTREAM | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B | 2" |  |  | AIR | FIELD | UCP-B | 24VDC | - | 4-20mA Hart | IS |  | 0-16 | BARG |  |  |  |  | ZONE2, IIB, T3
114 | PI-2204 | PI-2204B | B | PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | - | UCP-B | CCR
115 | PAL-2204 | PAL-2204B | B | PRESSURE ALARM LOW |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | - | UCP-B | CCR
116 | PAH-2204 | PAH-2204B | B | PRESSURE ALARM HIGH |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | - | UCP-B | CCR
117 | PAH2-2204 | PAH2-2204B | B | PRESSURE ALARM HIGH2 |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | - | UCP-B | CCR
118
119 | PS-2204 | PS-2204B | B | PRESSURE SWITCH | LUBE OIL FILTER DOWNSTREAM | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | DI | Field | Trip Relay UCP B |  |  |  | N'IS |  | 0-16/6 | BARG |  |  |  |  | ZONE2, IIB, T3
120 | PALL-2204 | PALL-2204B | B | PRESSURE ALARM LOW LOW |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | - | Field | UCP-B
121
122 | PDT-2204 | PDT-2204 B | B | DIFF. PRESSURE TRANSMITTER | LUBE OIL FILTER | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B | 1" |  |  | AIR | FIELD | UCP-B | 24VDC | - | 4-20mA Hart | IS |  | 0-6 | BARG |  |  |  |  | ZONE2, IIB, T3
123 | PDI-2204 | PDI-2204 B | B | DIFF. PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | - | UCP-B | CCR
124 | PDAH-2204 | PDAH-2204 B | B | DIFF. PRESSURE ALARM HIGH |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | - | UCP-B | CCR
125 |  |  | B
126 | HST-2202 | HST-2202 B | B | START COMMAND AUX. OIL PUMP | AUX. OIL PUMP (P-2101-AP B) | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | DOR | UCP-B | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
127 | HSP-2202 | HSP-2202 B | B | STOP COMMAND AUX. OIL PUMP | AUX. OIL PUMP (P-2101-AP B) | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | DOR | UCP-B | MCC | 24VDC | D | NC | NIS | [7 empty] | ZONE2, IIB, T3
128 | XL-2202 | XL-2202 B | B | RUNNING STATUSAUX. OIL PUMP | AUX. OIL PUMP (P-2101-AP B) | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | DI | MCC | UCP-B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
129 | XA-2202 | XA-2202 B | B | FAILURE STATUS AUX. OIL PUMP | AUX. OIL PUMP (P-2101-AP B) | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | DI | MCC | UCP-B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
130
131 | HST-2201 | HST-2201 B | B | START COMMAND LUBRICATOR. OIL PUMP | LUBRICATOR. OIL PUMP (2101-LP B) | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | DOR | UCP-B | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
132 | HSP-2201 | HSP-2201 B | B | STOP COMMAND LUBRICATOR. OIL PUMP | LUBRICATOR. OIL PUMP (2101-LP B) | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | DOR | UCP-B | MCC | 24VDC | D | NC | NIS | [7 empty] | ZONE2, IIB, T3
133 | XL-2201 | XL-2201 B | B | RUNNING STATUS LUBRICATOR. OIL PUMP | LUBRICATOR. OIL PUMP (2101-LP B) | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | DI | MCC | UCP-B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
134 | XA-2201 | XA-2201 B | B | FAILURE STATUS LUBRICATOR. OIL PUMP | LUBRICATOR. OIL PUMP (2101-LP B) | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | DI | MCC | UCP-B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
135
136 | HST-2205 | HST-2205 B | B | START COMMAND LUB OIL COOLER | LUB OIL COOLER (AE-2101-OC B) | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | DOR | UCP-B | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
137 | HSP-2205 | HSP-2205 B | B | STOP COMMAND LUB OIL COOLER | LUB OIL COOLER (AE-2101-OC B) | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | DOR | UCP-B | MCC | 24VDC | D | NC | NIS | [7 empty] | ZONE2, IIB, T3
138 | XL-2205 | XL-2205 B | B | RUNNING STATUS LUB OIL COOLER | LUB OIL COOLER (AE-2101-OC B) | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | DI | MCC | UCP-B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
139 | XA-2205 | XA-2205 B | B | FAILURE STATUS LUB OIL COOLER | LUB OIL COOLER (AE-2101-OC B) | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | DI | MCC | UCP-B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
140
141 | PT-2210 | PT-2210B | B | PRESSURE TRANSMITTER | N2 TO CYLINDER PACKING INLET | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 4B | 1" |  |  | AI | FIELD | UCP-B | 24VDC | - | 4-20mA Hart | IS |  | 0-6 | BARG |  |  |  |  | ZONE2, IIB, T3
142 | PI-2210 | PI-2210B | B | PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 4B |  |  |  | - | UCP-B | CCR
143 | PAL-2210 | PAL-2210B | B | PRESSURE ALARM LOW |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 4B |  |  |  | - | UCP-B | CCR
144
145 | PT-2211 | PT-2211B | B | PRESSURE TRANSMITTER | N2 TO CYLINDER PACKING INLET | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 4B | 1" |  |  | AI | FIELD | UCP-B | 24VDC | - | 4-20mA Hart | IS |  | 0-6 | BARG |  |  |  |  | ZONE2, IIB, T3
146 | PI-2211 | PI-2211B | B | PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 4B |  |  |  | - | UCP-B | CCR
147 | PAL-2211 | PAL-2211B | B | PRESSURE ALARM LOW |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 4B |  |  |  | - | UCP-B | CCR
148
149 | HST-2220 | HST-2220 B | B | START COMMAND WATER CONSULE COOLER | WATER CONSULE COOLER (AE-2101-WC B) | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  | DOR | UCP-B | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
150 | HSP-2220 | HSP-2220 B | B | STOP COMMAND WATER CONSULE COOLER | WATER CONSULE COOLER (AE-2101-WC B) | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  | DOR | UCP-B | MCC | 24VDC | D | NC | NIS | [7 empty] | ZONE2, IIB, T3
151 | XL-2220 | XL-2220 B | B | RUNNING STATUS WATER CONSULE COOLER | WATER CONSULE COOLER (AE-2101-WC B) | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  | DI | MCC | UCP-B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
152 | XA-2220 | XA-2220 B | B | FAILURE STATUS WATER CONSULE COOLER | WATER CONSULE COOLER (AE-2101-WC B) | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  | DI | MCC | UCP-B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
153
154 | HST-2221 | HST-2221 B | B | START COMMAND AUX WATER PUMP | AUX WATER PUMP (P-2101-AX B) | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  | DOR | UCP-B | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
155 | HSP-2221 | HSP-2221 B | B | STOT COMMAND AUX WATER PUMP | AUX WATER PUMP (P-2101-AX B) | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  | DOR | UCP-B | MCC | 24VDC | D | NC | NIS | [7 empty] | ZONE2, IIB, T3
156 | XL-2221 | XL-2221B | B | RUNNING STATUS AUX WATER PUMP | AUX WATER PUMP (P-2101-AX B) | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  | DI | MCC | UCP-B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
157 | XA-2221 | XA-2221 B | B | FAILURE STATUS AUX WATER PUMP | AUX WATER PUMP (P-2101-AX B) | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  | DI | MCC | UCP-B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
158
159 | HST-2222 | HST-2222 B | B | START COMMAND MAIN WATER PUMP | MAIN WATER PUMP (P-2101-WP B) | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  | DOR | UCP-B | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
160 | HSP-2222 | HSP-2222 B | B | STOP COMMAND MAIN WATER PUMP | MAIN WATER PUMP (P-2101-WP B) | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  | DOR | UCP-B | MCC | 24VDC | D | NC | NIS | [7 empty] | ZONE2, IIB, T3
161 | XL-2222 | XL-2222B | B | RUNNING STATUS MAIN WATER PUMP | MAIN WATER PUMP (P-2101-WP B) | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  | DI | MCC | UCP-B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
162 | XA-2222 | XA-2222 B | B | FAILURE STATUS MAIN WATER PUMP | MAIN WATER PUMP (P-2101-WP B) | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  | DI | MCC | UCP-B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
163
164 | HST-2223 | HST-2223 B | B | START COMMAND HEATER WATER CONSULE | WATER CONSULE COOLER HEATER (AE-2101-WC B) | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  | DOR | UCP-B | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
165 | HSP-2223 | HSP-2223 B | B | STOP COMMAND HEATER WATER CONSULE | WATER CONSULE COOLER HEATER (AE-2101-WC B) | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  | DOR | UCP-B | MCC | 24VDC | D | NC | NIS | [7 empty] | ZONE2, IIB, T3
166 | XL-2223 | XL-2223B | B | RUNNING STATUS HEATER WATER CONSULE | WATER CONSULE COOLER HEATER (AE-2101-WC B) | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  | DI | MCC | UCP-B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
167 | XA-2223 | XA-2223 B | B | FAILURE STATUS HEATER WATER CONSULE | WATER CONSULE COOLER HEATER (AE-2101-WC B) | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  | DI | MCC | UCP-B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
168
169 | PT-2220 | PT-2220B | B | PRESSURE TRANSMITTER | WATER TO CYLINDERS | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B | 2" |  |  | AIR | FIELD | FIELD | 24VDC | - | 4-20mA Hart | IS |  | 0-16 | BARG |  |  |  |  | ZONE2, IIB, T3
170 | PI-2220 | PI-2220B | B | PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  | - | UCP-B | CCR
171 | PAL-2220 | PAL-2220B | B | PRESSURE ALARM LOW |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  | - | UCP-B | CCR
172 | PAH-2220 | PAH-2220B | B | PRESSURE ALARM HIGH |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  | - | UCP-B | CCR
173
174 | PT-2221 | PT-2221B | B | PRESSURE TRANSMITTER | WATER TO CYLINDERS | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B | 2" |  |  | AI | FIELD | FIELD | 24VDC | - | 4-20mA Hart | IS |  | 0-16 | BARG |  |  |  |  | ZONE2, IIB, T3
175 | PI-2221 | PI-2221B | B | PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  | - | UCP-B | CCR
176 | PAL-2221 | PAL-2221B | B | PRESSURE ALARM LOW |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  | - | UCP-B | CCR
177
178 | PS-2220 | PS-2220B | B | PRESSURE SWITCH | WATER TO CYLINDERS | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B | 2" |  |  | DI | Field | USD |  |  |  | N'IS |  | 0-16 | BARG
179 | PALL-2220 | PALL-2220B | B | PRESSURE ALARM LOW LOW |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  | - | Field | UCP-B
180
181 | TT-2213 | TT-2213B | B | TEMPERATURE TRANSMITTER | WATER RESERVOIR | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  | AIR | FIELD | UCP-B | 24VDC | - | 4-20mA Hart | IS |  | 0-100 | °C |  |  |  |  | ZONE2, IIB, T3
182 | TE-2213 | TE-2213B | B | THERMO ELEMENT |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B | [5 empty] | FIELD
183 | TW-2213 | TW-2213B | B | THERMOWELL |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B | [5 empty] | FIELD
184 | TI-2213 | TI-2213B | B | TEMPERATURE INDICATING |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  | - | UCP-B | CCR
185 | TAH-2213 | TAH-2213B | B | TEMPERATURE ALARM HIGH |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  | - | UCP-B | CCR
186 | TAL-2213 | TAL-2213B | B | TEMPERATURE ALARM LOW |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  | - | UCP-B | CCR
187
188 | FT-2206 | FT-2206B | B | FLOW TRANSMITTER | WATER TO CYLINDERS | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B | 2" |  |  | AI | FIELD | UCP-B | 24VDC | - | 4-20mA Hart | IS |  | 0-16 | BARG |  |  |  |  | ZONE2, IIB, T3
189 | FE-2221 | FE-2221B | B | FLOW ELEMENT |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  | - | FIELD | -
190 | FI-2221 | FI-2221B | B | FLOW INDICATING |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  | - | UCP-B | CCR
191
192 | HS-2239-L | HS-2239-LB | B | SELECTOR SWITCH | LOCAL MODE SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B | - | - | - | DI | LCP-B | UCP-B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
193 | HS-2239-R | HS-2239-RB | B | SELECTOR SWITCH | REMOTE MODE SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B | - | - | - | DI | LCP-B | UCP-B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
194 | HS-2230-M | HS-2230-MB | B | SELECTOR SWITCH | AUX. LUBE OIL PUMP MANU. SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B | - | - | - | DI | LCP-B | UCP-B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
195 | HS-2230-U | HS-2230-UB | B | SELECTOR SWITCH | AUX. LUBE OIL PUMP AUTO. SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B | - | - | - | DI | LCP-B | UCP-B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
196 | HS-2231-M | HS-2231-MB | B | SELECTOR SWITCH | OIL COOLER . SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B | - | - | - | DI | LCP-B | UCP-B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
197 | HS-2231-U | HS-2231-UB | B | SELECTOR SWITCH | OIL COOLER . SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B | - | - | - | DI | LCP-B | UCP-B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
198 | HS-2233-M | HS-2233-MB | B | SELECTOR SWITCH | MAIN WATER PUMP MANU SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B | - | - | - | DI | LCP-B | UCP-B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
199 | HS-2233-U | HS-2233-UB | B | SELECTOR SWITCH | MAIN WATER PUMP AUTO SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B | - | - | - | DI | LCP-B | UCP-B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
200 | HS-2234-M | HS-2234-MB | B | SELECTOR SWITCH | AUX WATER PUMP MANU SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B | - | - | - | DI | LCP-B | UCP-B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
201 | HS-2234-U | HS-2234-UB | B | SELECTOR SWITCH | AUX WATER PUMP AUTO SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B | - | - | - | DI | LCP-B | UCP-B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
202 | HS-2235-M | HS-2235-MB | B | SELECTOR SWITCH | WATER COOLER MANU SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B | - | - | - | DI | LCP-B | UCP-B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
203 | HS-2235-U | HS-2235-UB | B | SELECTOR SWITCH | WATER COOLER AUTO SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B | - | - | - | DI | LCP-B | UCP-B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
204 | HS-2236 | HS-2236B | B | PUSH BUTTON | LAMP TEST PUSHBUTTON SWITCH | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B | - | - | - | DI | LCP-B | UCP-B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
205 | HS-2237-T | HS-2237-TB | B | PUSH BUTTON | MAIN MOTOR START PUSHBUTTON | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B |  |  |  | DI | LCP-B | UCP-B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
206 | HS-2237-P | HS-2237-PB | B | PUSH BUTTON | MAIN MOTOR STOP PUSHBUTTON | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B |  |  |  | DI | LCP-B | UCP-B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
207 | HS-2238-T | HS-2238-TB | B | PUSH BUTTON | OIL HEATER ON PUSHBUTTON | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B |  |  |  | DI | LCP-B | UCP-B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
208 | HS-2238-P | HS-2238-PB | B | PUSH BUTTON | OIL HEATER OFF PUSHBUTTON | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B |  |  |  | DI | LCP-B | UCP-B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
209 | HS-2239-T | HS-2239-TB | B | PUSH BUTTON | AUX. LUBE OIL PUMP START PUSHBUTTON | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B |  |  |  | DI | LCP-B | UCP-B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
210 | HS-2239-P | HS-2239-PB | B | PUSH BUTTON | AUX. LUBE OIL PUMP STOP PUSHBUTTON | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B |  |  |  | DI | LCP-B | UCP-B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
211 | HS-2240-T | HS-2240-TB | B | PUSH BUTTON | OIL COOLER MOTOR A START PUSHBUTTON | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B |  |  |  | DI | LCP-B | UCP-B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
212 | HS-2240-P | HS-2240-PB | B | PUSH BUTTON | OIL COOLER MOTOR A STOP PUSHBUTTON | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B |  |  |  | DI | LCP-B | UCP-B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
213 | HS-2241-T | HS-2241-TB | B | PUSH BUTTON | OIL COOLER MOTOR B START PUSHBUTTON | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B |  |  |  | DI | LCP-B | UCP-B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
214 | HS-2241-P | HS-2241-PB | B | PUSH BUTTON | OIL COOLER MOTOR B STOP PUSHBUTTON | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B |  |  |  | DI | LCP-B | UCP-B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
215 | HS-2242-T | HS-2242-TB | B | PUSH BUTTON | LUB L HEATER ON PUSHBUTTON | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B |  |  |  | DI | LCP-B | UCP-B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
216 | HS-2242-P | HS-2242-PB | B | PUSH BUTTON | LUB HEATER OFF PUSHBUTTON | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B |  |  |  | DI | LCP-B | UCP-B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
217 | HS-2243-T | HS-2243-TB | B | PUSH BUTTON | LUB MOTOR START PUSHBUTTON | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B |  |  |  | DI | LCP-B | UCP-B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
218 | HS-2243-P | HS-2243-PB | B | PUSH BUTTON | LUB MOTOR STOP PUSHBUTTON | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B |  |  |  | DI | LCP-B | UCP-B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
219 | HS-2244-T | HS-2244-TB | B | PUSH BUTTON | MAIN WATER PUMP MOTOR START PUSHBUTTON | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B |  |  |  | DI | LCP-B | UCP-B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
220 | HS-2244-P | HS-2244-PB | B | PUSH BUTTON | MAIN WATER PUMP MOTOR STOP PUSHBUTTON | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B |  |  |  | DI | LCP-B | UCP-B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
221 | HS-2245-T | HS-2245-TB | B | PUSH BUTTON | AUX WATER PUMP MOTOR START PUSHBUTTON | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B |  |  |  | DI | LCP-B | UCP-B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
222 | HS-2245-P | HS-2245-PB | B | PUSH BUTTON | AUX WATER PUMP MOTOR STOP PUSHBUTTON | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B |  |  |  | DI | LCP-B | UCP-B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
223 | HS-2246-T | HS-2246-TB | B | PUSH BUTTON | WATER HEATER ON PUSHBUTTON | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B |  |  |  | DI | LCP-B | UCP-B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
224 | HS-2246-P | HS-2246-PB | B | PUSH BUTTON | WATER HEATER OFF PUSHBUTTON | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B |  |  |  | DI | LCP-B | UCP-B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
225 | HS-2247-T | HS-2247-TB | B | PUSH BUTTON | WATER COOLER MOTOR START PUSHBUTTON | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B |  |  |  | DI | LCP-B | UCP-B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
226 | HS-2247-P | HS-2247-PB | B | PUSH BUTTON | WATER COOLER MOTOR STOP PUSHBUTTON | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B |  |  |  | DI | LCP-B | UCP-B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
227 | HS-2248-T | HS-2248-TB | B | PUSH BUTTON | BEARING MOTOR START PUSHBUTTON | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B |  |  |  | DI | LCP-B | UCP-B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
228 | HS-2248-P | HS-2248-PB | B | PUSH BUTTON | BEARING MOTOR STOP PUSHBUTTON | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B |  |  |  | DI | LCP-B | UCP-B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
229 | HS-2250 | HS-2250B | B | PUSH BUTTON | RESET PUSH BUTTON | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B |  |  |  | DI | LCP-B | UCP-B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
230 | HS-2238-U | HS-2238-UB | B | SELECTOR SWITCH | OIL COOLER AUTO SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B | - | - | - | DI | LCP-B | UCP-B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
231 | HS-2240 | HS-2240B | B | EMERGENCY SHUT DOWN | RESET PUSH BUTTON | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B |  |  |  | DI | LCP-B | UCP-B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
232 | XL-2230 | XL-2230B | B | SIGNAL LAMP | OIL HEATER ACTIVE LAMP | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B | - | - | - | DO | UCP-B | LCP-B | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T3
233 | XL-2231 | XL-2231B | B | SIGNAL LAMP | AUX LUBE OILPUMP MOTOR START LAMP | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B | - | - | - | DO | UCP-B | LCP-B | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T3
234 | XL-2184 | XL-2184B | B | SIGNAL LAMP | COMMON ALARM LAMP | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B | - | - | - | DO | UCP-B | LCP-B | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T3
235 | XL-2185 | XL-2185B | B | SIGNAL LAMP | COMMON SHUTDOWN LAMP | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B | - | - | - | DO | UCP-B | LCP-B | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T3
236 | XL-2232 | XL-2232B | B | SIGNAL LAMP | LUBRICATOR OIL HEATER ON LAMP | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B | - | - | - | DO | UCP-B | LCP-B | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T3
237 | XL-2233 | XL-2233B | B | SIGNAL LAMP | LUBRICATOR OIL MOTOR START LAMP | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B | - | - | - | DO | UCP-B | LCP-B | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T3
238 | XL-2234 | XL-2234B | B | SIGNAL LAMP | MAIN MOTOR RUNNING LAMP | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B | - | - | - | DO | UCP-B | LCP-B | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T3
239 | XL-2235 | XL-2235B | B | SIGNAL LAMP | OIL COOLER MOTOR A RUNNING LAMP | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B | - | - | - | DO | UCP-B | LCP-B | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T3
240 | XL-2236 | XL-2236B | B | SIGNAL LAMP | OIL COOLER MOTOR B RUNNING LAMP | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B |  |  |  | DO | UCP-B | LCP-B | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T3
241 | XL-2237 | XL-2237B | B | SIGNAL LAMP | MAIN WATER PUMP MOTOR RUNNING LAMP | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B |  |  |  | DO | UCP-B | LCP-B | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T3
242 | XL-2238 | XL-2238B | B | SIGNAL LAMP | AUX WATER PUMP MOTOR RUNNING LAMP | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B |  |  |  | DO | UCP-B | LCP-B | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T3
243 | XL-2239 | XL-2239B | B | SIGNAL LAMP | WATER HEATER ACTIVE LAMP | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B |  |  |  | DO | UCP-B | LCP-B | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T3
244 | XL-2240 | XL-2240B | B | SIGNAL LAMP | WATER COOLER RUNNING LAMP | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B |  |  |  | DO | UCP-B | LCP-B | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T3
245 | XL-2241 | XL-2241B | B | SIGNAL LAMP | BEARRING MOTOR RUNNING LAMP | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B |  |  |  | DO | UCP-B | LCP-B | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T3
246 | XL-2242 | XL-2242B | B | SIGNAL LAMP | READY TO START LAMP | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B |  |  |  | DO | UCP-B | LCP-B | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T3
247 | XL-2243 | XL-2243B | B | SIGNAL LAMP | COMMON ALARM LAMP | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B |  |  |  | DO | UCP-B | LCP-B | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T3
248 | XL-2244 | XL-2244B | B | SIGNAL LAMP | COMMON SHUT DOWN LAMP | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B |  |  |  | DO | UCP-B | LCP-B | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T3
249
250 | VT-2202 | VT-2202B | B | VIBRATION TRANSMITTER | FRAME VIBRATION | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | AI | FIELD | Trip Relay UCP B | 24VDC | - | 4-20mA | IS |  | HOLD | HOLD |  |  |  |  | ZONE2, IIB, T3
251 | VE--2202 | VE--2202B | B | VIBRATION ELEMENT |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | - | FIELD | -
252 | VI--2202 | VI--2202B | B | VIBRATION INDICATING |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | - | UCP-B | CCR
253 | VAH-2202 | VAH-2202B | B | VIBRATION ALARM HIGH |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | - | UCP-B | CCR
254 | VAHH-2202 | VAHH-2202B | B | VIBRATION ALARM HIGH HIGH |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | AI | UCP-B | CCR
255
256 | VT--2200 | VT--2200B | B | VIBRATION TRANSMITTER | FRAME VIBRATION | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | AI | FIELD | Trip Relay UCP B | 24VDC | - | 4-20mA | IS |  | HOLD | HOLD |  |  |  |  | ZONE2, IIB, T3
257 | VE--2200 | VE--2200B | B | VIBRATION ELEMENT |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | - | FIELD | -
258 | VI--2200 | VI--2200B | B | VIBRATION INDICATING |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | - | UCP-B | CCR
259 | VAH-2200 | VAH-2200B | B | VIBRATION ALARM HIGH |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | - | UCP-B | CCR
260 | VAHH-2200 | VAHH-2200B | B | VIBRATION ALARM HIGH HIGH |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | AI | UCP-B | CCR
261
262 | VT-2201 | VT-2201B | B | VIBRATION TRANSMITTER | FRAME VIBRATION | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | AI | FIELD | Trip Relay UCP B | 24VDC | - | 4-20mA | IS |  | HOLD | HOLD |  |  |  |  | ZONE2, IIB, T3
263 | VE-2201 | VE-2201B | B | VIBRATION ELEMENT |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | - | FIELD | -
264 | VI-2201 | VI-2201B | B | VIBRATION INDICATING |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | - | UCP-B | CCR
265 | VAH-2201 | VAH-2201B | B | VIBRATION ALARM HIGH |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | - | UCP-B | CCR
266 | VAHH-2201 | VAHH-2201B | B | VIBRATION ALARM HIGH HIGH |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | AI | UCP-B | CCR
267
268 | TE-2214 | TE-2214B | B | RTD THERMO ELEMENT | Comp. Frame Temp. Measurment | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  |  | FIELD |  |  | - | RTD |  |  | HOLD | [5 empty] | ZONE2, IIB, T3
269 | TT-2214 | TT-2214B | B | TEMPERATURE TRAMSMITTER |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | AI | FIELD | UCP-B | 24VDC |  | 4-20mA Hart | IS |  | HOLD
270 | TI-2214 | TI-2214B | B | TEMPERATURE INDICATION |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | - | UCP-B | CCR
271 | TAH-2214 | TAH-2214B | B | TEMPERATURE ALARM HIGH |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | - | UCP-B | CCR
272 |  |  | B
273 | TE-2215 | TE-2215B | B | RTD THERMO ELEMENT | Comp. Frame Temp. Measurment | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  |  | FIELD |  |  | - | RTD |  |  | HOLD | [5 empty] | ZONE2, IIB, T3
274 | TT-2215 | TT-2215B | B | TEMPERATURE TRAMSMITTER |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | AI | FIELD | UCP-B | 24VDC |  | 4-20mA Hart | IS
275 | TI-2215 | TI-2215B | B | TEMPERATURE INDICATION |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | - | UCP-B | CCR
276 | TAH-2215 | TAH-2215B | B | TEMPERATURE ALARM HIGH |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | - | UCP-B | CCR
277
278 | TE-2216 | TE-2216B | B | RTD THERMO ELEMENT | Comp. Frame Temp. Measurment | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  |  | FIELD |  |  | - | RTD |  |  | HOLD | [5 empty] | ZONE2, IIB, T3
279 | TT-2216 | TT-2216B | B | TEMPERATURE TRANSMITTER |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | AI | FIELD | Trip Relay UCP B | 24VDC | - | 4-20mA Hart | IS |  | HOLD | HOLD |  |  |  |  | ZONE2, IIB, T3
280 | TI-2216 | TI-2216B | B | RTD THERMO ELEMENT |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  |  | UCP-B | CCR
281 | TAH-2216 | TAH-2216B | B | TEMPERATURE ALARM HIGH |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | - | UCP-B | CCR
282 | TAHH-2216 | TAHH-2216B | B | TEMPERATURE ALARM HIGH HIGH |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  |  | UCP-B | CCR
283
284 | TE-2217 | TE-2217B | B | RTD THERMO ELEMENT | Comp. Power Bearing Temp. Measurment | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  |  | FIELD |  |  | - | RTD |  |  | HOLD | [5 empty] | ZONE2, IIB, T3
285 | TT-2217 | TT-2217B | B | TEMPERATURET RAMSMITTER |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | AI | UCP-B | Trip Relay UCP B | 24VDC |  | 4-20mA Hart | IS
286 | TI-2217 | TI-2217B | B | RTD THERMO ELEMENT |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  |  | UCP-B | CCR
287 | TAH-2217 | TAH-2217B | B | TEMPERATURE ALARM HIGH |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | - | UCP-B | CCR
288 | TAHH-2217 | TAHH-2217B | B | TEMPERATURE ALARM HIGH HIGH |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | - | UCP-B | CCR
289
290 | TE-2218 | TE-2218B | B | RTD THERMO ELEMENT | Comp. Power Bearing Temp. Measurment | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  |  | FIELD |  |  | - | RTD |  |  | HOLD | [5 empty] | ZONE2, IIB, T3
291 | TT-2218 | TT-2218B | B | TEMPERATURE TRANSMITTER |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | AI | FIELD | Trip Relay UCP B | 24VDC | - | 4-20mA Hart | IS |  | HOLD | HOLD |  |  |  |  | ZONE2, IIB, T3
292 | TI-2218 | TI-2218B | B | RTD THERMO ELEMENT |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | - | UCP-B | CCR
293 | TAH-2218 | TAH-2218B | B | TEMPERATURE ALARM HIGH |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | - | UCP-B | CCR
294 | TAHH-2218 | TAHH-2218B | B | TEMPERATURE ALARM HIGH HIGH |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | - | UCP-B | CCR
295
296 | TE-2219 | TE-2219B | B | RTD THERMO ELEMENT | Comp. Power Bearing Temp. Measurment | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  |  | FIELD |  |  | - | RTD |  |  | HOLD | [5 empty] | ZONE2, IIB, T3
297 | TT-2219 | TT-2219B | B | TEMPERATURE TRANSMITTER |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | AI | FIELD | Trip Relay UCP B | 24VDC | - | 4-20mA Hart | IS |  | HOLD | HOLD |  |  |  |  | ZONE2, IIB, T3
298 | TI-2219 | TI-2219B | B | TEMPERATURE TRAMSMITTER |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | - | UCP-B | CCR
299 | TAH-2219 | TAH-2219B | B | TEMPERATURE ALARM HIGH |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | - | UCP-B | CCR
300 | TAHH-2219 | TAHH-2219B | B | TEMPERATURE ALARM HIGH HIGH |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | - | UCP-B | CCR
301
302 | ZT-2201 | ZT-2201B | B | ROD DROP TRANSMITTER | Cylinder Rod Drop Detector | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | AI | FIELD | UCP-B | 24VDC | - | 4-20mA | IS |  | HOLD | HOLD |  |  |  |  | ZONE2, IIB, T3
303 | ZE-2201 | ZE-2201B | B | ROD DROP ELEMENT |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  |  | FIELD
304 | ZI-2201 | ZI-2201B | B | ROD DROP INDICATOR |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  |  | UCP-B | CCR
305 | ZAH-2201 | ZAH-2201B | B | ROD DROP ALARM HIGH |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | - | UCP-B | CCR
306
307 | ZT-2200 | ZT-2200B | B | ROD DROP TRANSMITTER | LEFT Cylinder Rod Drop Detector | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | AI | FIELD | UCP-B | 24VDC | - | 4-20mA | IS |  | HOLD | HOLD |  |  |  |  | ZONE2, IIB, T3
308 | ZE-2200 | ZE-2200B | B | ROD DROP ELEMENT |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  |  | FIELD
309 | ZI-2200 | ZI-2200B | B | ROD DROP INDICATOR |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  |  | UCP-B | CCR
310 | ZAH-2200 | ZAH-2200B | B | ROD DROP ALARM HIGH |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | - | UCP-B | CCR
311
312 | TE-2222 | TE-2222B | B | RTD THERMO ELEMENT | MAIN MOTOR R-PHASE WINDING TEMP. | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | AI | Motor | MCC | 24VDC | - | RTD | NIS |  | 1-100 | °C |  |  |  |  | ZONE2, IIB, T3
314 | TE-2228 | XL-2222B | B | RTD R TRIP FEEDBACK | MAIN MOTOR R-PHASE WINDING TEMPTRIP FEEDBACK. | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | DI | MCC | UCP-B | 24VDC | - | N.O | NIS
314
315 | TE-2225 | TE-2225B | B | RTD THERMO ELEMENT | MAIN MOTOR S-PHASE WINDING TEMP. | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | AI | Motor | MCC | 24VDC | - | RTD | NIS |  | 0-100 | °C |  |  |  |  | ZONE2, IIB, T3
314 | TE-2228 | XL-2225B | B | RTD S TRIP FEEDBACK | MAIN MOTOR S-PHASE WINDING TEMPTRIP FEEDBACK. | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | DI | MCC | UCP-B | 24VDC | - | N.O | NIS
317
318 | TE-2228 | TE-2228B | B | RTD THERMO ELEMENT | MAIN MOTOR T-PHASE WINDING TEMP. | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | AI | Motor | MCC | 24VDC | - | RTD | NIS |  | 0-100 | °C |  |  |  |  | ZONE2, IIB, T3
314 | TE-2228 | XL-2228B | B | RTD T TRIP FEEDBACK | MAIN MOTOR T-PHASE WINDING TEMPTRIP FEEDBACK. | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | DI | MCC | UCP-B | 24VDC | - | N.O | NIS
320
321 | HST-2205 | HST-2205 B | B | START COMMAND | LOOB OIL COOLER (AE-2101-OC A/B/C) | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | DOR | UCP-B | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
322 | HSP-2205 | HSP-2205 B | B | STOP COMMAND |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | DOR | UCP-B | MCC | 24VDC | D | NC | NIS | [7 empty] | ZONE2, IIB, T3
323 | XL-2205 | XL-2205 B | B | RUNNING STATUS |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | DI | MCC | UCP-B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
324 | XA-2205 | XA-2205 B | B | FAILURE STATUS |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | DI | MCC | UCP-B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
325 |  |  | B
326 | HST-2225 | HST-2225 B | B | START COMMAND | MOTOR BEARING DEVICE MOTOR | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B | - | - | - | DOR | UCP-B | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
327 | HSP-2225 | HSP-2225 B | B | STOP COMMAND |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B | - | - | - | DOR | UCP-B | MCC | 24VDC | D | NC | NIS | [7 empty] | ZONE2, IIB, T3
328 | XL-2225 | XL-2225 B | B | RUNNING STATUS |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B | - | - | - | DI | MCC | UCP-B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
329 | XA-2225 | XA-2225 B | B | FAULT STATUS |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B | - | - | - | DI | MCC | UCP-B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
330 |  |  | B
331 | HST-2224 | HST-2224 B | B | START COMMAND | MAKE UP GAS COMPRESSOR MAIN MOTOR | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B | - | - | - | DOR | UCP-B | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
332 | HSP-2224 | HSP-2224 B | B | STOP COMMAND |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B | - | - | - | DOR | UCP-B | MCC | 24VDC | D | NC | NIS | [7 empty] | ZONE2, IIB, T3
333 | XL-2224 | XL-2224 B | B | RUNNING STATUS |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B | - | - | - | DI | MCC | UCP-B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
334 | XA-2224 | XA-2224 B | B | FAULT STATUS |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B | - | - | - | DI | MCC | UCP-B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
335 |  |  | B
336 | PCV-2123 | PCV-2123B | B | CONTROL VALVE | SPILL BACK VALVE | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  | - | UCP-B | FIELD |  | - |  |  | FO
337 | PCY-2123 | PCY-2123 B | B | CONTROLLER |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  | AOR | UCP-B | FIELD |  |  | 4-20mA | IS
339 | PCVY-2123 | PCYZ-2123B | B | Feed back |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  | AI | UCP-A | FIELD |  |  | 4-20mA | IS
338 | CZSO-2123 | CZSO-2123 B | B | LIMIT SWITCH |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  | DI | FIELD | UCP-B | 24VDC |  |  | NIS
339 | CZSC-2123 | CZSC-2123 B | B | LIMIT SWITCH |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  | DI | FIELD | UCP-B | 24VDC |  |  | NIS
340 | PY-2123 | PY-2123 B | B | SOLENOID VALVE |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  | DOR | UCP-B | FIELD | 24VDC |  |  | NIS
341
345 | XV-2121 | XV-2121B | B | INPUT ON OFF VALVE | INPUT ON OFF VALVE(CLINET SIDE) | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  | - | FIELD
346 | PSOV-2121 | PSOV-2121B | B | ON OFF VALVE SOLENOID |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  | DOR | UCP-B | FIELD | 24VDC | W | 24VDC | NIS | FO | [9 empty] | Valve is in client scope of supply
347 | XZIC-2121 | XZIC-2121B | B | LIMIT SWITCH |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  | DI | FIELD | UCP-B | 24VDC | W | 24VDC | NIS
348 | XZIO-2121 | XZIO-2121B | B | LIMIT SWITCH |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  | DI | FIELD | UCP-B | 24VDC | W | 24VDC | NIS
349
350 | XV-2133 | XV-2133B | B | OUTPUT OFF VALVE | OUTPUT OFF VALVE(CLINET SIDE) | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  | - | FIELD | [15 empty] | Valve is in client scope of supply
351 | PSOV-2233 | PSOV-2233B | B | ON OFF VALVE SOLENOID |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  | DOR | UCP-A | FIELD | 24VDC | W | 24VDC | NIS | FO
352 | XZIC-2133 | XZIC-2133B | B | LIMIT SWITCH |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  | DI | FIELD | UCP-B | 24VDC | W | 24VDC | NIS
353 | XZIO-2133 | XZIO-2133B | B | LIMIT SWITCH |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  | DI | FIELD | UCP-B | 24VDC | W | 24VDC | NIS
342 | XV-2121 | XV-2121B | B | ON OFF VALVE | INPUT ON OFF VALVE(CLINET SIDE) | PACKAGE COMPRESSOR C-2101 B | BK-GCS-PEDCO-120-PR-PI-0006-SHEET 1B |  |  |  |  | FIELD
343 | PSOV-2121 | PSOV-2121B | B | ON OFF VALVE SOLENOID |  | PACKAGE COMPRESSOR C-2101 B | BK-GCS-PEDCO-120-PR-PI-0006-SHEET 1B |  |  |  | DOR | UCP-B | FIELD | 24VDC | W | 24VDC | NIS | FO
344 | XZIC-2121 | XZIC-2121B | B | LIMIT SWITCH |  | PACKAGE COMPRESSOR C-2101 B | BK-GCS-PEDCO-120-PR-PI-0006-SHEET 1B |  |  |  | DI | FIELD | UCP-B | 24VDC | W | 24VDC | NIS
345 | XZIO-2121 | XZIO-2121B | B | LIMIT SWITCH |  | PACKAGE COMPRESSOR C-2101 B | BK-GCS-PEDCO-120-PR-PI-0006-SHEET 1B |  |  |  | DI | FIELD | UCP-B | 24VDC | W | 24VDC | NIS
346
347 | XV-2133 | XV-2133B | B | ON OFF VALVE | OUTPUT OFF VALVE(CLINET SIDE) | PACKAGE COMPRESSOR C-2101 B | BK-GCS-PEDCO-120-PR-PI-0011-SHEET 1B |  |  |  |  | FIELD
348 | PSOV-2233 | PSOV-2233B | B | ON OFF VALVE SOLENOID |  | PACKAGE COMPRESSOR C-2101 B | BK-GCS-PEDCO-120-PR-PI-0011-SHEET 1B |  |  |  | DOR | UCP-B | FIELD | 24VDC | W | 24VDC | NIS | FO
349 | XZIC-2133 | XZIC-2133B | B | LIMIT SWITCH |  | PACKAGE COMPRESSOR C-2101 B | BK-GCS-PEDCO-120-PR-PI-0011-SHEET 1B |  |  |  | DI | FIELD | UCP-B | 24VDC | W | 24VDC | NIS
350 | XZIO-2133 | XZIO-2133B | B | LIMIT SWITCH |  | PACKAGE COMPRESSOR C-2101 B | BK-GCS-PEDCO-120-PR-PI-0011-SHEET 1B |  |  |  | DI | FIELD | UCP-B | 24VDC | W | 24VDC | NIS
Note on B108: Forouzandeh Fatemeh: ALARM L,H چک شود

## LIST-C
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض
خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03)
I/O LIST
شماره پیمان: | [5 empty] | پروژه | بسته کاری | صادرکننده |  |  | تسهیلات |  | رشته | نوع مدرک |  | سریال | نسخه |  | از |  |  |  |  | شماره صفحه:
9184 – 073 - 053 | [5 empty] | BK | GCS | HY |  |  | 120 |  | IN | LI |  | 0005 | V01
Item No. |  |  |  | Description | Service 1 | Service 2 | P&ID No. | line Size | Connection |  | I/O Type |  | Location, Signal (To) | Power Supply | W/D | Signal Type | IS/NIS | Valve Action | Range/ Alarm Set point | Eng. Units | Engineering Documents |  |  |  | Hazardous Area | Manufacturer | Model Number | Remark
|  | Tag Number | Unit Number | [5 empty] | Size | Rating |  | Location, Signal ( From) | [8 empty] | Loop Diagram No. | Inst. Location Layout | Hook-Up Drawing | Data Sheet
1 | SV-2201 | SV-2201C | C | SOLENOID VALVE | INST. AIR SUPPLY | PACKAGE COMPRESSOR C-2101,2 C | BK-GCS-HY-120-PR-PI-0001-SHEET 2C |  |  |  | DOR | UCP-C | FIELD | 24VDC | W | 24VDC | NIS | [7 empty] | ZONE2, IIB, T3
2 | SV-2202 | SV-2202C | C | SOLENOID VALVE | INST. AIR SUPPLY | PACKAGE COMPRESSOR C-2101,2 C | BK-GCS-HY-120-PR-PI-0001-SHEET 2C |  |  |  | DOR | UCP-C | FIELD | 24VDC | W | 24VDC | NIS | [7 empty] | ZONE2, IIB, T3
3 | SV-2203 | SV-2203C | C | SOLENOID VALVE | INST. AIR SUPPLY | PACKAGE COMPRESSOR C-2101,2 C | BK-GCS-HY-120-PR-PI-0001-SHEET 2C |  |  |  | DOR | UCP-C | FIELD | 24VDC | W | 24VDC | NIS | [7 empty] | ZONE2, IIB, T3
4
5 | PT-2123 | PT-2123C | C | PRESSURE TRANSMITTER | ON SUCTION SNUBBER 1S STAGE | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C | 8" |  |  | AI | FIELD | UCP-C | 4-20mA Hart | - | 4-20mA | IS |  | 0-16 | BARG |  |  |  |  | ZONE2, IIB, T3
6 | PI-2123 | PI-2123C | C | PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C |  |  |  | - | UCP-C | CCR
7 | PAH-2123 | PAH-2123C | C | PRESSURE ALARM HIGH |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C |  |  |  | - | UCP-C | CCR
8
9 | FT-2121 | FT-2121C | C | FLOW TRANSMITTER | ON SUCTION SNUBBER 1S STAGE | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C | 8" |  |  | AI | FIELD | UCP-C | 4-20mA Hart | - | 4-20mA | IS |  | 0-14000 | NM3/H |  |  |  |  | ZONE2, IIB, T3
10 | FE-2121 | FE-2121 C | C | FLOW ELEMENT |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C |  |  |  | - | FIELD | -
11 | FI-2121 | FI-2121 C | C | FLOW INDICATING |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C |  |  |  | - | UCP-C | CCR
12
13 | TT-2122 | TT-2122 C | C | TEMPERATURE TRANSMITTER | ON SUCTION SNUBBER 1S STAGE | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C | 8" |  |  | AI | FIELD | UCP-C | 4-20mA Hart | - | 4-20mA | IS |  | 0-100 | °C |  |  |  |  | ZONE2, IIB, T3
14 | TI-2122 | TI-2122 C | C | TEMPERATURE INDICATING |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C |  |  |  | - | UCP-C | CCR
15 | TE-2122 | TE-2122C | C | THERMO ELEMENT |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C |  |  |  | -
16 | TW-2122 | TW-2122 C | C | THERMOWELL |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C |  |  |  | -
17
18 | PDT-2122 | PDT-2122 C | C | DIFF. PRESSURE TRANSMITTER | STRAINER FILTER | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C | 1" |  |  | AI | FIELD | UCP-C | 4-20mA Hart | - | 4-20mA | IS |  | 0-1 | BARG |  |  |  |  | ZONE2, IIB, T3
19 | PDI-2122 | PDI-2122 C | C | DIFF. PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C |  |  |  | - | UCP-C | CCR
20 | PDAH-2122 | PDAH-2122 C | C | DIFF. PRESSURE ALARM HIGH |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C |  |  |  | - | UCP-C | CCR
21
22 | PT-2192 A/B | PT-2192 A/BC | C | PRESSURE TRANSMITTER | ON DISCHARGE SNUBBER 1ST STAGE | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C | 6" |  |  | AI | FIELD | UCP-C | 4-20mA Hart | - | 4-20mA | IS |  | 0-40 | BARG |  |  |  |  | ZONE2, IIB, T3
23 | PI-2192 A/B | PI-2192 A/BC | C | PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C |  |  |  | - | UCP-C | CCR
24 | PAH-2192 A/B | PAH-2192 A/BC | C | PRESSURE ALARM HIGH |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C |  |  |  | - | UCP-C | CCR
25
26 | TT-2192 | TT-2192 C | C | TEMPERATURE TRANSMITTER | ON DISCHARGE SNUBBER 1ST STAGE | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C | 6" |  |  | AI | FIELD | UCP-C | 4-20mA Hart | - | 4-20mA | IS |  | 0-200 | °C |  |  |  |  | ZONE2, IIB, T3
27 | TE-2191 | TE-2191 C | C | THERMO ELEMENT |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C |  |  |  |  | FIELD | -
28 | TW-2191 | TW-2191 C | C | THERMOWELL |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C |  |  |  |  | FIELD | -
29 | TI-2192 | TI-2192 C | C | TEMPERATURE INDICATING |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C |  |  |  | - | UCP-C | CCR
30
31 | TT-2191 | TT-2191 C | C | TEMPERATURE TRANSMITTER | ON DISCHARGE SNUBBER 1ST STAGE | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C |  |  |  | AI | FIELD | UCP-C | 4-20mA Hart | - | 4-20mA | IS |  | 0-200 | °C |  |  |  |  | ZONE2, IIB, T3
32 | TI-2191 | TI-2191C | C | TEMPERATURE INDICATING |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C |  |  |  | - | UCP-C | CCR
33 | TAH-2191 | TAH-2191C | C | TEMPERATURE ALARM HIGH |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C |  |  |  | - | UCP-C | CCR
34
35 | TS-2191 | TS-2191C | C | TEMPERATURE SWITCH | ON DISCHARGE SNUBBER 1ST STAGE | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C |  |  |  | DI | FIELD | USD | NC |  | NC | NIS |  | 0-200/160 | °C
36 | TAHH-2191 | TAHH-2191C | C | TEMPERATURE ALARM HIGH HIGH |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C | - | - | - |  | FIELD | UCP-C
37
38 | TT-2194 | TT-2194 C | C | TEMPERATURE TRANSMITTER | ON DISCHARGE SNUBBER 2ND STAGE | PACKAGE COMPRESSOR C-2102 C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C |  |  |  | AI | FIELD | CCR | 4-20mA Hart | - | 4-20mA | IS |  | 0-200 | °C |  |  |  |  | ZONE2, IIB, T3
39 | TE-2194 | TE-2194 C | C | THERMO ELEMENT |  | PACKAGE COMPRESSOR C-2102 C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C |  |  |  |  | FIELD | -
40 | TW-2194 | TW-2194 C | C | THERMOWELL |  | PACKAGE COMPRESSOR C-2102 C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C |  |  |  |  | FIELD | -
41 | TI-2194 | TI-2194 C | C | TEMPERATURE INDICATING |  | PACKAGE COMPRESSOR C-2102 C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C |  |  |  | - | UCP-C | CCR
42 | TAH-2194 | TAH-2194 C | C | TEMPERATURE ALARM HIGH |  | PACKAGE COMPRESSOR C-2102 C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C |  |  |  | - | UCP-C | CCR
43
44 | TS-2194 | TS-2194 C | C | TEMPERATURE SWITCH | ON DISCHARGE SNUBBER 2ND STAGE | PACKAGE COMPRESSOR C-2102 C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C |  |  |  | DI | FIELD | Trip Relay UCP C |  |  |  | NIS
45 | TAHH-2194 | TAHH-2194 C | C | TEMPERATURE ALARAM HIGH HIGH |  | PACKAGE COMPRESSOR C-2102 C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C |  |  |  | - | FIELD | UCP
46
47 | PT-2124 | PT-2124 C | C | PRESSURE TRANSMITTER | ON DISCHARGE LINE SNUBBER 2ND STAGE | PACKAGE COMPRESSOR C-2102 C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C | 6" |  |  | AI | FIELD | UCP-C | 4-20mA Hart | - | 4-20mA | IS |  | 0-80 | BARG |  |  |  |  | ZONE2, IIB, T3
48 | PI-2124 | PI-2124 C | C | PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2102 C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C |  |  |  | - | UCP-C | CCR
49 | PAHH-2124 | PAHH-2124 C | C | PRESSURE ALARM HIGH HIGH |  | PACKAGE COMPRESSOR C-2102 C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C |  |  |  | - | UCP-C | CCR
50
51 | PS-2195 | PS-2195 C | C | PRESSURE SWITCH | ON DISCHARGE LINE SNUBBER 2ND STAGE | PACKAGE COMPRESSOR C-2102 C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C | 6" |  |  | DI | FIELD | Trip Relay UCP C |  |  |  | NIS
52 | PAHH-2195 | PAHH-2195 C | C | PRESSURE Trip HIGH HIGH |  | PACKAGE COMPRESSOR C-2102 C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C |  |  |  | - | FIELD | UCP-C
53
54 | TT-2123 | TT-2123 C | C | TEMPERATURE TRANSMITTER | ON DISCHARGE LINE SNUBBER 2ND STAGE | PACKAGE COMPRESSOR C-2102 C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C | 6" |  |  | AI | FIELD | UCP-C | 4-20mA Hart | - | 4-20mA | IS |  | 0-200 | °C |  |  |  |  | ZONE2, IIB, T3
55 | TE-2123 | TE-2123 C | C | THERMO ELEMENT |  | PACKAGE COMPRESSOR C-2102 C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C |  |  |  |  | - | FIELD
56 | TW2123 | TW2123 C | C | THERMOWELL |  | PACKAGE COMPRESSOR C-2102 C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C |  |  |  |  | - | FIELD
57 | TI-2123 | TI-2123 C | C | TEMPERATURE INDICATING |  | PACKAGE COMPRESSOR C-2102 C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C |  |  |  | - | UCP-C | CCR
58
59 | PT-2197 | PT-2197C | C | PRESSURE TRANSMITTER | ON SUCTION SNUBBER 2ND STAGE | PACKAGE COMPRESSOR C-2102 C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C | 6" |  |  | AI | FIELD | UCP-C | 4-20mA Hart | - | 4-20mA | IS |  | 0-40 | BARG |  |  |  |  | ZONE2, IIB, T3
60 | PI-2197 | PI-2197 C | C | PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2102 C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C |  |  |  | - | UCP-C | CCR
61
62 | FT-2197 | FT-2197C | C | FLOW TRANSMITTER | ON SUCTION SNUBBER 2ND STAGE | PACKAGE COMPRESSOR C-2102 C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C | 6" |  |  | AI | FIELD | UCP-C | 4-20mA Hart | - | 4-20mA | IS |  | 0-14000 | NM3/H |  |  |  |  | ZONE2, IIB, T3
63 | FE-2197 | FE-2197C | C | FLOW ELEMENT |  | PACKAGE COMPRESSOR C-2102 C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C |  |  |  | - | FIELD | -
64 | FI-2197 | FI-2197C | C | FLOW INDICATING |  | PACKAGE COMPRESSOR C-2102 C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C |  |  |  | - | UCP-C | CCR
65
66 | TT-2197 | TT-2197C | C | TEMPERATURE TRANSMITTER | ON SUCTION SNUBBER 2ND STAGE | PACKAGE COMPRESSOR C-2102 C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C | 6" |  |  | AI | FIELD | UCP-C | 4-20mA Hart | - | 4-20mA | IS |  | 0-100 | °C |  |  |  |  | ZONE2, IIB, T3
67 | TE-2197 | TE-2197C | C | THERMO ELEMENT |  | PACKAGE COMPRESSOR C-2102 C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C |  |  |  | - | - | FIELD
68 | TW-2197 | TW-2197C | C | THERMOWELL |  | PACKAGE COMPRESSOR C-2102 C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C |  |  |  |  | - | FIELD
69 | TI-2197 | TI-2197C | C | TEMPERATURE INDICATING |  | PACKAGE COMPRESSOR C-2102 C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C |  |  |  |  | UCP-C | CCR
70
71 | PDT-2197 | PDT-2197C | C | DIFF. PRESSURE TRANSMITTER | STRAINER FILTER 2ND STAGE | PACKAGE COMPRESSOR C-2102 C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C | 1" |  |  | AI | FIELD | UCP-C | 4-20mA Hart | - | 4-20mA | IS |  | 0-6 | BARG |  |  |  |  | ZONE2, IIB, T3
72 | PDI-2197 | PDI-2197C | C | DIFF. PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2102 C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C |  |  |  | - | UCP-C | CCR
73 | PDAH-2197 | PDAH-2197C | C | DIFF. PRESSURE ALARM HIGH |  | PACKAGE COMPRESSOR C-2102 C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C |  |  |  | - | UCP-C | CCR
74
75 | PT-2201 | PT-2201C | C | PRESSURE TRANSMITTER | ON INSTRUMENT LINE | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 2C | 2" |  |  | AI | FIELD | UCP-C | 4-20mA Hart | - | 4-20mA | IS |  | HOLD | HOLD |  |  |  |  | ZONE2, IIB, T3
76 | PI-2201 | PI-2201C | C | PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 2C |  |  |  | - | UCP-C | CCR
77 | PAL-2201 | PAL-2201C | C | PRESSURE ALARM LOW |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 2C |  |  |  | - | UCP-C | CCR
78
79 | PT-2200 | PT-2200 C | C | PRESSURE TRANSMITTER | ON LUBRICATOR | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | AI | FIELD | UCP-C | 4-20mA Hart | - | 4-20mA | IS |  | HOLD | HOLD |  |  |  |  | ZONE2, IIB, T3
80 | PI-2200 | PI-2200 C | C | PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | - | UCP-C | CCR
81 | PAL-2200 | PAL-2200 C | C | PRESSURE ALARM LOW |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | - | UCP-C | CCR
82
83 | LT-2200 | LT-2200 C | C | LEVEL TRANSMITTER | ON CRANK CASE | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | AI | FIELD | UCP-C | 4-20mA Hart | - | 4-20mA | IS |  | HOLD | HOLD |  |  |  |  | ZONE2, IIB, T3
84 | LI-2200 | LI-2200 C | C | LEVEL INDICATING |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | - | UCP-C | CCR
85 | LAL-2200 | LAL-2200 C | C | LEVEL ALARM LOW |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | - | UCP-C | CCR
86
87 | LT-2213 | LT-2213 C | C | LEVEL TRANSMITTER | WATER RESERVOIR | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | AI | FIELD | Trip Relay UCP C | 4-20mA Hart | - | 4-20mA | IS |  | HOLD | HOLD |  |  |  |  | ZONE2, IIB, T3
88 | LI-2213 | LI-2213 C | C | LEVEL INDICATING |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | - | UCP-C | CCR
89 | LAL-2213 | LAL-2213 C | C | LEVEL ALARM LOW |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | - | UCP-C | CCR
90 | LALL-2213 | LALL-2213 C | C | LEVEL ALARM LOW LOW |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | - | UCP-C | CCR
91
92 | TT-2203 | TT-2203 C | C | TEMPERATURE TRANSMITTER | ON CRANK CASE | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | AIR | FIELD | UCP-C | 4-20mA Hart | - | 4-20mA | IS |  | 0-200 | °C |  |  |  |  | ZONE2, IIB, T3
93 | TE-2203 | TE-2203 C | C | THERMO ELEMENT | ON CRANK CASE | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  |  | FIELD | -
94 | TW-2203 | TW-2203 C | C | THERMOWELL |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  |  | FIELD | -
95 | TI-2203 | TI-2203 C | C | THERMO ELEMENT |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  |  | UCP-C | CCR
96
97 | HSP-2203 | HSP-2203 C | C | START COMMAND HEATER CRANK CASE | START COMMAND HEATER CRANK CASE | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | DOR | UCP-C | MCC | NO | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
98 | HST-2203 | HST-2203 C | C | STOP COMMAND HEATER CRANK CASE | STOP COMMAND HEATER CRANK CASE | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | DOR | UCP-C | MCC | NO | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
99 | XL-2203 | XL-2203 C | C | RUNNING STATUS HEATER CRANK CASE | RUNNING STATUS HEATER CRANK CASE | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | DI | MCC | UCP-C | NO | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
100 | XA-2203 | XA-2203 C | C | FAILURE STATUS HEATER CRANK CASE | FAILURE STATUS HEATER CRANK CASE | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | DI | MCC | UCP-C | NO | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
101
102 | HST-2200 | HST-2200 C | C | START COMMAND HEATER LUBRICATOR | HEATER ON LUBRICATOR | PACKAGE COMPRESSOR C-1401 C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | DOR | UCP-C | MCC | NO | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
103 | HSP-2200 | HSP-2200 C | C | STOP COMMAND HEATER LUBRICATOR | HEATER ON LUBRICATOR | PACKAGE COMPRESSOR C-1401 C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | DOR | UCP-C | MCC | NO | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
104 | XL-2200 | XL-2200 C | C | RUNNING STATUS HEATER LUBRICATOR | HEATER ON LUBRICATOR | PACKAGE COMPRESSOR C-1401 C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | DI | MCC | UCP-C | NO | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
105 | XA-2200 | XA-2200 C | C | FAILURE STATUS HEATER LUBRICATOR | HEATER ON LUBRICATOR | PACKAGE COMPRESSOR C-1401 C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | DI | MCC | UCP-C | NO | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
106
107 | TT-2204 | TT-2204C | C | TEMPERATURE TRANSMITTER | LUBE OIL FILTER DOWNSTREAM | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C | 4" |  |  | AI | FIELD | UCP-C | 4-20mA Hart | - | 4-20mA | IS |  | 0-100 | °C |  |  |  |  | ZONE2, IIB, T3
108 | TI-2204 | TI-2204C | C | TEMPERATURE INDICATING |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | - | UCP-C | CCR
109 | TW-2204 | TW-2204C | C | THERMOWELL | LUBE OIL FILTER DOWNSTREAM | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  |  | FIELD | -
110 | TAH-2204 | TAH-2204C | C | TEMPERATURE ALARM HIGH |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | - | UCP-C | CCR
111 | TAL-2204 | TAL-2204C | C | TEMPERATURE ALARM LOW |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | - | UCP-C | CCR
112
113 | PT-2204 | PT-2204C | C | PRESSURE TRANSMITTER | LUBE OIL FILTER DOWNSTREAM | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C | 2" |  |  | AIR | FIELD | UCP-C | 4-20mA Hart | - | 4-20mA | IS |  | 0-16 | BARG |  |  |  |  | ZONE2, IIB, T3
114 | PI-2204 | PI-2204C | C | PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | - | UCP-C | CCR
115 | PAL-2204 | PAL-2204C | C | PRESSURE ALARM LOW |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | - | UCP-C | CCR
116 | PAH-2204 | PAH-2204C | C | PRESSURE ALARM HIGH |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | - | UCP-C | CCR
117 | PAH2-2204 | PAH2-2204C | C | PRESSURE ALARM HIGH2 |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | - | UCP-C | CCR
118
119 | PS-2204 | PS-2204C | C | PRESSURE SWITCH | LUBE OIL FILTER DOWNSTREAM | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | DI | Field | Trip Relay UCP C |  |  |  | NIS |  | 0-16/6 | BARG |  |  |  |  | ZONE2, IIB, T3
120 | PALL-2204 | PALL-2204C | C | PRESSURE ALARM LOW LOW |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | - | Field | UCP-C
121 |  |  | C
122 | PDT-2204 | PDT-2204 C | C | DIFF. PRESSURE TRANSMITTER | LUBE OIL FILTER | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C | 1" |  |  | AIR | FIELD | UCP-C | 4-20mA Hart | - | 4-20mA | IS |  | 0-6 | BARG |  |  |  |  | ZONE2, IIB, T3
123 | PDI-2204 | PDI-2204 C | C | DIFF. PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | - | UCP-C | CCR
124 | PDAH-2204 | PDAH-2204 C | C | DIFF. PRESSURE ALARM HIGH |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | - | UCP-C | CCR
125
126 | HST-2202 | HST-2202 C | C | START COMMAND AUX. OIL PUMP | AUX. OIL PUMP (P-2101-AP C) | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | DOR | UCP-C | MCC | NO | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
127 | HSP-2202 | HSP-2202 C | C | STOP COMMAND AUX. OIL PUMP | AUX. OIL PUMP (P-2101-AP C) | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | DOR | UCP-C | MCC | NC | D | NC | NIS | [7 empty] | ZONE2, IIB, T3
128 | XL-2202 | XL-2202 C | C | RUNNING STATUSAUX. OIL PUMP | AUX. OIL PUMP (P-2101-AP C) | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | DI | MCC | UCP-C | NO | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
129 | XA-2202 | XA-2202 C | C | FAILURE STATUS AUX. OIL PUMP | AUX. OIL PUMP (P-2101-AP C) | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | DI | MCC | UCP-C | NO | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
130
131 | HST-2201 | HST-2201 C | C | START COMMAND LUBRICATOR. OIL PUMP | LUBRICATOR. OIL PUMP (2101-LP C) | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | DOR | UCP-C | MCC | NO | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
132 | HSP-2201 | HSP-2201 C | C | STOP COMMAND LUBRICATOR. OIL PUMP | LUBRICATOR. OIL PUMP (2101-LP C) | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | DOR | UCP-C | MCC | NC | D | NC | NIS | [7 empty] | ZONE2, IIB, T3
133 | XL-2201 | XL-2201 C | C | RUNNING STATUS LUBRICATOR. OIL PUMP | LUBRICATOR. OIL PUMP (2101-LP C) | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | DI | MCC | UCP-C | NO | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
134 | XA-2201 | XA-2201 C | C | FAILURE STATUS LUBRICATOR. OIL PUMP | LUBRICATOR. OIL PUMP (2101-LP C) | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | DI | MCC | UCP-C | NO | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
135
136 | HST-2205 | HST-2205 C | C | START COMMAND LUB OIL COOLER | LUB OIL COOLER (AE-2101-OC C) | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | DOR | UCP-C | MCC | NO | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
137 | HSP-2205 | HSP-2205 C | C | STOP COMMAND LUB OIL COOLER | LUB OIL COOLER (AE-2101-OC C) | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | DOR | UCP-C | MCC | NC | D | NC | NIS | [7 empty] | ZONE2, IIB, T3
138 | XL-2205 | XL-2205 C | C | RUNNING STATUS LUB OIL COOLER | LUB OIL COOLER (AE-2101-OC C) | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | DI | MCC | UCP-C | NO | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
139 | XA-2205 | XA-2205 C | C | FAILURE STATUS LUB OIL COOLER | LUB OIL COOLER (AE-2101-OC C) | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | DI | MCC | UCP-C | NO | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
140
141 | PT-2210 | PT-2210C | C | PRESSURE TRANSMITTER | N2 TO CYLINDER PACKING INLET | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 4C | 1" |  |  | AI | FIELD | UCP-C | 4-20mA Hart | - | 4-20mA | IS |  | 0-6 | BARG |  |  |  |  | ZONE2, IIB, T3
142 | PI-2210 | PI-2210C | C | PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 4C |  |  |  | - | UCP-C | CCR
143 | PAL-2210 | PAL-2210C | C | PRESSURE ALARM LOW |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 4C |  |  |  | - | UCP-C | CCR
144
145 | PT-2211 | PT-2211C | C | PRESSURE TRANSMITTER | N2 TO CYLINDER PACKING INLET | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 4C | 1" |  |  | AI | FIELD | UCP-C | 4-20mA Hart | - | 4-20mA | IS |  | 0-6 | BARG |  |  |  |  | ZONE2, IIB, T3
146 | PI-2211 | PI-2211C | C | PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 4C |  |  |  | - | UCP-C | CCR
147 | PAL-2211 | PAL-2211C | C | PRESSURE ALARM LOW |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 4C |  |  |  | - | UCP-C | CCR
148
149 | HST-2220 | HST-2220 C | C | START COMMAND WATER CONSULE COOLER | WATER CONSULE COOLER (AE-2101-WC C) | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  | DOR | UCP-C | MCC | NO | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
150 | HSP-2220 | HSP-2220 C | C | STOP COMMAND WATER CONSULE COOLER | WATER CONSULE COOLER (AE-2101-WC C) | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  | DOR | UCP-C | MCC | NC | D | NC | NIS | [7 empty] | ZONE2, IIB, T3
151 | XL-2220 | XL-2220 C | C | RUNNING STATUS WATER CONSULE COOLER | WATER CONSULE COOLER (AE-2101-WC C) | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  | DI | MCC | UCP-C | NO | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
152 | XA-2220 | XA-2220 C | C | FAILURE STATUS WATER CONSULE COOLER | WATER CONSULE COOLER (AE-2101-WC C) | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  | DI | MCC | UCP-C | NO | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
153
154 | HST-2221 | HST-2221 C | C | START COMMAND AUX WATER PUMP | AUX WATER PUMP (P-2101-AX C) | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  | DOR | UCP-C | MCC | NO | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
155 | HSP-2221 | HSP-2221 C | C | STOT COMMAND AUX WATER PUMP | AUX WATER PUMP (P-2101-AX C) | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  | DOR | UCP-C | MCC | NC | D | NC | NIS | [7 empty] | ZONE2, IIB, T3
156 | XL-2221 | XL-2221C | C | RUNNING STATUS AUX WATER PUMP | AUX WATER PUMP (P-2101-AX C) | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  | DI | MCC | UCP-C | NO | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
157 | XA-2221 | XA-2221 C | C | FAILURE STATUS AUX WATER PUMP | AUX WATER PUMP (P-2101-AX C) | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  | DI | MCC | UCP-C | NO | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
158
159 | HST-2222 | HST-2222 C | C | START COMMAND MAIN WATER PUMP | MAIN WATER PUMP (P-2101-WP C) | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  | DOR | UCP-C | MCC | NO | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
160 | HSP-2222 | HSP-2222 C | C | STOP COMMAND MAIN WATER PUMP | MAIN WATER PUMP (P-2101-WP C) | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  | DOR | UCP-C | MCC | NC | D | NC | NIS | [7 empty] | ZONE2, IIB, T3
161 | XL-2222 | XL-2222C | C | RUNNING STATUS MAIN WATER PUMP | MAIN WATER PUMP (P-2101-WP C) | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  | DI | MCC | UCP-C | NO | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
162 | XA-2222 | XA-2222 C | C | FAILURE STATUS MAIN WATER PUMP | MAIN WATER PUMP (P-2101-WP C) | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  | DI | MCC | UCP-C | NO | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
163
164 | HST-2223 | HST-2223 C | C | START COMMAND HEATER WATER CONSULE | WATER CONSULE COOLER HEATER (AE-2101-WC C) | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  | DOR | UCP-C | MCC | NO | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
165 | HSP-2223 | HSP-2223 C | C | STOP COMMAND HEATER WATER CONSULE | WATER CONSULE COOLER HEATER (AE-2101-WC C) | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  | DOR | UCP-C | MCC | NC | D | NC | NIS | [7 empty] | ZONE2, IIB, T3
166 | XL-2223 | XL-2223C | C | RUNNING STATUS HEATER WATER CONSULE | WATER CONSULE COOLER HEATER (AE-2101-WC C) | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  | DI | MCC | UCP-C | NO | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
167 | XA-2223 | XA-2223 C | C | FAILURE STATUS HEATER WATER CONSULE | WATER CONSULE COOLER HEATER (AE-2101-WC C) | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  | DI | MCC | UCP-C | NO | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
168
169 | PT-2220 | PT-2220C | C | PRESSURE TRANSMITTER | WATER TO CYLINDERS | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C | 2" |  |  | AIR | FIELD | FIELD | 4-20mA Hart | - | 4-20mA | IS |  | 0-16 | BARG |  |  |  |  | ZONE2, IIB, T3
170 | PI-2220 | PI-2220C | C | PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  | - | UCP-C | CCR
171 | PAL-2220 | PAL-2220C | C | PRESSURE ALARM LOW |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  | - | UCP-C | CCR
172 | PAH-2220 | PAH-2220C | C | PRESSURE ALARM HIGH |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  | - | UCP-C | CCR
173
174 | PT-2221 | PT-2221C | C | PRESSURE TRANSMITTER | WATER TO CYLINDERS | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C | 2" |  |  | AI | FIELD | FIELD | 4-20mA Hart | - | 4-20mA | IS |  | 0-16 | BARG |  |  |  |  | ZONE2, IIB, T3
175 | PI-2221 | PI-2221C | C | PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  | - | UCP-C | CCR
176 | PAL-2221 | PAL-2221C | C | PRESSURE ALARM LOW |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  | - | UCP-C | CCR
177 |  |  | C
178 | PS-2220 | PS-2220C | C | PRESSURE SWITCH | WATER TO CYLINDERS | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C | 2" |  |  | DI | Field | USD |  |  |  | NIS |  | 0-16 | BARG
179 | PALL-2220 | PALL-2220C | C | PRESSURE ALARM LOW LOW | WATER TO CYLINDERS | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  | - | Field | UCP-C
180
181 | TT-2213 | TT-2213C | C | TEMPERATURE TRANSMITTER | WATER RESERVOIR | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  | AIR | FIELD | UCP-C | 4-20mA Hart | - | 4-20mA | IS |  | 0-100 | °C |  |  |  |  | ZONE2, IIB, T3
182 | TE-2213 | TE-2213C | C | THERMO ELEMENT |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C | [5 empty] | FIELD
183 | TW-2213 | TW-2213C | C | THERMOWELL |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C | [5 empty] | FIELD
184 | TI-2213 | TI-2213C | C | TEMPERATURE INDICATING |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  | - | UCP-C | CCR
185 | TAH-2213 | TAH-2213C | C | TEMPERATURE ALARM HIGH |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  | - | UCP-C | CCR
186 | TAL-2213 | TAL-2213C | C | TEMPERATURE ALARM LOW |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  | - | UCP-C | CCR
187 |  |  | C
188 | FT-2206 | FT-2206C | C | FLOW TRANSMITTER | WATER TO CYLINDERS | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C | 2" |  |  | AI | FIELD | UCP-C | 4-20mA Hart | - | 4-20mA | IS |  | 0-16 | BARG |  |  |  |  | ZONE2, IIB, T3
189 | FE-2221 | FE-2221C | C | FLOW ELEMENT |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  | - | FIELD | -
190 | FI-2221 | FI-2221C | C | FLOW INDICATING |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  | - | UCP-C | CCR
191
192 | HS-2239-L | HS-2239-LC | C | SELECTOR SWITCH | LOCAL MODE SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C | - | - | - | DI | LCP-C | UCP-C | NO | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
193 | HS-2239-R | HS-2239-RC | C | SELECTOR SWITCH | REMOTE MODE SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C | - | - | - | DI | LCP-C | UCP-C | NO | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
194 | HS-2230-M | HS-2230-MC | C | SELECTOR SWITCH | AUX. LUBE OIL PUMP MANU. SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C | - | - | - | DI | LCP-C | UCP-C | NO | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
195 | HS-2230-U | HS-2230-UC | C | SELECTOR SWITCH | AUX. LUBE OIL PUMP AUTO. SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C | - | - | - | DI | LCP-C | UCP-C | NO | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
196 | HS-2231-M | HS-2231-MC | C | SELECTOR SWITCH | OIL COOLER . SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C | - | - | - | DI | LCP-C | UCP-C | NO | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
197 | HS-2231-U | HS-2231-UC | C | SELECTOR SWITCH | OIL COOLER . SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C | - | - | - | DI | LCP-C | UCP-C | NO | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
198 | HS-2233-M | HS-2233-MC | C | SELECTOR SWITCH | MAIN WATER PUMP MANU SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C | - | - | - | DI | LCP-C | UCP-C | NO | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
199 | HS-2233-U | HS-2233-UC | C | SELECTOR SWITCH | MAIN WATER PUMP AUTO SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C | - | - | - | DI | LCP-C | UCP-C | NO | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
200 | HS-2234-M | HS-2234-MC | C | SELECTOR SWITCH | AUX WATER PUMP MANU SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C | - | - | - | DI | LCP-C | UCP-C | NO | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
201 | HS-2234-U | HS-2234-UC | C | SELECTOR SWITCH | AUX WATER PUMP AUTO SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C | - | - | - | DI | LCP-C | UCP-C | NO | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
202 | HS-2235-M | HS-2235-MC | C | SELECTOR SWITCH | WATER COOLER MANU SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C | - | - | - | DI | LCP-C | UCP-C | NO | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
203 | HS-2235-U | HS-2235-UC | C | SELECTOR SWITCH | WATER COOLER AUTO SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C | - | - | - | DI | LCP-C | UCP-C | NO | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
204 | HS-2236 | HS-2236C | C | PUSH BUTTON | LAMP TEST PUSHBUTTON SWITCH | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C | - | - | - | DI | LCP-C | UCP-C | NO | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
205 | HS-2237-T | HS-2237-TC | C | PUSH BUTTON | MAIN MOTOR START PUSHBUTTON | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C |  |  |  | DI | LCP-C | UCP-C | NO | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
206 | HS-2237-P | HS-2237-PC | C | PUSH BUTTON | MAIN MOTOR STOP PUSHBUTTON | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C |  |  |  | DI | LCP-C | UCP-C | NO | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
207 | HS-2238-T | HS-2238-TC | C | PUSH BUTTON | OIL HEATER ON PUSHBUTTON | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C |  |  |  | DI | LCP-C | UCP-C | NO | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
208 | HS-2238-P | HS-2238-PC | C | PUSH BUTTON | OIL HEATER OFF PUSHBUTTON | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C |  |  |  | DI | LCP-C | UCP-C | NO | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
209 | HS-2239-T | HS-2239-TC | C | PUSH BUTTON | AUX. LUBE OIL PUMP START PUSHBUTTON | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C |  |  |  | DI | LCP-C | UCP-C | NO | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
210 | HS-2239-P | HS-2239-PC | C | PUSH BUTTON | AUX. LUBE OIL PUMP STOP PUSHBUTTON | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C |  |  |  | DI | LCP-C | UCP-C | NO | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
211 | HS-2240-T | HS-2240-TC | C | PUSH BUTTON | OIL COOLER MOTOR A START PUSHBUTTON | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C |  |  |  | DI | LCP-C | UCP-C | NO | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
212 | HS-2240-P | HS-2240-PC | C | PUSH BUTTON | OIL COOLER MOTOR A STOP PUSHBUTTON | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C |  |  |  | DI | LCP-C | UCP-C | NO | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
213 | HS-2241-T | HS-2241-TC | C | PUSH BUTTON | OIL COOLER MOTOR B START PUSHBUTTON | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C |  |  |  | DI | LCP-C | UCP-C | NO | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
214 | HS-2241-P | HS-2241-PC | C | PUSH BUTTON | OIL COOLER MOTOR B STOP PUSHBUTTON | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C |  |  |  | DI | LCP-C | UCP-C | NO | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
215 | HS-2242-T | HS-2242-TC | C | PUSH BUTTON | LUB L HEATER ON PUSHBUTTON | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C |  |  |  | DI | LCP-C | UCP-C | NO | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
216 | HS-2242-P | HS-2242-PC | C | PUSH BUTTON | LUB HEATER OFF PUSHBUTTON | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C |  |  |  | DI | LCP-C | UCP-C | NO | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
217 | HS-2243-T | HS-2243-TC | C | PUSH BUTTON | LUB MOTOR START PUSHBUTTON | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C |  |  |  | DI | LCP-C | UCP-C | NO | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
218 | HS-2243-P | HS-2243-PC | C | PUSH BUTTON | LUB MOTOR STOP PUSHBUTTON | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C |  |  |  | DI | LCP-C | UCP-C | NO | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
219 | HS-2244-T | HS-2244-TC | C | PUSH BUTTON | MAIN WATER PUMP MOTOR START PUSHBUTTON | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C |  |  |  | DI | LCP-C | UCP-C | NO | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
220 | HS-2244-P | HS-2244-PC | C | PUSH BUTTON | MAIN WATER PUMP MOTOR STOP PUSHBUTTON | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C |  |  |  | DI | LCP-C | UCP-C | NO | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
221 | HS-2245-T | HS-2245-TC | C | PUSH BUTTON | AUX WATER PUMP MOTOR START PUSHBUTTON | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C |  |  |  | DI | LCP-C | UCP-C | NO | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
222 | HS-2245-P | HS-2245-PC | C | PUSH BUTTON | AUX WATER PUMP MOTOR STOP PUSHBUTTON | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C |  |  |  | DI | LCP-C | UCP-C | NO | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
223 | HS-2246-T | HS-2246-TC | C | PUSH BUTTON | WATER HEATER ON PUSHBUTTON | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C |  |  |  | DI | LCP-C | UCP-C | NO | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
224 | HS-2246-P | HS-2246-PC | C | PUSH BUTTON | WATER HEATER OFF PUSHBUTTON | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C |  |  |  | DI | LCP-C | UCP-C | NO | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
225 | HS-2247-T | HS-2247-TC | C | PUSH BUTTON | WATER COOLER MOTOR START PUSHBUTTON | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C |  |  |  | DI | LCP-C | UCP-C | NO | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
226 | HS-2247-P | HS-2247-PC | C | PUSH BUTTON | WATER COOLER MOTOR STOP PUSHBUTTON | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C |  |  |  | DI | LCP-C | UCP-C | NO | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
227 | HS-2248-T | HS-2248-TC | C | PUSH BUTTON | BEARING MOTOR START PUSHBUTTON | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C |  |  |  | DI | LCP-C | UCP-C | NO | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
228 | HS-2248-P | HS-2248-PC | C | PUSH BUTTON | BEARING MOTOR STOP PUSHBUTTON | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C |  |  |  | DI | LCP-C | UCP-C | NO | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
229 | HS-2250 | HS-2250C | C | PUSH BUTTON | RESET PUSH BUTTON | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C |  |  |  | DI | LCP-C | UCP-C | NO | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
230 | HS-2238-U | HS-2238-UC | C | SELECTOR SWITCH | OIL COOLER AUTO SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C | - | - | - | DI | LCP-C | UCP-C | NO | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
231 | HS-2240 | HS-2240C | C | EMERGENCY SHUT DOWN | RESET PUSH BUTTON | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C |  |  |  | DI | LCP-C | UCP-C | NO | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
232 | XL-2230 | XL-2230C | C | SIGNAL LAMP | OIL HEATER ACTIVE LAMP | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C | - | - | - | DO | UCP-C | LCP-C | NO | W | NO | NIS | [7 empty] | ZONE2, IIB, T3
233 | XL-2231 | XL-2231C | C | SIGNAL LAMP | AUX LUBE OILPUMP MOTOR START LAMP | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C | - | - | - | DO | UCP-C | LCP-C | NO | W | NO | NIS | [7 empty] | ZONE2, IIB, T3
234 | XL-2184 | XL-2184C | C | SIGNAL LAMP | COMMON ALARM LAMP | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C | - | - | - | DO | UCP-C | LCP-C | NO | W | NO | NIS | [7 empty] | ZONE2, IIB, T3
235 | XL-2185 | XL-2185C | C | SIGNAL LAMP | COMMON SHUTDOWN LAMP | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C | - | - | - | DO | UCP-C | LCP-C | NO | W | NO | NIS | [7 empty] | ZONE2, IIB, T3
236 | XL-2232 | XL-2232C | C | SIGNAL LAMP | LUBRICATOR OIL HEATER ON LAMP | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C | - | - | - | DO | UCP-C | LCP-C | NO | W | NO | NIS | [7 empty] | ZONE2, IIB, T3
237 | XL-2233 | XL-2233C | C | SIGNAL LAMP | LUBRICATOR OIL MOTOR START LAMP | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C | - | - | - | DO | UCP-C | LCP-C | NO | W | NO | NIS | [7 empty] | ZONE2, IIB, T3
238 | XL-2234 | XL-2234C | C | SIGNAL LAMP | MAIN MOTOR RUNNING LAMP | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C | - | - | - | DO | UCP-C | LCP-C | NO | W | NO | NIS | [7 empty] | ZONE2, IIB, T3
239 | XL-2235 | XL-2235C | C | SIGNAL LAMP | OIL COOLER MOTOR A RUNNING LAMP | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C | - | - | - | DO | UCP-C | LCP-C | NO | W | NO | NIS | [7 empty] | ZONE2, IIB, T3
240 | XL-2236 | XL-2236C | C | SIGNAL LAMP | OIL COOLER MOTOR B RUNNING LAMP | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C |  |  |  | DO | UCP-C | LCP-C | NO | W | NO | NIS | [7 empty] | ZONE2, IIB, T3
241 | XL-2237 | XL-2237C | C | SIGNAL LAMP | MAIN WATER PUMP MOTOR RUNNING LAMP | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C |  |  |  | DO | UCP-C | LCP-C | NO | W | NO | NIS | [7 empty] | ZONE2, IIB, T3
242 | XL-2238 | XL-2238C | C | SIGNAL LAMP | AUX WATER PUMP MOTOR RUNNING LAMP | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C |  |  |  | DO | UCP-C | LCP-C | NO | W | NO | NIS | [7 empty] | ZONE2, IIB, T3
243 | XL-2239 | XL-2239C | C | SIGNAL LAMP | WATER HEATER ACTIVE LAMP | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C |  |  |  | DO | UCP-C | LCP-C | NO | W | NO | NIS | [7 empty] | ZONE2, IIB, T3
244 | XL-2240 | XL-2240C | C | SIGNAL LAMP | WATER COOLER RUNNING LAMP | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C |  |  |  | DO | UCP-C | LCP-C | NO | W | NO | NIS | [7 empty] | ZONE2, IIB, T3
245 | XL-2241 | XL-2241C | C | SIGNAL LAMP | BEARRING MOTOR RUNNING LAMP | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C |  |  |  | DO | UCP-C | LCP-C | NO | W | NO | NIS | [7 empty] | ZONE2, IIB, T3
246 | XL-2242 | XL-2242C | C | SIGNAL LAMP | READY TO START LAMP | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C |  |  |  | DO | UCP-C | LCP-C | NO | W | NO | NIS | [7 empty] | ZONE2, IIB, T3
247 | XL-2243 | XL-2243C | C | SIGNAL LAMP | COMMON ALARM LAMP | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C |  |  |  | DO | UCP-C | LCP-C | NO | W | NO | NIS | [7 empty] | ZONE2, IIB, T3
248 | XL-2244 | XL-2244C | C | SIGNAL LAMP | COMMON SHUT DOWN LAMP | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C |  |  |  | DO | UCP-C | LCP-C | NO | W | NO | NIS | [7 empty] | ZONE2, IIB, T3
249 |  |  | C
250 | VT-2202 | VT-2202C | C | VIBRATION TRANSMITTER | FRAME VIBRATION | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | AI | FIELD | Trip Relay UCP C | 4-20mA | - | 4-20mA | IS |  | HOLD | HOLD |  |  |  |  | ZONE2, IIB, T3
251 | VE--2202 | VE--2202C | C | VIBRATION ELEMENT |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C | DO DO DO DO DO DO DO DO: -; UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C: FIELD; LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C: -
252 | VI--2202 | VI--2202C | C | VIBRATION INDICATING |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C | DO DO DO DO DO DO DO DO: -; UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C: UCP-C; LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C: CCR
253 | VAH-2202 | VAH-2202C | C | VIBRATION ALARM HIGH |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C | DO DO DO DO DO DO DO DO: -; UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C: UCP-C; LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C: CCR
254 | VAHH-2202 | VAHH-2202C | C | VIBRATION ALARM HIGH HIGH |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C | DO DO DO DO DO DO DO DO: AI; UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C: UCP-C; LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C: CCR
255 |  |  | C
256 | VT--2200 | VT--2200C | C | VIBRATION TRANSMITTER | FRAME VIBRATION | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | AI | FIELD | Trip Relay UCP C | 4-20mA | - | 4-20mA | IS |  | HOLD | HOLD |  |  |  |  | ZONE2, IIB, T3
257 | VE--2200 | VE--2200C | C | VIBRATION ELEMENT |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C | DO DO DO DO DO DO DO DO: -; UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C: FIELD; LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C: -
258 | VI--2200 | VI--2200C | C | VIBRATION INDICATING |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C | DO DO DO DO DO DO DO DO: -; UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C: UCP-C; LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C: CCR
259 | VAH-2200 | VAH-2200C | C | VIBRATION ALARM HIGH |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C | DO DO DO DO DO DO DO DO: -; UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C: UCP-C; LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C: CCR
260 | VAHH-2200 | VAHH-2200C | C | VIBRATION ALARM HIGH HIGH |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C | DO DO DO DO DO DO DO DO: AI; UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C: UCP-C; LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C: CCR
261 |  |  | C
262 | VT-2201 | VT-2201C | C | VIBRATION TRANSMITTER | FRAME VIBRATION | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | AI | FIELD | Trip Relay UCP C | 4-20mA | - | 4-20mA | IS |  | HOLD | HOLD |  |  |  |  | ZONE2, IIB, T3
263 | VE-2201 | VE-2201C | C | VIBRATION ELEMENT |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C | DO DO DO DO DO DO DO DO: -; UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C: FIELD; LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C: -
264 | VI-2201 | VI-2201C | C | VIBRATION INDICATING |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C | DO DO DO DO DO DO DO DO: -; UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C: UCP-C; LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C: CCR
265 | VAH-2201 | VAH-2201C | C | VIBRATION ALARM HIGH |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C | DO DO DO DO DO DO DO DO: -; UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C: UCP-C; LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C: CCR
266 | VAHH-2201 | VAHH-2201C | C | VIBRATION ALARM HIGH HIGH |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C | DO DO DO DO DO DO DO DO: AI; UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C: UCP-C; LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C: CCR
267
268 |  |  | C
269 | TE-2214 | TE-2214C | C | RTD THERMO ELEMENT | Comp. Frame Temp. Measurment | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C | UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C: FIELD; NO NO NO NO NO NO NO NO: RTD; W W W W W W W W: -; NO NO NO NO NO NO NO NO: RTD |  | HOLD | [5 empty] | ZONE2, IIB, T3
270 | TT-2214 | TT-2214C | C | TEMPERATURE TRAMSMITTER |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C | DO DO DO DO DO DO DO DO: AI; UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C: FIELD; LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C: UCP-C; NO NO NO NO NO NO NO NO: 4-20mA Hart; NIS NIS NIS NIS NIS NIS NIS NIS: IS |  | HOLD
271 | TI-2214 | TI-2214C | C | TEMPERATURE INDICATION |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C | DO DO DO DO DO DO DO DO: -; UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C: UCP-C; LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C: CCR
272 | TAH-2214 | TAH-2214C | C | TEMPERATURE ALARM HIGH |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C | DO DO DO DO DO DO DO DO: -; UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C: UCP-C; LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C: CCR
273
274 | TE-2215 | TE-2215C | C | RTD THERMO ELEMENT | Comp. Frame Temp. Measurment | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C | UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C: FIELD; NO NO NO NO NO NO NO NO: RTD; W W W W W W W W: -; NO NO NO NO NO NO NO NO: RTD |  | HOLD | [5 empty] | ZONE2, IIB, T3
275 | TT-2215 | TT-2215C | C | TEMPERATURE TRAMSMITTER |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C | DO DO DO DO DO DO DO DO: AI; UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C: FIELD; LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C: UCP-C; NO NO NO NO NO NO NO NO: 4-20mA Hart; NIS NIS NIS NIS NIS NIS NIS NIS: IS
276 | TI-2215 | TI-2215C | C | TEMPERATURE INDICATION |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C | DO DO DO DO DO DO DO DO: -; UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C: UCP-C; LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C: CCR
277 | TAH-2215 | TAH-2215C | C | TEMPERATURE ALARM HIGH |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C | DO DO DO DO DO DO DO DO: -; UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C: UCP-C; LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C: CCR
278
279 | TE-2216 | TE-2216C | C | RTD THERMO ELEMENT | Comp. Frame Temp. Measurment | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C | UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C: FIELD; NO NO NO NO NO NO NO NO: RTD; W W W W W W W W: -; NO NO NO NO NO NO NO NO: RTD |  | HOLD | [5 empty] | ZONE2, IIB, T3
280 | TT-2216 | TT-2216C | C | TEMPERATURE TRANSMITTER | Cylinder Rod Temp. Measurment | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | AI | FIELD | Trip Relay UCP C | 4-20mA Hart | - | 4-20mA | IS |  | HOLD | HOLD |  |  |  |  | ZONE2, IIB, T3
281 | TI-2216 | TI-2216C | C | RTD THERMO ELEMENT |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C | UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C: UCP-C; LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C: CCR
282 | TAH-2216 | TAH-2216C | C | TEMPERATURE ALARM HIGH |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C | DO DO DO DO DO DO DO DO: -; UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C: UCP-C; LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C: CCR
283 | TAHH-2216 | TAHH-2216C | C | TEMPERATURE ALARM HIGH HIGH |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C | UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C: UCP-C; LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C: CCR
284 |  |  | C
285 | TE-2217 | TE-2217C | C | RTD THERMO ELEMENT | Comp. Power Bearing Temp. Measurment | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C | UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C: FIELD; NO NO NO NO NO NO NO NO: RTD; W W W W W W W W: -; NO NO NO NO NO NO NO NO: RTD; NIS NIS NIS NIS NIS NIS NIS NIS: IS |  | HOLD | [5 empty] | ZONE2, IIB, T3
286 | TT-2217 | TT-2217C | C | TEMPERATURET RAMSMITTER |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C | DO DO DO DO DO DO DO DO: AI; UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C: UCP-C; LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C: Trip Relay UCP C; NO NO NO NO NO NO NO NO: 4-20mA Hart; NO NO NO NO NO NO NO NO: 4-20mA
287 | TI-2217 | TI-2217C | C | RTD THERMO ELEMENT |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C | UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C: UCP-C; LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C: CCR
288 | TAH-2217 | TAH-2217C | C | TEMPERATURE ALARM HIGH |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C | DO DO DO DO DO DO DO DO: -; UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C: UCP-C; LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C: CCR
289 | TAHH-2217 | TAHH-2217C | C | TEMPERATURE ALARM HIGH HIGH |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C | DO DO DO DO DO DO DO DO: -; UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C: UCP-C; LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C: CCR
290
291 | TE-2218 | TE-2218C | C | RTD THERMO ELEMENT | Comp. Power Bearing Temp. Measurment | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C | UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C: FIELD; NO NO NO NO NO NO NO NO: RTD; W W W W W W W W: -; NO NO NO NO NO NO NO NO: RTD |  | HOLD | [5 empty] | ZONE2, IIB, T3
292 | TT-2218 | TT-2218C | C | TEMPERATURE TRANSMITTER | RIGHT Cylinder Rod Temp. Measurment | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | AI | FIELD | Trip Relay UCP C | 4-20mA Hart | - | 4-20mA | IS |  | HOLD | HOLD |  |  |  |  | ZONE2, IIB, T3
293 | TI-2218 | TI-2218C | C | RTD THERMO ELEMENT |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C | DO DO DO DO DO DO DO DO: -; UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C: UCP-C; LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C: CCR
294 | TAH-2218 | TAH-2218C | C | TEMPERATURE ALARM HIGH |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C | DO DO DO DO DO DO DO DO: -; UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C: UCP-C; LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C: CCR
295 | TAHH-2218 | TAHH-2218C | C | TEMPERATURE ALARM HIGH HIGH |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C | DO DO DO DO DO DO DO DO: -; UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C: UCP-C; LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C: CCR
296
297 | TE-2219 | TE-2219C | C | RTD THERMO ELEMENT | Comp. Power Bearing Temp. Measurment | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C | UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C: FIELD; NO NO NO NO NO NO NO NO: RTD; W W W W W W W W: -; NO NO NO NO NO NO NO NO: RTD |  | HOLD | [5 empty] | ZONE2, IIB, T3
298 | TT-2219 | TT-2219C | C | TEMPERATURE TRANSMITTER | RIGHT Cylinder Rod Temp. Measurment | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | AI | FIELD | Trip Relay UCP C | 4-20mA Hart | - | 4-20mA | IS |  | HOLD | HOLD |  |  |  |  | ZONE2, IIB, T3
299 | TI-2219 | TI-2219C | C | TEMPERATURE TRAMSMITTER |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C | DO DO DO DO DO DO DO DO: -; UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C: UCP-C; LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C: CCR
300 | TAH-2219 | TAH-2219C | C | TEMPERATURE ALARM HIGH |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C | DO DO DO DO DO DO DO DO: -; UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C: UCP-C; LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C: CCR
301 | TAHH-2219 | TAHH-2219C | C | TEMPERATURE ALARM HIGH HIGH |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C | DO DO DO DO DO DO DO DO: -; UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C: UCP-C; LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C: CCR
302 |  |  | C
303 | ZT-2201 | ZT-2201C | C | ROD DROP TRANSMITTER | Cylinder Rod Drop Detector | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | AI | FIELD | UCP-C | 4-20mA | - | 4-20mA | IS |  | HOLD | HOLD |  |  |  |  | ZONE2, IIB, T3
304 | ZE-2201 | ZE-2201C | C | ROD DROP ELEMENT |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C | UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C: FIELD
305 | ZI-2201 | ZI-2201C | C | ROD DROP INDICATOR |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C | UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C: UCP-C; LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C: CCR
306 | ZAH-2201 | ZAH-2201C | C | ROD DROP ALARM HIGH |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C | DO DO DO DO DO DO DO DO: -; UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C: UCP-C; LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C: CCR
307
308 | ZT-2200 | ZT-2200C | C | ROD DROP TRANSMITTER | LEFT Cylinder Rod Drop Detector | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | AI | FIELD | UCP-C | 4-20mA | - | 4-20mA | IS |  | HOLD | HOLD |  |  |  |  | ZONE2, IIB, T3
309 | ZE-2200 | ZE-2200C | C | ROD DROP ELEMENT |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C | UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C: FIELD
310 | ZI-2200 | ZI-2200C | C | ROD DROP INDICATOR |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C | UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C: UCP-C; LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C: CCR
311 | ZAH-2200 | ZAH-2200C | C | ROD DROP ALARM HIGH |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C | DO DO DO DO DO DO DO DO: -; UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C UCP-C: UCP-C; LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C LCP-C: CCR
312
313 | TE-2222 | TE-2222C | C | RTD THERMO ELEMENT | MAIN MOTOR R-PHASE WINDING TEMP. | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | AI | Motor | MCC | RTD | - | RTD | IS |  | 1-100 | °C |  |  |  |  | ZONE2, IIB, T3
314 | TE-2228 | XL-2222C | C | RTD R TRIP FEEDBACK | MAIN MOTOR R-PHASE WINDING TEMPTRIP FEEDBACK. | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | DI | MCC | UCP-C | 24VDC | - | N.O | NIS
315
316 | TE-2225 | TE-2225C | C | RTD THERMO ELEMENT | MAIN MOTOR S-PHASE WINDING TEMP. | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | AI | Motor | MCC | RTD | - | RTD | IS |  | 0-100 | °C |  |  |  |  | ZONE2, IIB, T3
314 | TE-2228 | XL-2225C | C | RTD S TRIP FEEDBACK | MAIN MOTOR S-PHASE WINDING TEMPTRIP FEEDBACK. | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | DI | MCC | UCP-C | 24VDC | - | N.O | NIS
318
319 | TE-2228 | TE-2228C | C | RTD THERMO ELEMENT | MAIN MOTOR T-PHASE WINDING TEMP. | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | AI | Motor | MCC | RTD | - | RTD | IS |  | 0-100 | °C |  |  |  |  | ZONE2, IIB, T3
314 | TE-2228 | XL-2228C | C | RTD T TRIP FEEDBACK | MAIN MOTOR T-PHASE WINDING TEMPTRIP FEEDBACK. | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | DI | MCC | UCP-C | 24VDC | - | N.O | NIS
321
322 | HST-2205 | HST-2205 C | C | START COMMAND | LOOB OIL COOLER (AE-2101-OC A/B/C) | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | DOR | UCP-C | MCC | NO | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
323 | HSP-2205 | HSP-2205 C | C | STOP COMMAND |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | DOR | UCP-C | MCC | NC | D | NC | NIS | [7 empty] | ZONE2, IIB, T3
324 | XL-2205 | XL-2205 C | C | RUNNING STATUS |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | DI | MCC | UCP-C | NO | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
325 | XA-2205 | XA-2205 C | C | FAILURE STATUS |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | DI | MCC | UCP-C | NO | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
326
327 | HST-2225 | HST-2225 |  | START COMMAND | MOTOR BEARING DEVICE MOTOR | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C | - | - | - | DOR | UCP-C | MCC | NO | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
328 | HSP-2225 | HSP-2225 C | C | STOP COMMAND |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C | - | - | - | DOR | UCP-C | MCC | NC | D | NC | NIS | [7 empty] | ZONE2, IIB, T3
329 | XL-2225 | XL-2225 C | C | RUNNING STATUS |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C | - | - | - | DI | MCC | UCP-C | NO | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
330 | XA-2225 | XA-2225 C | C | FAULT STATUS |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C | - | - | - | DI | MCC | UCP-C | NO | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
331
332 | HST-2224 | HST-2224 C | C | START COMMAND | MAKE UP GAS COMPRESSOR MAIN MOTOR | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C | - | - | - | DOR | UCP-C | MCC | NO | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
333 | HSP-2224 | HSP-2224 C | C | STOP COMMAND |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C | - | - | - | DOR | UCP-C | MCC | NC | D | NC | NIS | [7 empty] | ZONE2, IIB, T3
334 | XL-2224 | XL-2224 C | C | RUNNING STATUS |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C | - | - | - | DI | MCC | UCP-C | NO | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
335 | XA-2224 | XA-2224 C | C | FAULT STATUS |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C | - | - | - | DI | MCC | UCP-C | NO | D | NO | NIS | [7 empty] | ZONE2, IIB, T3
336
337 | PCV-2123 | PCV-2123C | C | CONTROL VALVE | SPILL BACK VALVE | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C | UCP-C UCP-C MCC MCC: UCP-C; MCC MCC UCP-C UCP-C: FIELD; NIS NIS NIS NIS: IS | FO
338 | PCY-2123 | PCY-2123 C | C | CONTROLLER |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C |  |  |  | AOR | UCP-C | FIELD |  | - | 4-20mA | IS
339 | PCVY-2123 | PCYZ-2123C | C | Feed back |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C | DOR DOR DI DI: AI; UCP-C UCP-C MCC MCC: UCP-C; MCC MCC UCP-C UCP-C: FIELD; NO NC NO NO: 4-20mA; NIS NIS NIS NIS: IS
339 | CZSO-2123 | CZSO-2123 C | C | LIMIT SWITCH |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C | DOR DOR DI DI: DI; UCP-C UCP-C MCC MCC: FIELD; MCC MCC UCP-C UCP-C: UCP-C; NIS NIS NIS NIS: NIS
340 | CZSC-2123 | CZSC-2123 C | C | LIMIT SWITCH |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C | DOR DOR DI DI: DI; UCP-C UCP-C MCC MCC: FIELD; MCC MCC UCP-C UCP-C: UCP-C; NIS NIS NIS NIS: NIS
341 | PY-2123 | PY-2123 C | C | SOLENOID VALVE |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C | DOR DOR DI DI: DOR; UCP-C UCP-C MCC MCC: UCP-C; MCC MCC UCP-C UCP-C: FIELD; NIS NIS NIS NIS: NIS
342
343 | XV-2121 | XV-2121C | C | ON OFF VALVE | INPUT ON OFF VALVE(CLINET SIDE) | PACKAGE COMPRESSOR C-2101 C | BK-GCS-PEDCO-120-PR-PI-0006-SHEET 1C | UCP-C UCP-C MCC MCC: FIELD
344 | PSOV-2121 | PSOV-2121C | C | ON OFF VALVE SOLENOID |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-PEDCO-120-PR-PI-0006-SHEET 1C |  |  |  | DOR | UCP-C | FIELD |  | W | 24VDC | NIS | FO
345 | XZIC-2121 | XZIC-2121C | C | LIMIT SWITCH |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-PEDCO-120-PR-PI-0006-SHEET 1C |  |  |  | DI | FIELD | UCP-C |  | W | 24VDC | NIS
346 | XZIO-2121 | XZIO-2121C | C | LIMIT SWITCH |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-PEDCO-120-PR-PI-0006-SHEET 1C |  |  |  | DI | FIELD | UCP-C | 24VDC | W | 24VDC | NIS
347
348 | XV-2133 | XV-2133C | C | ON OFF VALVE | OUTPUT OFF VALVE(CLINET SIDE) | PACKAGE COMPRESSOR C-2101 C | BK-GCS-PEDCO-120-PR-PI-0011-SHEET 1C | UCP-C UCP-C MCC MCC: FIELD
349 | PSOV-2233 | PSOV-2233C | C | ON OFF VALVE SOLENOID |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-PEDCO-120-PR-PI-0011-SHEET 1C |  |  |  | DOR | UCP-C | FIELD |  | W | 24VDC | NIS | FO
350 | XZIC-2133 | XZIC-2133C | C | LIMIT SWITCH |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-PEDCO-120-PR-PI-0011-SHEET 1C |  |  |  | DI | FIELD | UCP-C |  | W | 24VDC | NIS
351 | XZIO-2133 | XZIO-2133C | C | LIMIT SWITCH |  | PACKAGE COMPRESSOR C-2101 C | BK-GCS-PEDCO-120-PR-PI-0011-SHEET 1C |  |  |  | DI | FIELD | UCP-C | 24VDC | W | 24VDC | NIS
312
313
314
315
316
317
318
319
320
321
322
323
324
325
326
327
328
329
330
331
332
332
333
334
335
336
337
338
339
340
341
342
343
344
345
346
347
348
348
349
350
351
352
351
352
353
354
355
356
357
Note on B108: Forouzandeh Fatemeh: ALARM L,H چک شود