## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-EL-TB-0003 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-2521 |  |  | Transmital Date: 12/26/2023
Document Title: TBE For Existent MV Switchgear Expansion & RCP |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0210-EL-TR-2521 |  |  | Transmital Date: 12/26/2023
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-PEDCO-120-EL-TB-0003_D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | Following items shall be added to TCL and completed by vendor in next revision: |  | BK-SUR-ENG-ELE-02-08933 | 2024-01-09
1-1 | Certificate or license, test reports and type test shall be submitted based on latest revison of related standard especially for MV switchgear such as IP, short circuit level, temperature rise and etc. |  | BK-SUR-ENG-ELE-02-08933 | 2024-01-09 | اضافه گردید.
1-2 | Vendor is supposed to prepare preliminary substation arrangement drawing for this project and consider dummy panel (if required). See and use attached file as project arrangement document. It is obvious exact number of dummy panels will be specified by vendor. Meanwhile dummy panel(s) shall be similar to other cubicles. |  | BK-SUR-ENG-ELE-02-08933 | 2024-01-09 | اعمال گردید.
1-3 | Exact part list of the Switchgear including equipment name, brand, model and origin shall be submitted considering this TCL. Vendor is responsible for exact part list of the SWG. If any item to be missed from the part list, Vendor shall consider it without any cost & time impact. |  | BK-SUR-ENG-ELE-02-08933 | 2024-01-09 | بند 28 به TCL اضافه گردید.
1-4 | Native completed deviation from Purchase Order or Purchaser procurement documents shall be submitted in next revision. |  | BK-SUR-ENG-ELE-02-08933 | 2024-01-09 | اعمال گردید.
1-5 | All required signals and mapping shall be submitted and considered From/To DCS base on "Electrical I/O Signal List BK-GCS-PEDCO-120-EL-LI-0005". Manufacturer shall consider suitable relays / auxiliary contacts for this reason. Vendor shall confirm necessary facility will be considered. Please follow Electrical I/O Signal List (See attach file). |  | BK-SUR-ENG-ELE-02-08933 | 2024-01-09 | بند 29 به TCL اضافه گردید.
1-6 | Certificate for country of origin shall be submitted by Vendor (after PO.). Please confirm. |  | BK-SUR-ENG-ELE-02-08933 | 2024-01-09 | بند 26 از TCL اصلاح گردید.
1-7 | Burden of CT’ & PT’s will be finalized after purchase order based on the related calculation that will be submitted by Vendor and shall be approved by Purchaser. Please confirm. |  | BK-SUR-ENG-ELE-02-08933 | 2024-01-09 | اعمال گردیید.
1-8 | The software of the protection relay shall be provided with original licence. Please confirm. |  | BK-SUR-ENG-ELE-02-08933 | 2024-01-09 | اعمال گردیید.
1-9 | All protection relays are equipped with key pan and LCD display, and 7 Numbers Digital input /7 Numbers Dry Output Contacts as minimum which is should be re-checked with schematic diagram. |  | BK-SUR-ENG-ELE-02-08933 | 2024-01-09 | بند 32 از TCL اضافه گردید.
1-10 | All relays supplied with MV switchgear shall be microprocessor based, which will facilitate a connection to DCS. Please confirm. |  | BK-SUR-ENG-ELE-02-08933 | 2024-01-09 | اضافه گردید.
1-11 | Vendor shall perform programming of the relays based on requirements of logic diagram. Related documents shall be submitted. Please confirm. |  | BK-SUR-ENG-ELE-02-08933 | 2024-01-09 | اضافه گردید.
1-12 | Vendor shall perform relay setting and relay coordination based on project relay coordination and setting study. Please confirm. |  | BK-SUR-ENG-ELE-02-08933 | 2024-01-09 | اضافه گردید.
1-13 | All digital multimeters and protection relays shall have Mod Bus (RS 485) communication protocol. Please confirm. |  | BK-SUR-ENG-ELE-02-08933 | 2024-01-09 | اضافه گردید.
2 | Following description shall be added to Item 1 in TCL: Vendor shall submitted temperature de‐rating factors of equipment such as CB, etc. It means Vendor shall de-rate the rated current of equipment on the site condition such way that de-rated rated current be equal or higher than rate current. De-rating curves/Tables (altitude & Ambient Temperature) shall be submitted at this stage. Please confirm. |  | BK-SUR-ENG-ELE-02-08933 | 2024-01-09 | اضافه گردید.
3 | Following description shall be added to Item 7 in TCL: Sub vendor list shall be submitted and following items shall be specified in sub vendor list: -Manufacture -Country of origin -Model Consideration shall be given that |  | BK-SUR-ENG-ELE-02-08933 | 2024-01-09 | اعمال گردید.
4 | Item 8 in TCL shall be modified as below: Based on the 22-E&C-QC-SP-1,Spare parts for pre-commissioning, commissioning/start up and spare parts for two years shall be submitted separately based on Spare Parts Specification. The supplied spare parts shall comply with the same specifications as the original parts and shall be interchangeable with the original parts without any modification. |  | BK-SUR-ENG-ELE-02-08933 | 2024-01-09 | اضافه گردید.
5 | Item 18 in TCL shall be modified as below: All the following items shall be considered in proposal for all Vacuum Circuit Breakers: Anti-pumping device, Mechanical operations counter, Manual mechanical trip facility Closed/open position indication, Start/Stop & Emergency Stop push button, Charged/discharged spring indication, Emergency shutdown interposing relay and Minimum 4 numbers make contacts. |  | BK-SUR-ENG-ELE-02-08933 | 2024-01-09 | اعمال گردید.
6 | All manufacturers shall be considered based on MOP. Any deviation from MOP is not acceptable. For example it shall be checked for Petro Tajhiz Iliya. |  | BK-SUR-ENG-ELE-02-08933 | 2024-01-09 | شرکت ایلیاتجهیز حذف گردید.
7 | Complimentary comments will be submitted after submitting revised technical offer based on comments. |  | BK-SUR-ENG-ELE-02-08933 | 2024-01-09 | در صورت وجود کامنت های دیگر، این کامنتها در نظر گرفته خواهد شد.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: |  |  |  |  | Date: