## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GNRAL-PEDCO-000-TE-SP-0005 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1850 |  |  | Transmital Date: 2/7/2023
Document Title: Specification for Telecommunication Tower |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0111-TE-TR-1850 |  |  | Transmital Date: 2/7/2023
[5 empty] | CRS No: CRS-BK-GNRAL-PEDCO-000-TE-SP-0005_D03 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | از آنجا که دکل مخابراتی یکی از مرتفع ترین سازه های موجود در سایت است،که منجر به دریافت حداکثری صاعقه و انتقال آن به تجهیزات حساس مخابراتی میشود. لذا ضروری است، با توجه به حساسیت موضوع، سیستم زمین (Earthing system) در نظر گرفته شده برای دکل به صورت کاملا مجزا از سیستم ارت موجود در سایت طراحی و اجرا گردد. شیوه اجرای سیستم ارت دکل به صورت کلی (لازم است با جزییات تهیه و ارایه شود) به این صورت است که برای هر پایه دکل چاه مناسب در کنار دکل حفر میگردد و در درون این چاه صفحه مسی به ابعاد 50*50 سانتیمتر به همراه مواد کاهنده مقاومت قرار داده میشود. در ادامه کابل ارت برقگیر توسط کابل مسی و به وسیله جوش کدولد به صفحه مسی موجود در چاه متصل میشوند. |  | 1401-2294-485155 | 1401/12/20 | اجرای سیستم صاعقه گیر برای دکل مخابراتی بر اساس نظر آن کارفرمای محترم صورت خواهد پذیرفت که در زمان این دکل مخابراتی اجرا می گردد. ( بند شرح کار: تهيه، نصب و راه اندازي دكل مخابراتي در واحد بهره برداري بينك به ارتفاع حداقل 50 متر كه : خودايستا، نيمه سنگين با قابليت نصب آنتن مايكروويو در ارتفاع 50 متري، به همراه فونداسيون ، سيستم ارت، صاعقه گير، سيستم روشنايي و متعلقات ديگر مطابق با استاندارد نفت درنظر گرفته شود.)
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: |  |  |  |  | Date: