| طرح نگهداشت و افزایش تولید 27 مخزن |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Calculation Note for Tank Foundation (TK-2301 A/B) نگهداشت و افزایش تولید میدان نفتی بینک |  |  |  |  |  |  |  |
| D02 |  | FEB. 2024 | IFA | R.Berlouie | M.Fakharian | S.Faramarzpour |  |
| D01 |  | OCT. 2023 | IFA | R.Berlouie | M.Fakharian | S.Faramarzpour |  |
| D00 |  | SEP. 2023 | IFC | R.Berlouie | M.Fakharian | A.M.Mohseni |  |
| Rev. |  | Date | Purpose of Issue/Status | Prepared by: | Checked by: | Approved by: | CLIENT Approval |
| Class:2 |  |  | COMPANY Doc. Number: F0Z-709122 |  |  |  |  |
| Status: |  | IDC: Inter-Discipline Check IFC: Issued For Comment IFA: Issued For Approval AFD: Approved For Design AFC: Approved For Construction AFP: Approved For Purchase AFQ: Approved For Quotation IFI: Issued For Information AB-R: As-Built for CLIENT Review AB-A: As-Built –Approved |  |  |  |  |  |

REVISION RECORD SHEET

| PAGE | D00 | D01 | D02 | D03 | D04 |  | PAGE | D00 | D01 | D02 | D03 | D04 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | X | X | X |  |  |  | 66 |  |  |  |  |  |
| 2 | X | X | X |  |  |  | 67 |  |  |  |  |  |
| 3 | X | X |  |  |  |  | 68 |  |  |  |  |  |
| 4 | X |  |  |  |  |  | 69 |  |  |  |  |  |
| 5 | X |  |  |  |  |  | 70 |  |  |  |  |  |
| 6 | X |  | X |  |  |  | 71 |  |  |  |  |  |
| 7 | X |  |  |  |  |  | 72 |  |  |  |  |  |
| 8 | X |  |  |  |  |  | 73 |  |  |  |  |  |
| 9 | X |  | X |  |  |  | 74 |  |  |  |  |  |
| 10 | X |  | X |  |  |  | 75 |  |  |  |  |  |
| 11 | X |  | X |  |  |  | 76 |  |  |  |  |  |
| 12 | X |  | X |  |  |  | 77 |  |  |  |  |  |
| 13 | X |  | X |  |  |  | 78 |  |  |  |  |  |
| 14 | X |  |  |  |  |  | 79 |  |  |  |  |  |
| 15 | X |  |  |  |  |  | 80 |  |  |  |  |  |
| 16 | X |  | X |  |  |  | 81 |  |  |  |  |  |
| 17 | X |  | X |  |  |  | 82 |  |  |  |  |  |
| 18 | X |  |  |  |  |  | 83 |  |  |  |  |  |
| 19 | X |  |  |  |  |  | 84 |  |  |  |  |  |
| 20 | X |  |  |  |  |  | 85 |  |  |  |  |  |
| 21 | X |  |  |  |  |  | 86 |  |  |  |  |  |
| 22 | X |  | X |  |  |  | 87 |  |  |  |  |  |
| 23 | X |  |  |  |  |  | 88 |  |  |  |  |  |
| 24 | X |  |  |  |  |  | 89 |  |  |  |  |  |
| 25 |  | X |  |  |  |  | 90 |  |  |  |  |  |
| 26 |  | X |  |  |  |  | 91 |  |  |  |  |  |
| 27 |  | X |  |  |  |  | 92 |  |  |  |  |  |
| 28 |  |  |  |  |  |  | 93 |  |  |  |  |  |
| 29 |  |  |  |  |  |  | 94 |  |  |  |  |  |
| 30 |  |  |  |  |  |  | 95 |  |  |  |  |  |
| 31 |  |  |  |  |  |  | 96 |  |  |  |  |  |
| 32 |  |  |  |  |  |  | 97 |  |  |  |  |  |
| 33 |  |  |  |  |  |  | 98 |  |  |  |  |  |
| 34 |  |  |  |  |  |  | 99 |  |  |  |  |  |
| 35 |  |  |  |  |  |  | 100 |  |  |  |  |  |
| 36 |  |  |  |  |  |  | 101 |  |  |  |  |  |
| 37 |  |  |  |  |  |  | 102 |  |  |  |  |  |
| 38 |  |  |  |  |  |  | 103 |  |  |  |  |  |
| 39 |  |  |  |  |  |  | 104 |  |  |  |  |  |
| 40 |  |  |  |  |  |  | 105 |  |  |  |  |  |
| 41 |  |  |  |  |  |  | 106 |  |  |  |  |  |
| 42 |  |  |  |  |  |  | 107 |  |  |  |  |  |
| 43 |  |  |  |  |  |  | 108 |  |  |  |  |  |
| 44 |  |  |  |  |  |  | 109 |  |  |  |  |  |
| 45 |  |  |  |  |  |  | 110 |  |  |  |  |  |
| 46 |  |  |  |  |  |  | 111 |  |  |  |  |  |
| 47 |  |  |  |  |  |  | 112 |  |  |  |  |  |
| 48 |  |  |  |  |  |  | 113 |  |  |  |  |  |
| 49 |  |  |  |  |  |  | 114 |  |  |  |  |  |
| 50 |  |  |  |  |  |  | 115 |  |  |  |  |  |
| 51 |  |  |  |  |  |  | 116 |  |  |  |  |  |
| 52 |  |  |  |  |  |  | 117 |  |  |  |  |  |
| 53 |  |  |  |  |  |  | 118 |  |  |  |  |  |
| 54 |  |  |  |  |  |  | 119 |  |  |  |  |  |
| 55 |  |  |  |  |  |  | 120 |  |  |  |  |  |
| 56 |  |  |  |  |  |  | 121 |  |  |  |  |  |
| 57 |  |  |  |  |  |  | 122 |  |  |  |  |  |
| 58 |  |  |  |  |  |  | 123 |  |  |  |  |  |
| 59 |  |  |  |  |  |  | 124 |  |  |  |  |  |
| 60 |  |  |  |  |  |  | 125 |  |  |  |  |  |
| 61 |  |  |  |  |  |  | 126 |  |  |  |  |  |
| 62 |  |  |  |  |  |  | 127 |  |  |  |  |  |
| 63 |  |  |  |  |  |  | 128 |  |  |  |  |  |
| 64 |  |  |  |  |  |  | 129 |  |  |  |  |  |
| 65 |  |  |  |  |  |  | 130 |  |  |  |  |  |

CONTENTS

1.0	INTRODUCTION	4

2.0	Scope	4

3.0	NORMATIVE REFERENCE	4

3.1	Local Codes and Standards	4

3.2	International Codes and Standards	4

3.3	The Project Documents	5

4.0	Material properties	5

5.0	Computer software	5

6.0	Geometry	6

7.0	DESIGN LOAD	6

7.1	Ds (Total Dead Load of Structure and Foundation & Soil overburden)	7

7.2	De (Total dead load of tank)	8

7.3	F (Normal Fluid Load)	9

7.4	HT (Test Fluid Load)	11

7.5	E (Earthquake Load)	12

7.6	W (Wind Load)	12

8.0	Design Load Combinations	13

9.0	Tank ANALYSIS AND DESIGN	16

9.1	Tank geometry	16

9.2	Tank Design Results	16

10.0	ATTACHMENTS	27

10.1	SOWFTWARE FILE	27

10.2	MECHANICAL DATA SHEET	28

10.3	MECHANICAL CALCULATION	29

INTRODUCTION

Binak oilfield in Bushehr province is a part of the southern oilfields of Iran, is located 20 km northwest of Genaveh city.

With the aim of increasing production of oil from Binak oilfield, an EPC/EPD Project has been defined by NIOC/NISOC and awarded to Petro Iran Development Company (PEDCO). Also PEDCO (as General Contractor) has assigned the EPC-packages of the Project to "Hirgan Energy - Design and Inspection" JV.

- Scope

This report covers design of Fire Water Storage Tanks (TK-2301A/B). The calculation of foundation is performed using “SAP” software.

- NORMATIVE REFERENCE

  - Local Codes and Standards

- INBC Part 6 “Iranian National Building Code

- INBC Part 7 “Iranian National Building Code

- INBC Part 9 “Iranian National Building Code

- INBC Part 10 “Iranian National Building Code

- Iranian Seismic Design Code for Petroleum Facilities(3rd edition)

  - International Codes and Standards

- ASCE 7-10 “Minimum Design Loads and Associated Criteria for Buildings and Other Structures-American Society of Civil Engineers”.

- ACI 318. “Building Code Requirements for Reinforced Concrete”, American Concrete Institute.

- AISC 358 “Prequalified Connections for Special and Intermediate Steel Moment Frames for Seismic Applications.” American Institute of Steel Construction, Inc.

- AISC 360 - “Specification for Structural Steel Buildings”. American Institute of Steel Construction, Inc.

  - The Project Documents

- BK-GNRAL-PEDCO-000-ST-SP-0001 SPECIFICATION FOR CONCRETE WORK

- BK-GNRAL-PEDCO-000-ST-DC-0001 Structural Design Criteria

- BK-GNRAL-PEDCO-000-CV-SP-0004 Specification For Earth Work

- BK-GCS-PEDCO-120-GT-RT-0001 Geotechnical Investigation Report for Compressor Station

- Material properties

Material properties are delivered in the following table.

| Material properties |  |
| --- | --- |
| Structure and Foundation concrete | F’c=300kg/cm²(28 days cylindrical sample) |
| Long. Reinforcement | Fy=4000 kg/cm² (AIII) |
| Trans. Reinforcement | Fy=4000 kg/cm² (AIII) |

- Computer software

Computer’s Software, which is used in structure and foundation analysis and design, are defined in the following table.

| Computer software |  |
| --- | --- |
| analysis and design of structure and foundation | SAP 20.1.0 |

- Geometry

D02

- foundation and pedestal plan for TK-2301-A

- foundation and pedestal plan for TK-2301-B

- DESIGN LOAD

  - Load case for tank foundation design

The loads that apply on the foundation, according to tank design report (annex I), are as following:

| Empty Weight: | 45283 kg |
| --- | --- |
| Operating Weight: | 1085283 kg |
| Hydro test Weight: | 1085283 kg |
| Wind Shear: | 110468 N |
| Wind Moment: | 716860 N.m |
| Seismic Shear: | 1151613 N |
| Seismic Moment: | 3679379 N.m |

  - Ds (Total Dead Load of Structure and Foundation & Soil overburden)

Soil overburden:

Inside of Ring wall = 1.85 × 1.5 = 2.78 t/m²

Outside of Ring wall = 1.85 × 0.9 = 1.67 t/m²

Top of Pedestal = +0.60

Top of Foundation= -0.90

Soil Pressure on Ring wall:

Ds = 0.5 × 1.85 × (1.5) = 1.40 ton/m²

- area surface pressure for ring wall (face top)

  - De (Total dead load of tank)

Weight of empty tank: 45.283 ton

Weight of bottom plate: 9.353 ton

Weight of roof plate: 11.98 ton

Weight of shell with roof: 45.283 + 11.98 = 57.265 ton

De = 57.265/40(joint) = 1.43 ton

- joint load on ring wall

D02

F (Normal Fluid Load)

Normal Fluid Load on ring foundation:

F = Ope load / area of ring foundation → area of ring foundation: (𝜋 × 13²)/4- (𝜋 × 11²)/4 = 95 m2 → 1085283/ 95 = 11.42 ton/m²

Soil Pressure Due to Normal Fluid Load on Ring wall:

F = 11.42 × (Kₒ = 0.5) = 5.71 t/m²

- Area uniform F load on the inside ring foundation

- Area uniform F load on the ring wall

  - HT (Test Fluid Load)

Test Load on ring foundation:

HT = Hydro test load / area of ring foundation → area of ring foundation: (𝜋 × 13²)/4- (𝜋 × 11²)/4 = 95 m2 → 1085283/ 95 = 11.42 ton/m²

D02

Soil Pressure Due to Test Fluid Load on Ring wall:

HT = 11.42 × (Kₒ = 0.5) = 5.71 t/m²

- area uniform HT load on the inside ring foundation

- area uniform HT load on the ring wall

  - E (Earthquake Load)

Shear load = 1151613 N (based on Mechanical Data Sheet for fire water storage Tanks (TK-2301 A/B).

This shear is based on the datasheet, but we used API650 with ASD behavior coefficient so its value is multiplied by 1.4 → 1151613  1.4 = 1612258 N

Moment = 3679379 N.m (based on Mechanical Data Sheet for fire water storage Tanks (TK-2301 A/B).

This moment is based on the datasheet, but we used API650 with ASD behavior coefficient so its value is multiplied by 1.4 → 3679379  1.4 = 5151131 N.m

D02

- Earthquake Load (EX)

  - W (Wind Load)

Shear load = 110468 N (based on Mechanical Data Sheet for fire water storage Tanks (TK-2301 A/B).

This shear is based on the datasheet, but we used API650 with ASD behavior coefficient so its value is multiplied by 1.4 → 110468  1.4 = 154655 N

Moment = 716860 N.m (based on Mechanical Data Sheet for fire water storage Tanks (TK-2301 A/B).

This moment is based on the datasheet, but we used API650 with ASD behavior coefficient so its value is multiplied by 1.4 → 716860  1.4 = 1003604 N.m

- Wind load (WX)

- Design Load Combinations

| Load Assignments |  |  |  |
| --- | --- | --- | --- |
| Case | LoadType | LoadName | LoadSF |
| Text | Text | Text | Unitless |
| A.A.O.1-NL | Load pattern | DE | 1 |
|  | Load pattern | DL | 1 |
|  | Load pattern | DS | 1 |
|  | Load pattern | F | 1 |
| A.A.O.2-NL | Load pattern | DE | 1 |
|  | Load pattern | DL | 1 |
|  | Load pattern | DS | 1 |
|  | Load pattern | F | 1 |
|  | Load pattern | WX | 1 |
| A.B.T.1-NL | Load pattern | DL | 1 |
|  | Load pattern | DE | 1 |
|  | Load pattern | DS | 1 |
|  | Load pattern | HT | 1 |
|  | Load pattern | WX | 0.25 |
| A.B.T.2-NL | Load pattern | DL | 0.6 |
|  | Load pattern | DE | 0.6 |
|  | Load pattern | DS | 0.6 |
|  | Load pattern | HT | 0.6 |
|  | Load pattern | WX | 0.25 |
| A.C.E.1-NL | Load pattern | DL | 1 |
|  | Load pattern | DE | 1 |
|  | Load pattern | DS | 1 |
|  | Load pattern | WX | 1 |
| A.C.E.2-NL | Load pattern | DL | 0.6 |
|  | Load pattern | DE | 0.6 |
|  | Load pattern | DS | 0.6 |
|  | Load pattern | WX | 1 |
| A.D.E.1-NL | Load pattern | DL | 1 |
|  | Load pattern | DS | 1 |
|  | Load pattern | DE | 1 |
|  | Load pattern | F | 1 |
|  | Load pattern | EX | 0.7 |
| A.D.E.2-NL | Load pattern | DL | 0.6 |
|  | Load pattern | DS | 0.6 |
|  | Load pattern | DE | 0.6 |
|  | Load pattern | F | 0.6 |
|  | Load pattern | EX | 0.7 |
| S.A.O.1-NL | Load pattern | DL | 1.4 |
|  | Load pattern | DS | 1.4 |
|  | Load pattern | DE | 1.4 |
|  | Load pattern | F | 1.4 |
| S.A.O.2-NL | Load pattern | DL | 1.2 |
|  | Load pattern | DS | 1.2 |
|  | Load pattern | DE | 1.2 |
|  | Load pattern | F | 1.2 |
|  | Load pattern | WX | 1 |
| S.A.O.3-NL | Load pattern | DL | 0.9 |
|  | Load pattern | DS | 0.9 |
|  | Load pattern | DE | 0.9 |
|  | Load pattern | F | 0.9 |
|  | Load pattern | WX | 1 |
| S.B.T.1-NL | Load pattern | DL | 1.2 |
|  | Load pattern | DE | 1.2 |
|  | Load pattern | DS | 1.2 |
|  | Load pattern | HT | 1.2 |
|  | Load pattern | WX | 0.25 |
| S.B.T.2-NL | Load pattern | DL | 0.9 |
|  | Load pattern | DE | 0.9 |
|  | Load pattern | DS | 0.9 |
|  | Load pattern | HT | 0.9 |
|  | Load pattern | WX | 0.25 |
| S.C.E.1-NL | Load pattern | DE | 1.2 |
|  | Load pattern | DL | 1.2 |
|  | Load pattern | DS | 1.2 |
|  | Load pattern | WX | 1 |
| S.C.E.2-NL | Load pattern | DE | 0.9 |
|  | Load pattern | DL | 0.9 |
|  | Load pattern | DS | 0.9 |
|  | Load pattern | WX | 1 |
| S.D.E.1-NL | Load pattern | DE | 1.2 |
|  | Load pattern | DL | 1.2 |
|  | Load pattern | DS | 1.2 |
|  | Load pattern | F | 1.2 |
|  | Load pattern | EX | 1 |
| S.D.E.2-NL | Load pattern | DE | 0.9 |
|  | Load pattern | DL | 0.9 |
|  | Load pattern | DS | 0.9 |
|  | Load pattern | F | 0.9 |
|  | Load pattern | EX | 1 |

- Tank ANALYSIS AND DESIGN

  - Tank geometry

As noted before, the structure has modelled and analysed by SAP2000. This figure shows a 3D view of the model in software.

- 3D model

  - Tank Design Results

Soil Pressure Control

Soil pressures in different service load combinations should be checked by allowable value. The following figure is extracted from “SAP” model.

According to Geotechnical report Ks = 0.73 Kg/cm³ ,allowable settlement = 2.5 cm and  Max soil pressure for this foundation is 2.00 Kg/cm², in this foundation maximum existing settlement is 1.64 cm and maximum existing stress is about 1.50 Kg/cm² .

Soil pressure

D02

According to Geotechnical report allowable soil pressure in mat foundation (middle of tank) is 0.88 Kg/cm²

In this foundation maximum soil pressure is:

Qliquid<Qall(Circular Mat)

(Operation load / tank area) 1085283/ 1372587.32=0.79 Kg/cm²  < 0.88 Kg/cm²

Displacement check

Based on SAP2000 output the maximum deflection in foundation is 0.41 cm and the maximum drift is 1.64 cm.

| TABLE: Joint Displacements |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Joint | OutputCase | CaseType | StepType | U1 | U2 | U3 |
| Text | Text | Text | Text | cm | cm | cm |
| 1 | ENV A | Combination | Max | 0 | 0 | -0.456155 |
| 1 | ENV A | Combination | Min | 0 | 0 | -1.425239 |
| 2 | ENV A | Combination | Max | 0 | 0 | -0.45562 |
| 2 | ENV A | Combination | Min | 0 | 0 | -1.424702 |
| 7 | ENV A | Combination | Max | 0 | 0 | -0.454027 |
| 7 | ENV A | Combination | Min | 0 | 0 | -1.423111 |
| 8 | ENV A | Combination | Max | 0 | 0 | -0.446368 |
| 8 | ENV A | Combination | Min | 0 | 0 | -1.427256 |
| 9 | ENV A | Combination | Max | 0 | 0 | -0.460501 |
| 9 | ENV A | Combination | Min | 0 | 0 | -1.417767 |
| 12 | ENV A | Combination | Max | 0 | 0 | -0.451417 |
| 12 | ENV A | Combination | Min | 0 | 0 | -1.420499 |
| 13 | ENV A | Combination | Max | 0 | 0 | -0.444266 |
| 13 | ENV A | Combination | Min | 0 | 0 | -1.425154 |
| 14 | ENV A | Combination | Max | 0 | 0 | -0.457409 |
| 14 | ENV A | Combination | Min | 0 | 0 | -1.414675 |
| 17 | ENV A | Combination | Max | 0 | 0 | -0.447852 |
| 17 | ENV A | Combination | Min | 0 | 0 | -1.416937 |
| 18 | ENV A | Combination | Max | 0 | 0 | -0.44139 |
| 18 | ENV A | Combination | Min | 0 | 0 | -1.422279 |
| 19 | ENV A | Combination | Max | 0 | 0 | -0.453176 |
| 19 | ENV A | Combination | Min | 0 | 0 | -1.410442 |
| 22 | ENV A | Combination | Max | 0 | 0 | -0.443422 |
| 22 | ENV A | Combination | Min | 0 | 0 | -1.412505 |
| 23 | ENV A | Combination | Max | 0 | 0 | -0.437821 |
| 23 | ENV A | Combination | Min | 0 | 0 | -1.41871 |
| 24 | ENV A | Combination | Max | 0 | 0 | -0.447925 |
| 24 | ENV A | Combination | Min | 0 | 0 | -1.405191 |
| 27 | ENV A | Combination | Max | 0 | 0 | -0.438235 |
| 27 | ENV A | Combination | Min | 0 | 0 | -1.407319 |
| 28 | ENV A | Combination | Max | 0 | 0 | -0.433637 |
| 28 | ENV A | Combination | Min | 0 | 0 | -1.414526 |
| 29 | ENV A | Combination | Max | 0 | 0 | -0.441768 |
| 29 | ENV A | Combination | Min | 0 | 0 | -1.399034 |
| 32 | ENV A | Combination | Max | 0 | 0 | -0.432419 |
| 32 | ENV A | Combination | Min | 0 | 0 | -1.401501 |
| 33 | ENV A | Combination | Max | 0 | 0 | -0.42895 |
| 33 | ENV A | Combination | Min | 0 | 0 | -1.409839 |
| 34 | ENV A | Combination | Max | 0 | 0 | -0.434871 |
|  |  |  |  |  | MAX | -1.427256 |

D02

D02

Reinforcing

Hoop tension control

Ph=k0hQliquid+0.5k0Ɣh2=0.5*2.1*8.18+0.5*0.5*1.85*2.12=10.62 T/m

T HOOP=PHD/2=10.62*13/2=69 T

T HOOP=As Fy= As= THOOP /Fy =69000/4000=17.25 cm

Use 10T16        As=20                          OK

Dowel reinforcement of ring wall

AS≥(0.75FuA)anchorφFyrein.=0.75*4000*3.1415*3*340.9*4000=5.89

Use T16@200       As=20.00                         OK

Foundation reinforcement

According to ACI-318-08:

AS,min=0.0018×60×100=10.8cm2 for top and bottom 
→ If use Φ 12@200 → A = 5.65cm² → 5.65 cm² ≤ 10.8/2 = 5.4 cm² → ok

- Foundation reinforcement plan

fc=300  kg/cm²

fy=4000  kg/cm²

φ=0.9

As used=T12@200=5.6cm²

cover=75mm

h=600 mm

a=Asfy0.85bfc'=5.6*40000.85*100*300=0.9cm

Mn=0.9×5.6×4000×50.1=10.1 ton.m

- M11 Max

- M11 Min

- M22 Max

- M22 Min

- V3-3 EX

- V3-3 WX

- ATTACHMENTS

  - SOWFTWARE FILE

“SAP” software file is attached.

  - MECHANICAL DATA SHEET

Mechanical data sheet is attached.

  - MECHANICAL CALCULATION

Mechanical calculation file is attached.