## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-IN-DT-0009 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-2477 |  |  | Transmital Date: 11/11/2023
Document Title: Data Sheets For Pressure & Safety Relief Valves |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-IN-TR-2477 |  |  | Transmital Date: 11/11/2023
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-IN-DT-0009_D03 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
Instrument Comments
1 | با توجه به اینکه مطابق مدارک سازنده ، فشار طراحی بیان شده برای کمپرسور 24.5 barg در نظر گرفته شده است بنابراین لازم است یکسان سازی مدارک برای PSV های ذیر انجام پذیرد: PAV-2121A/B/Cو PSV-2131 A/B/C |  | 1402-2294-432218 | 1402/10/23 | مطابق آخرین P&ID سازنده کمپرسور فشار معادل 22 barg در نظرگرفته شد.
2 | VESSEL NO. برای تجهیزات زیر قید شود: TSV-2281, PSV-2293, PSV-2271, PSV-2211 |  | 1402-2294-432218 | 1402/10/23 | مطابق خواست کارفرمای محترم اصلاح شد.
3 | همانطور که در ویرایش پیشین مدرک اعلام شده است، در خصوص متریال اعلام شده تطابق مشخصات با PMS تایید شده الزامی است. در ضمن با توجه به اینکه تعیین نهایی متریال با سازنده میباشد ضروری است در مرحله TBEدر خصوص جنس شفاف سازی گردد. |  | 1402-2294-432218 | 1402/10/23 | موارد با PMS پروژه و برای موارد داخلی شیر با SPEC همخوانی دارد. مطابق خواست کارفرمای محترم در مرحله TBEدر خصوص جنس موارد نهایی می گردد.
kr
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: |  |  |  |  | Date: