## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-ME-DT-0017 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1592 |  |  | Transmital Date: 11/19/2022
Document Title: Mechanical Data Sheets For Fire Water Storage Tank |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-ME-TR-1592 |  |  | Transmital Date: 11/19/2022
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-ME-DT-0017_D01 |  |  | CRS Status:
| Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | میزان خوردگی مجاز پس از نهایی شدن مطالعات خوردگی قابل استناد خواهد بود. |  | 1401-2294-402149 | 1401/10/21 | میزان خوردگی مجار مطابق بند 10.3.6 مدرک خوردگی که تایید شده است در نظر گرفته شده است.
2 | مبنای درج پیش آمدگی نازلهای مخزن مشخص گردد. |  | 1401-2294-402149 | 1401/10/21 | مقدار پیش آمدگی نازلها بر اساس STANDARD DRAWING تصحیح گردید.
3 | همان گونه که در نامه شماره 01/2294/175140 بیان گردید، یادداشت شماره 12 با آخرین ویرایش استاندارد IPS-E-SF-400(1) مطابقت ندارد و می بایست اصلاح / حذف گردد. |  | 1401-2294-402149 | 1401/10/21 | یادداشت شماره 12 حذف شد.
4
5
6
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: |  |  |  |  | Date: