## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-PR-PI-0015 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-2414 |  |  | Transmital Date:10/9/2023
Document Title: P&ID - Instrument & Plant Air System |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-PR-TR-2414 |  |  | Transmital Date: 10/9/2023
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-PEDCO-120-PR-PI-0015_D07 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | با توجه به سایز شیر PCV-2201، در بالا دست و پایین دست آن، Reducer/Expander در نظر گرفته شود. |  | BK-SUR-ENG-PCS-02-08653 | 2023-10-23 | اصلاح گردید.
2 | شیب خط خروجی از PSV-2201 درج گردد. |  | BK-SUR-ENG-PCS-02-08653 | 2023-10-23 | برای این خط نیازی به در نظر گرفتن شیب نمی باشد زیرا خروجی این خط به اتمسفر بوده و علاوه بر این، این خط خروجی Air Dryer بوده و Low Point ای ندارد.
3 | ایراد Drafting خط شماره 0002 در صفحه دوم اصلاح گردد. |  | BK-SUR-ENG-PCS-02-08653 | 2023-10-23 | اعمال گردید.
4 | ضروريست نقطه نظرات ذينفع اصلي در خصوص اين مدرك اعمال گردد. |  | BK-SUR-ENG-PCS-02-08653 | 2023-10-23 | اعمال گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: |  |  |  |  | Date: