## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-EL-PY-0008 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-2034 |  |  | Transmital Date: 4/16/2023
Document Title: Electrical Equipment Arrangement Layout For Building |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-EL-TR-2034 |  |  | Transmital Date: 4/16/2023
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-EL-PY-0008_D02 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | با توجه به نهایی نشدن ظرفیت دستگاه UPS، ضروری است پس از تأیید مدرک مصارف بارهای ابزاردقیق و تعیین ظرفیت واقعی سیستم UPS و مشخص شدن ابعاد rack باتریها، مدرک متناسب با نگهدارنده های باتری بازنگری گردد. |  | 1402-2294-68108 | 1402/02/25 | محاسبات جدید سیستم UPS با ترسنیمتال شماره 2538 ارسال شده است. در این محاسبات طول باتری ها از 9 متر به مقدار نشان داده شده کاهش یافته است. همچنین مطابق با محاسبات ترنسمتال شماره 2136 ابعاد باتریهای DC در نظر گرفته شده است.
2 | پیشنهاد می شود، به جای استفاده از Rack باتری به صورت یکپارچه به طول 9 متر، و اشغال تمام طول اتاق، نگهدارنده باتری به دو بخش 4.5 متری تقسیم و در عرض اتاق جانمایی گردند. |  | 1402-2294-68108 | 1402/02/25 | اعمال گردید.
3 | تجهیز شماره 12 مربوط به نماد بانک خازنی فشار ضعیف، به دو بخش مجزا تقسیم و نمایش داده شود. |  | 1402-2294-68108 | 1402/02/25 | مطابق با این نقشه، بانک خازنی از دو طرف نیاز به دسترسی دارد. در صورتیکه اگر بانک سوییچگیر A و B از هم جدا گردد، دسترسی برای چهار طرف باید منظور گردد، لذا در حال حاضر و قبل از دریافت پیشنهادات فنی تابلوسازان LV و به علت محدودیت جا، بهتر آن است به همین روش پیش رفت. ولی در آینده و پس از جانمایی دقیق، امکان جداسازی آن وجود دارد.
4 | در صورت ادغام ساختمان کنترل جدید در ساختمان کنترل موجود لازم است بخش مربوط به روزرسانی و اصلاح گردد. |  | 1402-2294-68108 | 1402/02/25 | معماری جدید ساختمان کنترل توسعه ای که با ترنسمیتال شماره 2617 ارسال شده، لحاظ شده است.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: |  |  |  |  | Date: