## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-HV-DG-0003 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1051 |  |  | Transmital Date: 6/7/2022
Document Title: HVAC Flow Diagram For Extension of Existing Elect. Building |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-HV-TR-1051 |  |  | Transmital Date: 6/7/2022
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-PEDCO-120-HV-DG-0003_D00 |  |  | CRS Status:
| Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | in calculation document , infilatration air had considered for capacitor bank, but here air come inside through a duct split unit , which design methode is correct? Based on correct design one of two document shall modify (however for pressurizing room infiltration method can not acceptable) |  | BK-SUR-ENG-HVC-01-04921 | 2022-06-29 | HVAC documents for extension of existing elect. Building, revised based on final heat dissipation data and final architectural design and details.
2 | refer to item 1 , if infiltation air considered for design PRD is not applicable, otherwise room pressure set point shall mention |  | BK-SUR-ENG-HVC-01-04921 | 2022-06-29
3 | to add tag number for STL and PRD (if it is applicable) |  | BK-SUR-ENG-HVC-01-04921 | 2022-06-29
4 | according to equipment layout SUI ,SUO -03C shall correct to 04 |  | BK-SUR-ENG-HVC-01-04921 | 2022-06-29
5 | split out door units shall show |  | BK-SUR-ENG-HVC-01-04921 | 2022-06-29
6 | load for duct split has not determined in calculation load |  | BK-SUR-ENG-HVC-01-04921 | 2022-06-29
7 | one of sand trap (and inlet air) for capacitor bank shall remove |  | BK-SUR-ENG-HVC-01-04921 | 2022-06-29
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: |  |  |  |  | Date: