## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-HV-CN-0002_D02 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1814 |  |  | Transmital Date:01/23/2023
Document Title: HVAC Calculation Note For Extension of Existing Elect. Building |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-HV-TR-1814 |  |  | Transmital Date:01/23/2023
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-PEDCO-120-HV-CN-0002_D02 |  |  | CRS Status:
| Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | Repeat: to explain reason why for roof and external walls insulation has not considered. Refer to page 8 of 20, for 200 mm polystyrene block R is between 3.57 and 5.3 m2.K/W. |  | BK-SUR-ENG-HVC-01-06857 | 2023-02-01 | HVAC calculation note revised based on final architectural design and details.
2 | since outdoor design temperature for select of equipment is 500C , in compare to standard cooling capacity rating based on 35 0C/27 0C , for 22-SUI-02A,B ,2x2400BTU/H is not sufficient , change to two30000 BTU/H. |  | BK-SUR-ENG-HVC-01-06857 | 2023-02-01 | HVAC calculation note revised based on final heat dissipation data and final architectural design and details.
3 | battery room shall be maitained about 240C, and cooling load for this area shall be considered. |  | BK-SUR-ENG-HVC-01-06857 | 2023-02-01 | Due to scope of contract, design and construct extension of existing building shall be considered whereas battery room is in existing limit.
4 | 100% reduandancy for HVAC systems inside battery room shall be considered including exhaust fan, cooling system... |  | BK-SUR-ENG-HVC-01-06857 | 2023-02-01 | Due to scope of contract, design and construct extension of existing building shall be considered whereas battery room is in existing limit.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: Ah.Behbahani | Signature | H.Naserizadeh |  |  | Clarified By: | Signature
| Date: 02/01/2023 |  |  |  |  | Date: