## Cover
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEET FOR ORIFICE PLATE / RESTRICTION ORIFICE
شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 8
9184 – 073 - 053 |  |  | BK |  | GCS | PEDCO | 120 |  | IN | DT | 0013 | D02
طرح نگهداشت و افزایش تولید 27 مخزن
DATA SHEET FOR ORIFICE PLATE / RESTRICTION ORIFICE نگهداشت و افزایش تولید میدان نفتی بینک
D02 |  | MAR.2024 |  | IFA |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | S.Faramarzpour
D01 |  | JUN.2023 |  | IFA |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | A.M.Mohseni
D00 |  | JUL.2022 |  | IFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
Class: 1 |  |  |  | CLIENT Doc. Number: F9Z-708934
status: | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved

## REVISION
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEET FOR ORIFICE PLATE / RESTRICTION ORIFICE
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 8
9184 – 073 - 053 |  |  | BK | GCS |  | PEDCO | 120 | IN | DT | 0013 |  | D02
REVISION RECORD SHEET
Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D01 |  | D02 | D03 | D04
1 | X | X | X | [5 empty] | 65
2 | X | X | X | [5 empty] | 66
3 | X | X | [6 empty] | 67
4 | X |  | X | [5 empty] | 68
5 | X | X | [6 empty] | 69
6 | X | X | X | [5 empty] | 70
7 | X | X | [6 empty] | 71
8 | X | X | X | [5 empty] | 72
9 | [8 empty] | 73
10 | [8 empty] | 74
11 | [8 empty] | 75
12 | [8 empty] | 76
13 | [8 empty] | 77
14 | [8 empty] | 78
15 | [8 empty] | 79
16 | [8 empty] | 80
17 | [8 empty] | 81
18 | [8 empty] | 82
19 | [8 empty] | 83
20 | [8 empty] | 84
21 | [8 empty] | 85
22 | [8 empty] | 86
23 | [8 empty] | 87
24 | [8 empty] | 88
25 | [8 empty] | 89
26 | [8 empty] | 90
27 | [8 empty] | 91
28 | [8 empty] | 92
29 | [8 empty] | 93
30 | [8 empty] | 94
31 | [8 empty] | 95
32 | [8 empty] | 96
33 | [8 empty] | 97
34 | [8 empty] | 98
35 | [8 empty] | 99
36 | [8 empty] | 100
37 | [8 empty] | 101
38 | [8 empty] | 102
39 | [8 empty] | 103
40 | [8 empty] | 104
41 | [8 empty] | 105
42 | [8 empty] | 106
43 | [8 empty] | 107
44 | [8 empty] | 108
45 | [8 empty] | 109
46 | [8 empty] | 110
47 | [8 empty] | 111
48 | [8 empty] | 112
49 | [8 empty] | 113
50 | [8 empty] | 114
51 | [8 empty] | 115
52 | [8 empty] | 116
53 | [8 empty] | 117
54 | [8 empty] | 118
55 | [8 empty] | 119
56 | [8 empty] | 120
57 | [8 empty] | 121
58 | [8 empty] | 122
59 | [8 empty] | 123
60 | [8 empty] | 124
61 | [8 empty] | 125
62 | [8 empty] | 126
63 | [8 empty] | 127
64 | [8 empty] | 128

## REFERENCE
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEET FOR ORIFICE PLATE / RESTRICTION ORIFICE
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 3 از 8
9184 – 073 - 053 |  |  | BK | GCS | PEDCO | 120 | IN | DT | 0013 | D02
REFERENCE DOCUMENTS :
|  | Specification For Instrumentation | [6 empty] | BK-GNRAL-PEDCO-000-IN-SP-0001
|  | Process Basis Of Design | [6 empty] | BK-GNRAL-PEDCO-000-PR-DB-0001
|  | Piping Material Specification | [6 empty] | BK-GCS-PEDCO-120-PI-SP-0001
|  | Instrument & Control System Design Criteria | [6 empty] | BK-GCS-PEDCO-120-IN-DC-0002
|  | Symbol & Legend For PFD and P&ID | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0001
|  | P&ID - Gas Compression Inlet Gas Pipeline (Binak) | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0002
|  | P&ID - Gas Compression Inlet Gas Pipeline (Golkhari) | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0003
|  | P&ID - Slug Catcher System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0004
|  | P&ID - Gas Compression Inlet Knock Out Drum | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0005
|  | P&ID - 1st Stage Gas Compression Suction Drums | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0006
|  | P&ID - 1st Stage Gas Compression Compressors | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0007
|  | P&ID - 1st Stage Gas Compression Air Coolers | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0008
|  | P&ID - 2nd Stage Gas Compression Suction Drums | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0009
|  | P&ID - 2nd Stage Gas Compression Compressors | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0010
|  | P&ID - 2nd Stage Gas Compression Air Coolers | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0011
|  | P&ID - 2nd Stage Gas Compression Discharge Drum | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0012
|  | P&ID - Gas Compression Dehydration Package | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0013
|  | P&ID - Lean Glycol Storage Tank | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0014
|  | P&ID - Instrument & Plant Air System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0015
|  | P&ID - Nitrogen Generation System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0016
|  | P&ID - Close Drain System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0017
|  | P&ID - Corrosion Inhibitor Package | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0018
|  | P&ID - Methanol Injection Package | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0019
|  | P&ID - LP Flare System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0020
|  | P&ID - Oily Water Sewer | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0021
|  | P&ID - Fuel Gas System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0022
|  | P&ID - Diesel Oil System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0023
|  | P&ID - Potable Water System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0024
|  | P&ID - Glycol Sump Drum | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0025
|  | P&ID - Fire Water Network | [6 empty] | BK-GCS-PEDCO-120-SA-PI-0001
|  | P&ID - Total Flooding System For Extension of Existing Elect. Building | [6 empty] | BK-GCS-PEDCO-120-SA-PI-0002

## Notes
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEET FOR ORIFICE PLATE / RESTRICTION ORIFICE
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 4 از 8
9184 – 073 - 053 |  |  |  | BK | GCS | PEDCO | 120 | IN | DT | 0013 | D02
GENERAL NOTES:
1. Orifice plate and restriction orifice plates shall be stamped with manufacturer's name, tag no., bore size, line size/rating, plate material , plate thickness and the word 'upstream' on the upstream side of the paddle.
2. Bore sizing shall be done as per the full scale flow rate.
3.The calculation for orifice plates shall be produced in accordance with ISO 5167.
4. Data sheets shall be submitted for approval by purchaser. The orifice bore diameter shall be as per vendor's approved calculations.
5. Vendor shall provide certificate of compliance to NACE MR-0175 requirement for the instrument supplied, wherever specified.
6. Beta ratio limits shall be 0.2 to 0.7 For some cases where there is constraint vendor can size for beta ratio of More than 0.7 but however the beta ratio shall not exceed 0.75 as per ISO 5167. The orifice plate thickness shall be As per manufacturer's standard, however as a minimum shall be to ISO 5167 requirements
7. Vendor shall supply the orifice plate assembly complete with flanges, gasket, bolt&nuts and jack screws. All orifice flanges shall be as per ANSI B16.5 and orifice plates shall be supplied suitable for the same. Wherever 'FF' flange facing is indicated, the orifice plates shall be suitable for mounting between the flat faced flanges.
8. Orifice bore shall not be beveled for the restriction orifice plates.
9. IPS-D-IN-103 regarding Orifice Plate Fabrication to be followed by vendor.
10. Max acceptable noise level for orifice and restriction orifice plate is 85 dbA in 1m.
11. Environmental condition for field instrumentation of Binak Oilfield shall be considered as per the followings:
Maximum ambient temperature: 50 (°C) Minimum ambient temperature: 5 (°C) Maximum steel surface exposed to sun: 85 (°C) Maximum summer dry bulb: 50 (°C) DB/RH for Summer HVAC Design: 41 °C / 61 % DB FOR Winter HVAC Design: 6 °C
Relative Humidity:
• Maximum Design relative humidity (%): 100 • Minimum Design relative humidity (%): 0
12. Necessity of considering multi-stage or multi-hole restriction orifice will be specified after detailed calculation by Vendor.
13. Multi-stage restriction orifice shall be ready to install flanged spool type.
14. Plate thickness for restriction orifice shall be specified by Vendor. However, minimum plate thickness specified in ISO 5167 shall be followed.
D02

## FE
نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEET FOR ORIFICE PLATE / RESTRICTION ORIFICE
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 5 از 8
9184 – 073 - 053 |  |  | BK | GCS | PEDCO | 120 | IN | DT | 0013 | D02
FLOW ELEMENT (ORIFICE PLATE)
GENERAL |  | 1 | Tag No. | [5 empty] | SEE PAGE 6
|  | 2 | P&ID No. |  |  | Service |  |  | SEE PAGE 6 |  |  | SEE PAGE 6
|  | 3 | Line Size |  |  | Schedule |  |  | SEE PAGE 6 |  |  | SEE PAGE 6
|  | 4 | Piping Class | [5 empty] | SEE PAGE 6
|  | 5 | Nace Requirements | [5 empty] | SEE PAGE 6
6
PROCESS CONDITION |  | 7 | Fluid |  |  | Phase |  |  | SEE PAGE 6 |  |  | SEE PAGE 6
|  | 8 | Design Temperature |  |  | Operating Temperature |  | (°C) | SEE PAGE 6 |  |  | SEE PAGE 6
|  | 9 | Design Pressure |  |  | Operating Pressure |  | (bar-g) | SEE PAGE 6 |  |  | SEE PAGE 6
|  | 10 | Minimum Flow Rate |  |  | Normal Flow Rate |  | (kg/h) | SEE PAGE 6 |  |  | SEE PAGE 6
|  | 11 | Maximum Flow Rate |  |  |  |  | (kg/h) | SEE PAGE 6
|  | 12 | Density |  | (kg/m3) | Molecular Weight |  |  | SEE PAGE 6 |  |  | SEE PAGE 6
|  | 13 | Viscosity |  |  | Gas Compressibility Factor |  |  | SEE PAGE 6 |  |  | SEE PAGE 6
|  | 14 | Limit On Pressure Drop Across Flowmeter |  |  |  |  | (bar) | SEE PAGE 6
|  | 15 | Cp / Cv |  |  | Allowable Press. Drop |  |  | SEE PAGE 6 |  |  | SEE PAGE 6
|  | 16 | Liquid Vapor Pressure |  |  |  |  | (bara) | SEE PAGE 6
ORIFICE PLATE |  | 17 | Type |  |  | Sub Type |  |  | Sharp Edge Orifice |  |  | Concentric with Flange Tappings
|  | 18 | Material | [5 empty] | 316L S.S
|  | 19 | Flow Full Scale |  |  | Diff. Pressure Range |  |  | SEE PAGE 6 |  |  | SEE PAGE 6
|  | 20 | Construction Standard | [5 empty] | EN ISO 5167
|  | 21 | Plate Thickness | [5 empty] | SEE PAGE 6
|  | 22 | Bore Diameter | [5 empty] | SEE PAGE 6
|  | 23 | Beta Ratio (d/D) | [5 empty] | SEE PAGE 6
|  | 24 | Drain / Vent Hole | [5 empty] | Note 2
25
ORIFICE FLANGE |  | 26 | Flange Type | [5 empty] | Weld Neck Flanged Tap
|  | 27 | Flange Size | [5 empty] | SEE PAGE 6
|  | 28 | Flange Rating | [5 empty] | SEE PAGE 6
|  | 29 | Flange Facing | [5 empty] | SEE PAGE 6
|  | 30 | FlangeTapping Size | [5 empty] | 1/2" NPT
|  | 31 | Flange Material | [5 empty] | SEE PAGE 6
|  | 32 | Gasket Material | [5 empty] | Spiral Wound, Thick.4.45 mm ,SS316 Winding with Stainless Steel Inner and Outer Rings, Graphite Filler, RF(125-250 AARH), ASME B16.20
PURCHASING DATA |  | 33 | Model |  |  | Manufacture |  |  | Will Be Finalized Later |  |  | Will Be Finalized Later
|  | 34 | Supplier |  |  | Order |  |  | Will Be Finalized Later |  |  | Will Be Finalized Later
35
NOTES : | 1) | VTA :Vendor To Advice |  |  |  |  | VTC: VENDOR TO CONFIRM
| 2) | A weep hole flush at the bottom of the orifice run to be used for Gas Services and for liquid services at top of the pipe to
prevent a build-up of condensate. The hole size is 0.125 in and to be as per standard. (VTC)

## FE List
نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEET FOR ORIFICE PLATE / RESTRICTION ORIFICE
شماره پیمان: |  |  |  |  | پروژه |  | بسته کاری |  | صادرکننده |  |  | تسهیلات |  | رشته |  |  | نوع مدرک |  | سریال |  |  | نسخه |  |  | شماره صفحه: 6 از 8
9184 – 073 - 053 |  |  |  |  | BK |  | GCS |  | PEDCO |  |  | 120 |  | IN |  |  | DT |  | 0013 |  |  | D02
FLOW ELEMENT (ORIFICE PLATE)
Rev. | Item No. | Tag No. | P&ID No. | Service | Line Size | Schedule / C.A | Piping Class | Nace | Fluid | Phase | Temperature (°C) |  | Pressure (barg) |  | Flow Rate (Kg/h) |  |  | Density (Kg/m3) (Mix./Liq./Ga) | Specific Gravity (Mix) | Molecular Weight(Kg/Kgmol) | Viscosity(CP) (Gas/Liquid) | Gas Compressibility Factor | Cp / Cv | Liquid Vapor Pressure (barg) | Max. Diff. Pressure Range (mbarg) | Min Plate Thickness (mm) (VTC) | Bore Diameter (mm) (VTC) | Beta Ratio (d/D) (VTC) | Flange Size | Flange Rating/Facing | Flange Material | Remark
[11 empty] | Design | Operating | Design | Operating | Min. | Normal | Max.
D02 | 1 | FE-2101 | BK-GCS-PEDCO-120-PR-PI-0002 | Gas Compression Inlet Gas Pipeline (Binak) | 6" | 80 / 6mm | AN07 | YES | HC | G | 85 | 46.11 | 18.2 | 6.75 | - | 6564.084 | 7220.493 | 6.66 | 0.90897 | 26.36 | 0.011 | 0.97 | 1.225 | - | 250 | 3.2 | 66.8934 | 0.45714 | 6" | 300# , RF | ASTM A105
D02 | 2 | FE-2102 | BK-GCS-PEDCO-120-PR-PI-0003 | Gas Compression Inlet Gas Pipeline (Golkhari) | 8" | 100 / 6mm | FN07 | YES | HC | G | 175 | 32 | 90 | 6.75 | - | 11269.03 | 12395.93 | 6.214 | 0.81276 | 23.57 | 0.011 | 0.973 | 1.261 | - | 250 | 3.2 | 89.4412 | 0.4507 | 8" | 600# , RF | ASTM A105
D02 | 3 | FE-2111 | BK-GCS-PEDCO-120-PR-PI-0004 (3 of 3) | Slug Catcher System | 3" | 40 / 3mm | CN05 | YES | CONDESATE | L | 155 | 32 | 47.7 | 19.75 | - | 7160 | 7876 | 716 | 0.716 | 48 | 0.27 ~ 0.76 | - | 1.15 | 5.5 | 250 | 3.2 | 23.086 | 0.29626 | 3" | 300# , RF | ASTM A105
D02 | 4 | FE-2271 | BK-GCS-PEDCO-120-PR-PI-0022 | Fuel Gas System | 2" | 80 / 6mm | AN07 | YES | HC | G | 85 | 36.78 | 18.2 | 4.9 | - | 505.8 | 55638 | 5.9689 | 0.84552 | 24.52 | 0.011 | - | 1.245 | - | 250 | 3.2 | 21.4915 | 0.22115 | 2" | 300# , RF | ASTM A105
D02 | 5 | FE-2211 | BK-GCS-PEDCO-120-PR-PI-0016 | Nitrogen Header | 1" | 40 / 1mm | AN01 | No | NIT | G | 85 | 60 | 18.2 | 7.5 | - | 38.61 | 42.4939 | 9.4144 | 0.96621 | 28.02 | 0.01 | 0.99 | 1.398 | - | 250 | 3.2 | 5.3678 | 0.20146 | 2" | 300# , RF | ASTM A105 | Meter Run
| Note: | (1) HC:HYDROCARBONE , L: LIQUID , G: GAS , M: MIXED
(2) Vendor shall calculate the bore size & beta for 2 phase orifice plates.
(3) BLANK PLATE to be supplied. The bore shall be drilled later by others.
(4) Flange with 1/2" NPT tapping, gasket, bolts & nuts shall be supplied by instr. Vendor.
(5) No of holes per flange for orifice plates to be specified by vendor.
(6) C.A : Corossion Allowance
D02

## RO
نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEET FOR ORIFICE PLATE / RESTRICTION ORIFICE
شماره پیمان: |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 7 از 8
9184 – 073 - 053 |  | BK | GCS | PEDCO | 120 | IN | DT | 0013 | D02
FLOW ELEMENT (ORIFICE PLATE)
GENERAL | 1 | Tag No. | [5 empty] | SEE PAGE 8
| 2 | P&ID No. |  |  | Service |  |  | SEE PAGE 8 |  |  | SEE PAGE 8
| 3 | Line Size |  |  | Schedule |  |  | SEE PAGE 8 |  |  | SEE PAGE 8
| 4 | Piping Class | [5 empty] | SEE PAGE 8
| 5 | Nace Requirements | [5 empty] | SEE PAGE 8
6
PROCESS CONDITION | 7 | Fluid |  |  | Phase |  |  | SEE PAGE 8 |  |  | SEE PAGE 8
| 8 | Design Temperature |  |  | Operating Temperature |  | (°C) | SEE PAGE 8 |  |  | SEE PAGE 8
| 9 | Design Pressure |  |  | Operating Pressure |  | (bar-g) | SEE PAGE 8 |  |  | SEE PAGE 8
| 10 | Minimum Flow Rate |  |  | Normal Flow Rate |  | (kg/h) | SEE PAGE 8 |  |  | SEE PAGE 8
| 11 | Maximum Flow Rate |  |  |  |  | (kg/h) | SEE PAGE 8
| 12 | Density |  | (kg/m3) | Molecular Weight |  |  | SEE PAGE 8 |  |  | SEE PAGE 8
| 13 | Viscosity |  |  | Gas Compressibility Factor |  |  | SEE PAGE 8 |  |  | SEE PAGE 8
| 14 | Limit On Pressure Drop Across Flowmeter |  |  |  |  | (bar) | SEE PAGE 8
| 15 | Cp / Cv | [5 empty] | SEE PAGE 8
| 16 | Liquid Vapor Pressure |  |  |  |  | (bara) | SEE PAGE 8
ORIFICE PLATE | 17 | Type |  |  | Sub Type |  |  | Restriction Device |  |  | VTA
| 18 | Material | [5 empty] | 316L S.S
| 19 | Flow Full Scale |  |  | Diff. Pressure Range |  |  | SEE PAGE 8 |  |  | SEE PAGE 8
| 20 | Construction Standard | [5 empty] | EN ISO 5167
| 21 | Plate Thickness | [5 empty] | SEE PAGE 8
| 22 | Bore Diameter | [5 empty] | SEE PAGE 8
| 23 | Beta Ratio (d/D) | [5 empty] | SEE PAGE 8
| 24 | Drain / Vent Hole | [5 empty] | -
25
ORIFICE FLANGE | 26 | Flange Type | [5 empty] | BY Piping
| 27 | Flange Size | [5 empty] | SEE PAGE 8
| 28 | Flange Rating | [5 empty] | SEE PAGE 8
| 29 | Flange Facing | [5 empty] | SEE PAGE 8
| 30 | Flange Material | [5 empty] | SEE PAGE 8
| 31 | Gasket Material | [5 empty] | Spiral Wound, Thick.4.45 mm ,SS316 Winding with Stainless Steel Inner and Outer Rings, Graphite Filler, RF(125-250 AARH), ASME B16.20
32
PURCHASING DATA | 33 | Model |  |  | Manufacture |  |  | Will Be Finalized Later |  |  | Will Be Finalized Later
| 34 | Supplier |  |  | Order |  |  | Will Be Finalized Later |  |  | Will Be Finalized Later
35
NOTES : | VTA :VENDOR TO ADVISE
VTC: VENDOR TO CONFIRM

## RO List
نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEET FOR ORIFICE PLATE / RESTRICTION ORIFICE
شماره پیمان: |  |  |  |  | پروژه |  | بسته کاری |  | صادرکننده |  |  | تسهیلات |  | رشته |  |  | نوع مدرک |  | سریال |  |  | نسخه |  |  | شماره صفحه: 8 از 8
9184 – 073 - 053 |  |  |  |  | BK |  | GCS |  | PEDCO |  |  | 120 |  | IN |  |  | DT |  | 0013 |  |  | D02
RESTRICTION ORIFICE
Rev. | Item No. | Tag No. | P&ID No. | Service | Line Size | Schedule / C.A | Piping Class | Nace | Fluid | Phase | Temperature (°C) |  | Pressure (barg) |  | Flow Rate (Kg/h) |  |  | Density (Kg/m3) (Mix./Liq./Ga) | Specific Gravity (Mix) | Molecular Weight(Kg/Kgmol) | Viscosity(CP) (Gas/Liquid) | Gas Compressibility Factor | Cp / Cv | Liquid Vapor Pressure (barg) | Max. Diff. Pressure (barg) | Min Plate Thickness (mm) (VTC) | Bore Diameter (mm) (VTC) | Beta Ratio (d/D) (VTC) | Flange Size | Flange Rating/Facing | Flange Material | Remark
[11 empty] | Design | Operating | Design | Operating | Min. | Normal | Max.
D02 | 1 | RO-2112 | BK-GCS-PEDCO-120-PR-PI-0005 | Gas Compression Inlet Knock Out Drum | 3" | 80 / 6mm | AN07 | YES | HC | G | 85 | 36.87 | 18.2 | 9 | - | 5665.4 | - | 5.96~9.264 | 0.743~ 0.845 | 21.56~ 24.52 | 0.01 | - | 1.246~1.260 | - | 4.5 | Note 14 | 34.6 | 0.467 | 3" | 300# , RF | ASTM A105
D02 | 2 | RO-2133A | BK-GCS-PEDCO-120-PR-PI-0011 (1 of 3) | 2nd Stage Gas Compression Air Coolers | 1 1/2" | 40S / 0mm | FS00 | YES | HC | G | 175 | 60 | 62.4 | 62 | - | 1333 | - | 59.63 ~ 72.94 | 0.743~ 0.845 | 21.56~ 24.52 | 0.011 | - | 1.457~1.692 | - | 55 | Note 14 | 6.32 | 0.185 | 1 1/2" | 600# , RF | ASTM A182 GR.F316L
D02 | 3 | RO-2133B | BK-GCS-PEDCO-120-PR-PI-0011 (2 of 3) | 2nd Stage Gas Compression Air Coolers | 1 1/2" | 40S / 0mm | FS00 | YES | HC | G | 175 | 60 | 62.4 | 62 | - | 1333 | - | 59.63 ~ 72.94 | 0.743~ 0.845 | 21.56~ 24.52 | 0.011 | - | 1.457~1.692 | - | 55 | Note 14 | 6.32 | 0.185 | 1 1/2" | 600# , RF | ASTM A182 GR.F316L
D02 | 4 | RO-2133C | BK-GCS-PEDCO-120-PR-PI-0011 (3 of 3) | 2nd Stage Gas Compression Air Coolers | 1 1/2" | 40S / 0mm | FS00 | YES | HC | G | 175 | 60 | 62.4 | 62 | - | 1333 | - | 59.63 ~ 72.94 | 0.743~ 0.845 | 21.56~ 24.52 | 0.011 | - | 1.457~1.692 | - | 55 | Note 14 | 6.32 | 0.185 | 1 1/2" | 600# , RF | ASTM A182 GR.F316L
D02 | 5 | RO-2141 | BK-GCS-PEDCO-120-PR-PI-0012 | 2nd Stage Gas Compression Discharge Drum | 1 1/2" | 160 / 3mm | FN05 | YES | HC | G | 175 | 60 | 90 | 62 | - | 1722 | - | 59.17 ~ 72.94 | 0.743~ 0.847 | 21.56~24.56 | 0.011 | - | 1.461~1.692 | - | 55 | Note 14 | 7.18 | 0.211 | 1 1/2" | 600# , RF | ASTM A105
D02 | 6 | RO-2144 | BK-GCS-PEDCO-120-PR-PI-0012 | Gas Compression Discharge Drum | 2" | 40S / 0mm | FS00 | YES | HC | L | 175 | 60 | 62.4 | 53.9 | - | 11500 | - | 982 | 0.982 | 18.0544 | 0.49517 | - | 1.1625 | 15.58 | 53.7 | Note 14 | 7.081 | 0.134 | 2" | 600# , RF | ASTM A182 GR.F316L
D02 | 7 | RO-2151 | BK-GCS-PEDCO-120-PR-PI-0013 (1 of 3) | Gas Compression Dehydration Package | 3" | 80 / 3mm | FN05 | YES | HC | G | 175 | 59.4 | 90 | 62 | - | 4578 | - | 58.06 ~ 72.94 | 0.743~ 0.848 | 21.56~24.58 | 0.011 | 0.825 | 1.212~1.692 | - | 55 | Note 14 | 11.7 | 0.158 | 3" | 600# , RF | ASTM A105
D02 | 8 | RO-2162 | BK-GCS-PEDCO-120-PR-PI-0014 | Lean Glycol Storage Tank | 2" | 80 / 3mm | AN04 | NO | TEG | L | 85 | AMB | 18.2 | 2.07 | - | 5575 | 6132.5 | 1115 | 1.115 | 150.2 | 23.7781 | - | 1.042 | -1.0132 | 2.06 | Note 14 | 11.33 | 0.215 | 2" | 300# , RF | ASTM A105 | Finalized after received data from vendor. Multi stage design shall be considered if required
D02 | 9 | RO-2131A | BK-GCS-PEDCO-120-PR-PI-0009 (1 of 3) | CLOSED DRAIN HEADER | 2" | 10S / 0mm | CS00 | YES | HC+WATER | L | 155 | 60 | 30.3 | 18.1 | - | 10000 | - | 829.0943 | 0.82909 | 18.03 | 0.44367 | - | 1.3263 | 2.2342 | 17.9 | Note 14 | 8.6746 | 0.15833 | 2" | 300# , RF | ASTM A182 GR.F316L
D02 | 10 | RO-2131B | BK-GCS-PEDCO-120-PR-PI-0009 (2 of 3) | CLOSED DRAIN HEADER | 2" | 10S / 0mm | CS00 | YES | HC+WATER | L | 155 | 60 | 30.3 | 18.1 | - | 10000 | - | 829.0943 | 0.82909 | 18.03 | 0.44367 | - | 1.3263 | 2.2342 | 17.9 | Note 14 | 8.6746 | 0.15833 | 2" | 300# , RF | ASTM A182 GR.F316L
D02 | 11 | RO-2131C | BK-GCS-PEDCO-120-PR-PI-0009 (3 of 3) | CLOSED DRAIN HEADER | 2" | 10S / 0mm | CS00 | YES | HC+WATER | L | 155 | 60 | 30.3 | 18.1 | - | 10000 | - | 829.0943 | 0.82909 | 18.03 | 0.44367 | - | 1.3263 | 2.2342 | 17.9 | Note 14 | 8.6746 | 0.15833 | 2" | 300# , RF | ASTM A182 GR.F316L
D02 | 12 | RO-2134A | BK-GCS-PEDCO-120-PR-PI-0009 (1 of 3) | LP FLARE HEADER | 2" | 80 / 3mm | CN05 | YES | HC | G | 155 | 60 | 47.7 | 22 | - | 778.4 | - | 18.08 ~ 22.31 | 0.743~ 0.846 | 21.56~24.52 | 0.011 | - | 1.278~1.362 | - | 250 | Note 14 | 8.5 | 0.172 | 2" | 300# , RF | ASTM A105
D02 | 13 | RO-2134B | BK-GCS-PEDCO-120-PR-PI-0009 (2 of 3) | LP FLARE HEADER | 2" | 80 / 3mm | CN05 | YES | HC | G | 155 | 60 | 47.7 | 22 | - | 778.4 | - | 18.08 ~ 22.31 | 0.743~ 0.846 | 21.56~24.52 | 0.011 | - | 1.278~1.362 | - | 250 | Note 14 | 8.5 | 0.172 | 2" | 300# , RF | ASTM A105
D02 | 14 | RO-2134C | BK-GCS-PEDCO-120-PR-PI-0009 (3 of 3) | LP FLARE HEADER | 2" | 80 / 3mm | CN05 | YES | HC | G | 155 | 60 | 47.7 | 22 | - | 778.4 | - | 18.08 ~ 22.31 | 0.743~ 0.846 | 21.56~24.52 | 0.011 | - | 1.278~1.362 | - | 250 | Note 14 | 8.5 | 0.172 | 2" | 300# , RF | ASTM A105
| Note: | (1) HC:HYDROCARBONE , L: LIQUID , G: GAS , M: MIXED
(2) Vendor shall calculate the bore size & beta for 2 phase orifice plates.
(3) BLANK PLATE to be supplied. The bore shall be drilled later by others.
(4) C.A : Corossion Allowance
D02