## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-ME-DT-0027 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1094 |  |  | Transmital Date: 6/19/2022
Document Title: Mechanical Data Sheets For Overhead Traveling Cranes |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-ME-TR-1094 |  |  | Transmital Date: 6/19/2022
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-ME-DT-0027_D03 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | ماکزیمم دمای طراحی جهت تجهیزات الکتریکی بر اساس مدارک پایه بخش الکتریکال می بایست 52°c در نظر گرفته شود. |  | 1401-2294-185626 | 1401/05/29 | مطابق پیوست 10 از شرح کار پروژه، برای سایبان کمپرسورهای گاز و پمپ های آتش نشانی، جرثقیل سقفی برقی پیش بینی شده است که مطابق نظر کارفرمای محترم ماکزیمم دمای طراحی این تجهیزات در یادداشت شماره 13 از مدرک مکانیکال دیتاشیت مربوطه 52°c در نظر گرفته خواهد شد.
2 | ظرفیت و تناژ جرثقیل سایبان دیزل ژنراتور 2 تن و بصورت دستی در نظر گرفته شده است. با توجه به دیتاشت دیزل ژنراتورهای موجود وزن پکیج و مجموعه دیزل ژنراتور بیش از 3 تن می باشد. ضروریست ظرفیت و نوع این جرثقیل پس از نهایی سازی مدارک دیزل ژنراتور، بازنگری و نتیجه جهت بررسی به این امور اعلام گردد. |  | 1401-2294-185626 | 1401/05/29 | جرثقیل های سقفی تعبیه شده در زیر سایبان ها برای جابجا نمودن قطعاتی که نیاز به تعمیر دارند استفاده می شود و نیازی به در نظر گرفتن جرثقیل با ظرفیت بالا نمی باشد. همچنین مطابق با شرح کار برای این تجهیز یک جرثقیل سقفی دستی به ظرفیت 2 تن در نظر گرفته شده است. اگر کارفرمای محترم با توجه به توضیحات فوق اصرار به در نظر گرفتن جرثقیل برقی با ظرفیت بالاتر دارد، در بازبینی های بعدی با در نظر گرفتن اثرات مالی و زمانی آن اعمال خواهد گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: |  |  |  |  | Date: