| طرح نگهداشت و افزایش تولید 27 مخزن |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| CALCULATION NOTE FOR UTILITY AREA SLEEPERS نگهداشت و افزایش تولید میدان نفتی بینک |  |  |  |  |  |  |
| D01 | MAR. 2024 | IFA | R.Berlouie | M.Fakharian | S.Faramarzpour |  |
| D00 | JUL. 2023 | IFC | R.Berlouie | M.Fakharian | A.M.Mohseni |  |
| Rev. | Date | Purpose of Issue/Status | Prepared by: | Checked by: | Approved by: | CLIENT Approval |
| Class:2 |  | CLIENT Doc. Number:F0Z-709139 |  |  |  |  |
| Status: | IDC: Inter-Discipline Check IFC: Issued For Comment IFA: Issued For Approval AFD: Approved For Design AFC: Approved For Construction AFP: Approved For Purchase AFQ: Approved For Quotation IFI: Issued For Information AB-R: As-Built for CLIENT Review AB-A: As-Built –Approved |  |  |  |  |  |

REVISION RECORD SHEET

| PAGE | D00 | D01 | D02 | D03 | D04 |  | PAGE | D00 | D01 | D02 | D03 | D04 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | X |  |  |  |  |  | 66 |  |  |  |  |  |
| 2 | X |  |  |  |  |  | 67 |  |  |  |  |  |
| 3 | X |  |  |  |  |  | 68 |  |  |  |  |  |
| 4 | X |  |  |  |  |  | 69 |  |  |  |  |  |
| 5 | X |  |  |  |  |  | 70 |  |  |  |  |  |
| 6 | X |  |  |  |  |  | 71 |  |  |  |  |  |
| 7 | X |  |  |  |  |  | 72 |  |  |  |  |  |
| 8 | X |  |  |  |  |  | 73 |  |  |  |  |  |
| 9 | X |  |  |  |  |  | 74 |  |  |  |  |  |
| 10 | X | X |  |  |  |  | 75 |  |  |  |  |  |
| 11 | X | X |  |  |  |  | 76 |  |  |  |  |  |
| 12 | X | X |  |  |  |  | 77 |  |  |  |  |  |
| 13 | X | X |  |  |  |  | 78 |  |  |  |  |  |
| 14 | X | X |  |  |  |  | 79 |  |  |  |  |  |
| 15 | X | X |  |  |  |  | 80 |  |  |  |  |  |
| 16 | X | X |  |  |  |  | 81 |  |  |  |  |  |
| 17 | X | X |  |  |  |  | 82 |  |  |  |  |  |
| 18 | X | X |  |  |  |  | 83 |  |  |  |  |  |
| 19 | X | X |  |  |  |  | 84 |  |  |  |  |  |
| 20 | X | X |  |  |  |  | 85 |  |  |  |  |  |
| 21 | X | X |  |  |  |  | 86 |  |  |  |  |  |
| 22 | X | X |  |  |  |  | 87 |  |  |  |  |  |
| 23 | X | X |  |  |  |  | 88 |  |  |  |  |  |
| 24 | X | X |  |  |  |  | 89 |  |  |  |  |  |
| 25 | X | X |  |  |  |  | 90 |  |  |  |  |  |
| 26 | X | X |  |  |  |  | 91 |  |  |  |  |  |
| 27 | X | X |  |  |  |  | 92 |  |  |  |  |  |
| 28 | X | X |  |  |  |  | 93 |  |  |  |  |  |
| 29 | X | X |  |  |  |  | 94 |  |  |  |  |  |
| 30 | X | X |  |  |  |  | 95 |  |  |  |  |  |
| 31 | X | X |  |  |  |  | 96 |  |  |  |  |  |
| 32 | X | X |  |  |  |  | 97 |  |  |  |  |  |
| 33 | X |  |  |  |  |  | 98 |  |  |  |  |  |
| 34 | X |  |  |  |  |  | 99 |  |  |  |  |  |
| 35 | X |  |  |  |  |  | 100 |  |  |  |  |  |
| 36 | X |  |  |  |  |  | 101 |  |  |  |  |  |
| 37 | X |  |  |  |  |  | 102 |  |  |  |  |  |
| 38 |  |  |  |  |  |  | 103 |  |  |  |  |  |
| 39 |  |  |  |  |  |  | 104 |  |  |  |  |  |
| 40 |  |  |  |  |  |  | 105 |  |  |  |  |  |
| 41 |  |  |  |  |  |  | 106 |  |  |  |  |  |
| 42 |  |  |  |  |  |  | 107 |  |  |  |  |  |
| 43 |  |  |  |  |  |  | 108 |  |  |  |  |  |
| 44 |  |  |  |  |  |  | 109 |  |  |  |  |  |
| 45 |  |  |  |  |  |  | 110 |  |  |  |  |  |
| 46 |  |  |  |  |  |  | 111 |  |  |  |  |  |
| 47 |  |  |  |  |  |  | 112 |  |  |  |  |  |
| 48 |  |  |  |  |  |  | 113 |  |  |  |  |  |
| 49 |  |  |  |  |  |  | 114 |  |  |  |  |  |
| 50 |  |  |  |  |  |  | 115 |  |  |  |  |  |
| 51 |  |  |  |  |  |  | 116 |  |  |  |  |  |
| 52 |  |  |  |  |  |  | 117 |  |  |  |  |  |
| 53 |  |  |  |  |  |  | 118 |  |  |  |  |  |
| 54 |  |  |  |  |  |  | 119 |  |  |  |  |  |
| 55 |  |  |  |  |  |  | 120 |  |  |  |  |  |
| 56 |  |  |  |  |  |  | 121 |  |  |  |  |  |
| 57 |  |  |  |  |  |  | 122 |  |  |  |  |  |
| 58 |  |  |  |  |  |  | 123 |  |  |  |  |  |
| 59 |  |  |  |  |  |  | 124 |  |  |  |  |  |
| 60 |  |  |  |  |  |  | 125 |  |  |  |  |  |
| 61 |  |  |  |  |  |  | 126 |  |  |  |  |  |
| 62 |  |  |  |  |  |  | 127 |  |  |  |  |  |
| 63 |  |  |  |  |  |  | 128 |  |  |  |  |  |
| 64 |  |  |  |  |  |  | 129 |  |  |  |  |  |
| 65 |  |  |  |  |  |  | 130 |  |  |  |  |  |

CONTENTS

1.0	INTRODUCTION	4

2.0	Scope	5

3.0	NORMATIVE REFERENCES	5

3.1.	Local Codes and Standards	5

3.2.	International Codes and Standards	5

3.3.	The Project Documents	5

3.4.	ENVIRONMENTAL DATA	5

3.5.	Order of Precedence	5

4.0	MATERIALS	6

5.0	DESIGN INFORMATION	7

5.1   LOCATION OF SLEEPERS	7

6.0	PIPING weigh	8

7.0	SOIL PARAMETERS	8

8.0	LOADING	9

8.1.	Dead Load	9

8.2.	Live Load	10

8.3.	Seismic Load	10

8.4.	Wind Load	10

9.0	LOAD COMBINITION FOR DESIGN	10

10.0	FOUNDATION ANALYsis	14

- INTRODUCTION

Binak oilfield in Bushehr province is a part of the southern oilfields of Iran, is located 20 km northwest of Genaveh city.

With the aim of increasing production of oil from Binak oilfield, an EPC/EPD Project has been defined by NIOC/NISOC and awarded to Petro Iran Development Company (PEDCO). Also PEDCO (as General Contractor) has assigned the EPC-packages of the Project to "Hirgan Energy - Design and Inspection" JV.

As a part of the Project, a New Gas Compressor Station (adjacent to existing Binak GCS) shall be constructed to gather of 15 MMSCFD (approx.) associated gases and compress & transfer them to Siahmakan GIS.

GENERAL DEFINITION

The following terms shall be used in this document.

| CLIENT: | National Iranian South Oilfields Company (NISOC) |
| --- | --- |
| PROJECT: | Binak Oilfield Development – Surface Fcilities; New Gas Compressor Station |
| EPD/EPC CONTRACTOR (GC): | Petro Iran Development Company (PEDCO) |
| EPC CONTRACTOR: | Joint Venture of : Hirgan Energy – Design & Inspection (D&I) Companies |
| VENDOR: | The firm or person who will fabricate the equipment or material. |
| EXECUTOR: | Executor is the party which carries out all or part of construction and/or commissioning for the project. |
| THIRD PARTY INSPECTOR (TPI): | The firm appointed by EPD/EPC CONTRACTOR (GC) and approved by CLIENT (in writing) for the inspection of goods. |
| SHALL: | Is used where a provision is mandatory. |
| SHOULD: | Is used where a provision is advisory only. |
| WILL: | Is normally used in connection with the action by CLIENT rather than by an EPC/EPD CONTRACTOR, supplier or VENDOR. |
| MAY: | Is used where a provision is completely discretionary. |

- Scope

This report covers the Sleeper Pipe Supports foundation Design. The structure modelled by “SAP” software.

- NORMATIVE REFERENCES

## Local Codes and Standards

- INBC Part 9                             Iranian National Building Code, Part 9 (4th Edition)

- Iranian Standard No.2800         Iranian Code of Practice for Seismic Resistant Design of                                                 Buildings (4th Edition)

## International Codes and Standards

- ACI 315                                Manual of Standard Practice for Detailing Reinforced Concrete

- ACI 318-14                           Building Code Requirements for Reinforced Concrete

- ASCE7-10                Minimum Design Loads and Associated Criteria for Buildings           and Other Structures-American Society of Civil Engineers

- ISDC-038                           Iranian Seismic Design Code for Petroleum Facilities(3rd edition)

## The Project Documents

- BK-GCS-PEDCO-120-GT-RT-0001     Geotechnical Investigation Report for                    Compressor Station

- BK-GNRAL-PEDCO-000-ST-DC-0001  Structural Design Criteria

- BNK-INTER-PI-DWG-1                              Sleeper Single Line Diagrem For GCS

## ENVIRONMENTAL DATA

Refer to "Process Basis of Design; Doc. No. BK-GNRAL-PEDCO-000-PR-DB-0001".

## Order of Precedence

In case of any conflict between the contents of this document or any discrepancy between this document and other project documents or reference standards, this issue must be reported to the CLIENT. The final decision in this situation will be made by CLIENT.

- MATERIALS

Material properties are delivered in the following table.

Table1-Material Properties

| Foundation Concrete | F'c = 300 kg/cm2 (28- day cylindrical sample) |
| --- | --- |
| Long. Reinforcement bar | Fy = 4000 kg/cm2 (AIII) |
| Trans. Reinforcement bar | Fy = 4000 kg/cm2 (AIII) |

- DESIGN INFORMATION

# 5.1   LOCATION OF SLEEPERS

- Location of Utility sleepers According to Piping SLD

Sleeper’s foundation plan (Type A & B) and section with embedded plate shown as follow:

- Sleeper Type A

- Sleeper Type B

- PIPING weigh

Data Received from Piping is as single lines and loading table for each point as bellow:

*Note:

Lateral & axial Friction loads for uniform loads=0.3*vertical load

Lateral & axial seismic load for uniform loads = 0.4* vertical load

Lateral seismic& friction loads for anchor sleepers =0.4*Vertical Load

Axial seismic & friction loads for anchor sleepers = 0.8* vertical load

- SOIL PARAMETERS

According to Soil Investigation Report, prepared by BKP:

- Geotechnical Parameters

- LOADING

## Dead Load

Dead load of pipes according to piping documents assign in model.

## Live Load

Live load (operation) of pipes according to piping documents assign in model.

## Seismic Load

Seismic load (occasional) pipes according to piping documents assign in model.

## Wind Load

Wind load is not applicable for pipe support foundation.

- LOAD COMBINITION FOR DESIGN

According to ASCE07-10 structures, components, and foundations shall be designed, so that their design strength equals or exceeds that effect of factored loads in the following combination

**Ev=αSDs*D

Ev=0.2*0.75*Sus=0.15*D

Vertical seismic load applied at combinations with load combination with coefficient of 0.15*dead load in combinations with earthquake load.

| TABLE: |  |  |  |
| --- | --- | --- | --- |
| LoadPat | DesignType | SelfWtMult | AutoLoad |
| SUS | Dead | 1 |  |
| OPE | Live | 0 |  |
| OCCX | Quake | 0 | None |
| OCCY | Quake | 0 | None |
| HYD | Dead | 0 |  |
| LIVE | Live | 0 |  |
| FRX | Other | 0 |  |
| FRY | Other | 0 |  |
| Ev | Quake | 0 | None |
| H | Other | 0 |  |

| TABLE: |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| ComboName | ComboType | AutoDesign | CaseName | ScaleFactor | SteelDesign |
| D+L+FR | Linear Add | No | SUS | 1 | Strength |
| D+L+FR |  |  | FRx | 1 |  |
| D+L+FR |  |  | OPE | 1 |  |
| HYD+FR | Linear Add | No | HYD | 1 | None |
| HYD+FR |  |  | FRx | 1 |  |
| 1.4D | Linear Add | No | SUS | 1.4 | None |
| 1.35D+L+EX+FR+1.6H | Linear Add | No | SUS | 1.35 | Strength |
| 1.35D+L+EX+FR+1.6H |  |  | OCCX | 1 |  |
| 1.35D+L+EX+FR+1.6H |  |  | OPE | 1 |  |
| 1.35D+L+EX+FR+1.6H |  |  | FRx | 1 |  |
| 1.35D+L+EX+FR+1.6H |  |  | FRY | 1 |  |
| 1.35D+L+EX+FR+1.6H |  |  | H | 1.6 |  |
| 1.35D+L-EX+FR+1.6H | Linear Add | No | SUS | 1.35 | Strength |
| 1.35D+L-EX+FR+1.6H |  |  | OCCX | -1 |  |
| 1.35D+L-EX+FR+1.6H |  |  | OPE | 1 |  |
| 1.35D+L-EX+FR+1.6H |  |  | FRx | 1 |  |
| 1.35D+L-EX+FR+1.6H |  |  | FRY | 1 |  |
| 1.35D+L-EX+FR+1.6H |  |  | H | 1.6 |  |
| 1.35D+L+EY+FR+1.6H | Linear Add | No | SUS | 1.35 | Strength |
| 1.35D+L+EY+FR+1.6H |  |  | OCCY | 1 |  |
| 1.35D+L+EY+FR+1.6H |  |  | FRx | 1 |  |
| 1.35D+L+EY+FR+1.6H |  |  | OPE | 1 |  |
| 1.35D+L+EY+FR+1.6H |  |  | FRY | 1 |  |
| 1.35D+L+EY+FR+1.6H |  |  | H | 1.6 |  |
| 1.35D+L-EY+FR+1.6H | Linear Add | No | SUS | 1.2 | Strength |
| 1.35D+L-EY+FR+1.6H |  |  | OCCY | -1 |  |
| 1.35D+L-EY+FR+1.6H |  |  | FRx | 1 |  |
| 1.35D+L-EY+FR+1.6H |  |  | OPE | 1 |  |
| 1.35D+L-EY+FR+1.6H |  |  | FRY | 1 |  |
| 1.35D+L-EY+FR+1.6H |  |  | H | 1.6 |  |
| 0.9D+Ex+1.6H | Linear Add | No | SUS | 0.9 | Strength |
| 0.9D+Ex+1.6H |  |  | OCCX | 1 |  |
| 0.9D+Ex+1.6H |  |  | H | 1.6 |  |
| 0.9D-Ex+1.6H | Linear Add | No | SUS | 0.9 | Strength |
| 0.9D-Ex+1.6H |  |  | OCCX | -1 |  |
| 0.9D-Ex+1.6H |  |  | H | 1.6 |  |
| 0.9D-Ey+1.6H | Linear Add | No | SUS | 0.9 | Strength |
| 0.9D-Ey+1.6H |  |  | OCCY | -1 |  |
| 0.9D-Ey+1.6H |  |  | H | 1.6 |  |
| 0.9D+Ey+1.6H | Linear Add | No | SUS | 0.9 | Strength |
| 0.9D+Ey+1.6H |  |  | OCCY | 1 |  |
| 0.9D+Ey+1.6H |  |  | H | 1.6 |  |
| 1.2D+1.6L+1.6FR+1.6H | Linear Add | No | SUS | 1.2 | Strength |
| 1.2D+1.6L+1.6FR+1.6H |  |  | OPE | 1.6 |  |
| 1.2D+1.6L+1.6FR+1.6H |  |  | FRx | 1.6 |  |
| 1.2D+1.6L+1.6FR+1.6H |  |  | FRY | 1.2 |  |
| 1.2D+1.6L+1.6FR+1.6H |  |  | H | 1.6 |  |
| 0.75D-Ex | Linear Add | No | SUS | 0.75 | Strength |
| 0.75D-Ex |  |  | OCCX | -1 |  |
| 0.75D-Ey | Linear Add | No | SUS | 0.75 | Strength |
| 0.75D-Ey |  |  | OCCY | -1 |  |
| 0.75D+Ey | Linear Add | No | SUS | 0.75 | Strength |
| 0.75D+Ey |  |  | OCCY | 1 |  |
| 0.75D+Ex | Linear Add | No | SUS | 0.75 | Strength |
| 0.75D+Ex |  |  | OCCX | 1 |  |
| Envelope Strength | Envelope | No | 1.4D | 1 | None |
| Envelope Strength |  |  | 1.35D+L+EY+FR+1.6H | 1 |  |
| Envelope Strength |  |  | 1.35D+L+EX+FR+1.6H | 1 |  |
| Envelope Strength |  |  | 1.35D+L-EY+FR+1.6H | 1 |  |
| Envelope Strength |  |  | 1.35D+L-EX+FR+1.6H | 1 |  |
| Envelope Strength |  |  | 1.2D+1.6L+1.6FR+1.6H | 1 |  |
| Envelope Strength |  |  | 0.9D+Ey+1.6H | 1 |  |
| Envelope Strength |  |  | 0.9D+Ex+1.6H | 1 |  |
| Envelope Strength |  |  | 0.9D-Ey+1.6H | 1 |  |
| Envelope Strength |  |  | 0.9D-Ex+1.6H | 1 |  |
| Envelope Strength |  |  | 0.75D-Ex | 1 |  |
| Envelope Strength |  |  | 0.75D-Ey | 1 |  |
| Envelope Strength |  |  | 0.75D+Ey | 1 |  |
| Envelope Strength |  |  | 0.75D+Ex | 1 |  |
| D+L+H | Linear Add | No | SUS | 1 | None |
| D+L+H |  |  | OPE | 1 |  |
| D+L+H |  |  | H | 1 |  |
| D+0.7OCCX+H | Linear Add | No | SUS | 1 | None |
| D+0.7OCCX+H |  |  | OCCX | 0.7 |  |
| D+0.7OCCX+H |  |  | H | 1 |  |
| D-0.7OCCX+H | Linear Add | No | SUS | 1 | None |
| D-0.7OCCX+H |  |  | OCCX | -0.7 |  |
| D-0.7OCCX+H |  |  | H | 1 |  |
| D+0.7OCCY+H | Linear Add | No | SUS | 1 | None |
| D+0.7OCCY+H |  |  | OCCY | 0.7 |  |
| D+0.7OCCY+H |  |  | H | 1 |  |
| D-0.7OCCY+H | Linear Add | No | SUS | 1 | None |
| D-0.7OCCY+H |  |  | OCCY | -0.7 |  |
| D-0.7OCCY+H |  |  | H | 1 |  |
| D+0.75L+0.75OCCX+H | Linear Add | No | SUS | 1 | None |
| D+0.75L+0.75OCCX+H |  |  | OPE | 0.75 |  |
| D+0.75L+0.75OCCX+H |  |  | OCCX | 0.75 |  |
| D+0.75L+0.75OCCX+H |  |  | H | 1 |  |
| D-0.75L-0.75OCCX+H | Linear Add | No | SUS | 1 | None |
| D-0.75L-0.75OCCX+H |  |  | OPE | 0.75 |  |
| D-0.75L-0.75OCCX+H |  |  | OCCX | -0.75 |  |
| D-0.75L-0.75OCCX+H |  |  | H | 1 |  |
| D+0.75L+0.75OCCY+H | Linear Add | No | SUS | 1 | None |
| D+0.75L+0.75OCCY+H |  |  | OPE | 0.75 |  |
| D+0.75L+0.75OCCY+H |  |  | OCCY | 0.75 |  |
| D+0.75L+0.75OCCY+H |  |  | H | 1 |  |
| D-0.75L-0.75OCCY+H | Linear Add | No | SUS | 1 | None |
| D-0.75L-0.75OCCY+H |  |  | OPE | 0.75 |  |
| D-0.75L-0.75OCCY+H |  |  | OCCY | -0.75 |  |
| D-0.75L-0.75OCCY+H |  |  | H | 1 |  |
| D+H | Linear Add | No | H | 1 | None |
| D+H |  |  | SUS | 1 |  |
| Envelope allowable | Envelope | No | D+L+H | 1 | None |
| Envelope allowable |  |  | HYD+FR | 1 |  |
| Envelope allowable |  |  | D+L+FR | 1 |  |
| Envelope allowable |  |  | D+H | 1 |  |
| Envelope allowable |  |  | D+0.7OCCY+H | 1 |  |
| Envelope allowable |  |  | D+0.7OCCX+H | 1 |  |
| Envelope allowable |  |  | D+0.75L+0.75OCCY+H | 1 |  |
| Envelope allowable |  |  | D+0.75L+0.75OCCX+H | 1 |  |
| Envelope allowable |  |  | D-0.75L-0.75OCCX+H | 1 |  |
| Envelope allowable |  |  | D-0.75L-0.75OCCY+H | 1 |  |
| Envelope allowable |  |  | 0.75D+Ey | 1 |  |
| Envelope allowable |  |  | 0.75D+Ex | 1 |  |
| Envelope allowable |  |  | 0.75D-Ex | 1 |  |
| Envelope allowable |  |  | 0.75D-Ey | 1 |  |

- FOUNDATION ANALYsis

## 10.1. SLEEPER

## piping load data

- 10.1.1.Operating weight of Piping

This type of loading is operating weight of pipes that are considered by Piping and illustrated in tables and is equal to OPR for each point.

- OPE  Points Loads on sleeper TYPE A

- 10.1.2.PURE SEISMIC WEIGHT OF PIPING (OCCX & OCCY)

Seismic loads of pipes according to piping documents assign in model. In some cases when the earthquake load is not provided by piping, the earthquake coefficient is calculated as follow:

Lateral & axial seismic load for uniform loads = 0.4* vertical load

Lateral & axial friction loads for anchor sleepers = 0.8* vertical load

Occx,y=5000 N/m×1m×0.4=2000 N

Occx,y(each point)=2000 kg÷2point=1000 N

- OCCX,Y Points Loads on sleeper

- 10.1.3.Friction Load (FRX & FRY)

Thermal displacement due to Operating condition and the friction between pipes and the sleepers, causes lateral forces according to piping documents assign in model. In some cases when the Friction load is not provided by piping, the Friction coefficient is calculated as follow:

Lateral & axial Friction loads for uniform loads=0.3*vertical load

Lateral & axial loads for anchor sleepers = 0.8* vertical load

FRx,y=5000 N/m×1m×0.3=1500 N

FRx,y(each point)=1500 N÷2point=750 N

- FRX,Y Points Loads on sleeper

- 10.1.4.Vertical seismic load

The vertical seismic load effect, 𝐸𝑣, shall be determined in accordance with the following Equation ASCE7-16 Eq. (12.14-6):

𝐸𝑣 = 0.2SDS𝐷                                           (ASCE7/ Eq. 12.14-6)

SDS = Design, 5% damped, spectral response acceleration parameter (g) at short periods (0.2 sec).=0.75

D = effect of dead load

Loads case name: EQZ=0.2×0.75×W=0.15×W

(where W=DL+OPR1+OPR FUTURE)

- applied Ev load

- 10.1.5.Soil load on foundation

Soil load weight has been applied on foundation as below

γsoil=1850kg/m3

hsoil=0.6m   P=γh=1850*0.6=1110kgm2

- applied soil load on foundation type A(1110Kg)

- applied soil load on foundation type B(1110Kg)

- 10.1.6.Soil Pressure on wall of sleeper

According to drawings approximately 0.6m is underground that horizontal pressure applied on model as below:

- Define joint Pattern

- Applied soil pressure load on sleeper Type A

- applied soil pressure load on sleeper Type B

## 10.2. wall design

- SAP2000 has been used in order to modeling, analyses and design of this wall &foundation.

# wall thickness=500 mm

# according to sap model Mmax=0.70  ton.m

- -Graphical output of M(1-1),(2-2)max Sleeper Type A(ton-m)

According to above output max Moment is  about 77777  kg-cm

# As(req)=ρreq.b.d=0.432 cm2      << :   uses Ø16@200    As=10.05cm2   ok

According to above output max Moment is about 177777 kg-cm

# As(req)=ρreq.b.d=0.989 cm2      << :   uses Ø16@200    As=10.05cm2   ok

## 10.3.check of stress & settlement for foundation (type A:300x130x40

## type b:300x90x40)

- stress diagram for foundation (Sleeper Type A)

According to Sap results, the maximum soil stress under the foundation in combination ENV-Allowable is:

max. stress under foundation:  1.8×0.7=1.26 kg/cm2< 2.40 kg/cm2         ok.

Foundation joints displacement under load combinations is as below:

| TABLE: Joint Displacements |  |  |  |  |
| --- | --- | --- | --- | --- |
| Joint | OutputCase | CaseType | StepType | U3 |
| Text | Text | Text | Text | cm |
| 35 | Envelope allowable | Combination | Max | 0.068 |
| 35 | Envelope allowable | Combination | Min | -0.526 |
| 36 | Envelope allowable | Combination | Max | -0.217 |
| 36 | Envelope allowable | Combination | Min | -0.727 |
| 39 | Envelope allowable | Combination | Max | 0.007 |
| 39 | Envelope allowable | Combination | Min | -0.512 |
| 47 | Envelope allowable | Combination | Max | -0.054 |
| 47 | Envelope allowable | Combination | Min | -0.504 |
| 52 | Envelope allowable | Combination | Max | -0.116 |
| 52 | Envelope allowable | Combination | Min | -0.512 |
| 57 | Envelope allowable | Combination | Max | -0.177 |
| 57 | Envelope allowable | Combination | Min | -0.583 |
| 62 | Envelope allowable | Combination | Max | -0.238 |
| 62 | Envelope allowable | Combination | Min | -0.655 |
| 70 | Envelope allowable | Combination | Max | 0.345 |
| 70 | Envelope allowable | Combination | Min | -0.875 |
| 71 | Envelope allowable | Combination | Max | 0.311 |
| 71 | Envelope allowable | Combination | Min | -0.875 |
| 72 | Envelope allowable | Combination | Max | 0.281 |
| 72 | Envelope allowable | Combination | Min | -1.310 |
| 73 | Envelope allowable | Combination | Max | 0.281 |
| 73 | Envelope allowable | Combination | Min | -1.277 |
| 74 | Envelope allowable | Combination | Max | 0.339 |
| 74 | Envelope allowable | Combination | Min | -0.875 |
| 75 | Envelope allowable | Combination | Max | 0.007 |
| 75 | Envelope allowable | Combination | Min | -0.586 |
| 76 | Envelope allowable | Combination | Max | 0.068 |
| 76 | Envelope allowable | Combination | Min | -0.586 |
| 77 | Envelope allowable | Combination | Max | 0.007 |
| 77 | Envelope allowable | Combination | Min | -0.877 |
| 78 | Envelope allowable | Combination | Max | 0.068 |
| 78 | Envelope allowable | Combination | Min | -0.871 |
| 79 | Envelope allowable | Combination | Max | 0.281 |
| 79 | Envelope allowable | Combination | Min | -1.282 |
| 80 | Envelope allowable | Combination | Max | 0.334 |
| 80 | Envelope allowable | Combination | Min | -0.875 |
| 81 | Envelope allowable | Combination | Max | -0.008 |
| 81 | Envelope allowable | Combination | Min | -0.586 |
| 82 | Envelope allowable | Combination | Max | -0.008 |
| 82 | Envelope allowable | Combination | Min | -0.883 |
| 83 | Envelope allowable | Combination | Max | 0.281 |
| 83 | Envelope allowable | Combination | Min | -1.288 |
| 84 | Envelope allowable | Combination | Max | 0.328 |
| 84 | Envelope allowable | Combination | Min | -0.875 |
| 85 | Envelope allowable | Combination | Max | -0.008 |
| 85 | Envelope allowable | Combination | Min | -0.586 |
| 86 | Envelope allowable | Combination | Max | -0.008 |
| 86 | Envelope allowable | Combination | Min | -0.888 |
| 87 | Envelope allowable | Combination | Max | 0.281 |
| 87 | Envelope allowable | Combination | Min | -1.293 |
| 88 | Envelope allowable | Combination | Max | 0.322 |
| 88 | Envelope allowable | Combination | Min | -0.875 |
| 89 | Envelope allowable | Combination | Max | -0.008 |
| 89 | Envelope allowable | Combination | Min | -0.586 |
| 90 | Envelope allowable | Combination | Max | -0.008 |
| 90 | Envelope allowable | Combination | Min | -0.894 |
| 91 | Envelope allowable | Combination | Max | 0.281 |
| 91 | Envelope allowable | Combination | Min | -1.299 |
| 92 | Envelope allowable | Combination | Max | 0.317 |
| 92 | Envelope allowable | Combination | Min | -0.875 |
| 93 | Envelope allowable | Combination | Max | -0.008 |
| 93 | Envelope allowable | Combination | Min | -0.586 |
| 94 | Envelope allowable | Combination | Max | -0.008 |
| 94 | Envelope allowable | Combination | Min | -0.906 |
| 95 | Envelope allowable | Combination | Max | 0.281 |
| 95 | Envelope allowable | Combination | Min | -1.305 |
| 96 | Envelope allowable | Combination | Max | -0.008 |
| 96 | Envelope allowable | Combination | Min | -0.586 |
| 97 | Envelope allowable | Combination | Max | -0.008 |
| 97 | Envelope allowable | Combination | Min | -0.978 |
|  |  |  | max | 0.345 |
|  |  |  | min | -1.310 |

According to above sap 2000 results, the maximum soil displacement under the foundation in combination ENV-COMB is:

max. displacement under foundation :1.310 cm    <   2 cm         ok.

- stress diagram for foundation (Sleeper Type B)

According to Sap results, the maximum soil stress under the foundation in combination ENV-Allowable is:

max. stress under foundation:  .022×0.9=0.198 kg/cm2< 2.40 kg/cm2         ok.

## 10.4. foundation REINFORCING CONTROL

for foundation : Asmin=0.0018 bh=0.0018×100×45=8.1 cm2

As used=∅16 @ 200=10.05 cm2    OK

- stress diagram for Sleeper Type A Foundation

Mu1=880373   kg.cm

b=100 cm

fc=300

fy=4000

d=35cm

∅=0.9

Mn=Mu∅=97819.222  kg.cm

# Rn1=Mn1b.d2=0.799

# m1=fy0.85fc=15.686

# ρreq=1m11-1-2m1Rn1fy=0.000200

# As(req)=ρreq.b.d=0.7cm2      << :   uses Ø16@200    As=10.05cm2   ok

- stress diagram for Sleeper Type B Foundation

Mu1=644960   kg.cm

b=100 cm

fc=300

fy=4000

d=35cm

∅=0.9

Mn=Mu∅=71662.22  kg.cm

# Rn1=Mn1b.d2=0.585

# m1=fy0.85fc=15.686

# ρreq=1m11-1-2m1Rn1fy=0.000146

# As(req)=ρreq.b.d=0.512cm2      << :   uses Ø16@200    As=10.05cm2   ok

## 10.5. OVERTURNING and sliding CONTROL CALCULATION

- 10.5.1.Anchor Sleeper TYPE A:

## 10.5.1.1. SLIDING control calculation:

L=3 m , B=1.3m , t=0.4m ,H=1.1m(1 m soil height &0.5m above ground)

### For pipe 10 inch weight per meter is about 25kg/ m .

### γSOIL=1850 kg/m3

### γconcrete=2500 kg/m3

### WF=3×1.3×0.4×2.5=3.9  ton

### Wwall=3×0.5×1.1×2.5=4.125  ton

### Wsoil=1.85×1×0.8×3=4.44 ton

### Wpipe=3.7 ton

### Mr=3.9+4.125+4.44+3.7×0.65=10.50  ton.m

### Mo=205×7×1.5=2.1525 ton .m

### SF= MrMo=10.502.1525=4.88>   1.5  OK

## 10.5.1.2. SLIDING control calculation:

According to design criteria the resisting force against sliding shall be calculated with the value whichever is greater of the followings:

(100 % friction force between soil and foundation) + (50%soil passive resistance)

(50% friction force between soil and foundation) + (100%soil passive resistance)

### μ=tan0.67∅=0.4

### Veqy=1.435  ton

### Kp=3

### γ=1.85 grcm3

### Rsliding=0.5×μ×WR+0.5KpγH2L=0.5×0.4×3.9+4.125+4.44+3.7+0.5×3×1.85×12×3= 11.55 ton

### Rsliding=μ×WR+0.5×0.5KpγH2L=0.4×3.9+4.125+4.44+3.7+0.5×0.5×3×1.85×12×3=10.62on

### Rsliding=min⁡(11.55.10.62)

### SF=RslidingVeqy=9.901.435=7.40        ≥     1.00   OK

- 10.5.1.Anchor Sleeper TYPE B:

## 10.5.2.1. SLIDING control calculation:

L=3 m , B=0.9 , t=0.4m ,H=1.1m(1m soil height &0.5m above ground)

### For pipe 10 inch weight per meter is about 25kg/ m.

### γSOIL=1850 kg/m3

### γconcrete=2500 kg/m3

### WF=3×0.9×0.4×2.5=2.7  ton

### Wwall=3×0.5×1.1×2.5=4.125  ton

### Wsoil=1.85×1×0.4×3=2.22 ton

### Wpipe=3.7 ton

### Mr=2.7+4.125+2.22+3.7×0.45=5.73 ton.m

### Mo=1440×1.5=2.16 ton .m

### SF= MrMo=5.732.16=2.65>   1.5  OK

## 10.5.2.2. SLIDING control calculation:

According to design criteria the resisting force against sliding shall be calculated with the value whichever is greater of the followings:

(100 % friction force between soil and foundation) + (50%soil passive resistance)

(50% friction force between soil and foundation) + (100%soil passive resistance)

### μ=tan0.67∅=0.4

### Veqy=1.44  ton

### Kp=3

### γ=1.85 grcm3

### Rsliding=0.5×μ×WR+0.5KpγH2L=0.5×0.4×2.7+4.125+2.22+3.7+0.5×3×1.85×12×3= 10.87 ton

### Rsliding=μ×WR+0.5×0.5KpγH2L=0.4×2.7+4.125+2.22+3.7+0.5×0.5×3×1.85×12×3= 9.26ton

### Rsliding=min⁡(10.87,9.26)

### SF=RslidingVeqy=9.261.435=6.45        ≥     1.00   OK