## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-HV-PY-0010 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-2545 |  |  | Transmital Date: 1/31/2024
Document Title: HVAC System Layout For CCTV Control Room – BINAK DU |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-HV-TR-2545 |  |  | Transmital Date: 1/31/2024
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-HV-PY-0010_D00 |  |  | CRS Status:
| Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | ظرفیت هوادهی فن های تخلیه می بایست حداقل 100 L/S در نظر گرفته شود. |  | 1402-2294-535557 | 1402/12/26 | در خصوص فن تخلیه هوای آبدارخانه ظرفیت فن تغییر یافت. اما در خصوص فن تخلیه هوای سرویس بهداشتی فن با بیشترین حجم هوای عبوری موجود در بازار برای فن سقفی، مد نظر قرار گرفت.
2 | کمپرسورهای کولر های دو تکه باید مناسب شرایط حاره ای و با قابلیت کارکرد در شرایط T3 باشد. |  | 1402-2294-535557 | 1402/12/26 | به عبارت T3در ستون TYPE جدول مشخصات کولرهای گازی اشاره شده است.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: |  |  |  |  | Date: