## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-HV-PY-0006 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1051 |  |  | Transmital Date: 07-June-2022
Document Title: HVAC System Layout & Section For Extension of Existing Elect. Building |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0103-HV-TR-1051 |  |  | Transmital Date: 07-June-2022
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-PEDCO-120-HV-PY-0006_D00 |  |  | CRS Status:
| Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | to add in split unit schedule table remark that the split unita shall work for T3 Category and actual load derate 30 % ( for standard rating 35/27) |  | BK-SUR-ENG-HVC-01-04921 | 2022-06-29 | In "data sheets for main HVAC equipment" will be added.
2 | one column for pressure drop in sand trap louvre table shall add also material shall specify |  | BK-SUR-ENG-HVC-01-04921 | 2022-06-29 | HVAC layout completely revised based on final heat dissipation data and final architectural design and details. Fan filter unit considered and there is no pressure relief damper.
3 | for PRD: standard opening pressure (pressure at which that the flap begins to open) has mention , normally from 10pa to 50 pa, add also material shall specify |  | BK-SUR-ENG-HVC-01-04921 | 2022-06-29
4
5
6
7
8
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature | H.Naserizadeh |  |  | Clarified By: M.Fakharian | Signature
| Date: |  |  |  |  | Date: