## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-EL-PY-0004 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-2144 |  |  | Transmital Date: 24-May-2023
Document Title: Lighting & Small Power Layout For Building & Shelter |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0203-EL-TR-2144 |  |  | Transmital Date: 24-May-2023
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-EL-PY-0004_D01 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | بند 9 ریپلای شیت در صورت موجود نبودن MICC از کابل ضد حریق به صورن نصب بر روی سینی کابل گالوانیزه در پوش دار استفاده گردد. استفاده از کابل معمولی و نصی در سیستم کاندوئیت بسته با توجه به تجریبات قبلی مورد تأیید نمی باشد. |  | 1402-2294-136312 | 1402/04/10 | اعمال خواهد شد.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: |  |  |  |  | Date: