## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-EL-CN-0002 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-2112 |  |  | Transmital Date: 20-May-2023
Document Title: Calculation Note For Indoor Area Lighting System |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0202-EL-TR-2112 |  |  | Transmital Date: 20-May-2023
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-EL-CN-0002_D03 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | از آنجا که لامپ های متال هالید نیز جزو لامپهای گازی محسوب می شوند، در اثر نوسانات ولتاژ با تاخیر روشن خواهند شد و موجب اخلال در بهره برداری واحد خواهند گردید. لذا دلایل مطرح شده در بند یک Reply Sheet قابل قبول نمی باشد. در صورتیکه در این خصوص از سازندگان لامپهای متال هالید مدرکی وجود دارد، لازم است جهت بررسی ارائه گردد. |  | 1402-2294-111185 | 1402-03-24 | با توجه به استاندارد پروژه مدرک Specification for Lighting & Small Power System و شماره BK-GNRAL-PEDCO-000-EL-SP-0007_D03 می بایست از چراغهای متال هالید در زیر شلتر استفاده نمود. از اینرو این لامپها ملاک طراحی می باشد.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: |  |  |  |  | Date: