| طرح نگهداشت و افزایش تولید 27 مخزن |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| CALCULATION REPORT FOR EXTENSION OF EXISTING ELECT. BUILDING نگهداشت و افزایش تولید میدان نفتی بینک |  |  |  |  |  |  |  |
| D01 | APR. 2024 | IFC | R.Berlouie | M.Fakharian | S.Faramarzpour |  |
| D00 | SEP. 2022 | IFC | R.Berlouie | M.Fakharian | M.Mehrshad |  |
| Rev. | Date | Purpose of Issue/Status | Prepared by: | Checked by: | Approved by: | CLIENT Approval |
| Class:2 |  | CLIENT Doc. Number:F0Z-709120 |  |  |  |  |
| Status: | IDC: Inter-Discipline Check IFC: Issued For Comment IFA: Issued For Approval AFD: Approved For Design AFC: Approved For Construction AFP: Approved For Purchase AFQ: Approved For Quotation IFI: Issued For Information AB-R: As-Built for CLIENT Review AB-A: As-Built –Approved |  |  |  |  |  |

REVISION RECORD SHEET

| PAGE | D00 | D01 | D02 | D03 | D04 |  | PAGE | D00 | D01 | D02 | D03 | D04 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | X | X |  |  |  |  | 77 |  | X |  |  |  |
| 2 | X | X |  |  |  |  | 78 |  | X |  |  |  |
| 3 | X | X |  |  |  |  | 79 |  | X |  |  |  |
| 4 | X | X |  |  |  |  | 80 |  | X |  |  |  |
| 5 | X | X |  |  |  |  | 81 |  | X |  |  |  |
| 6 | X | X |  |  |  |  | 82 |  | X |  |  |  |
| 7 | X | X |  |  |  |  | 83 |  | X |  |  |  |
| 8 | X | X |  |  |  |  | 84 |  | X |  |  |  |
| 9 | X | X |  |  |  |  | 85 |  | X |  |  |  |
| 10 | X | X |  |  |  |  | 86 |  | X |  |  |  |
| 11 | X | X |  |  |  |  | 87 |  | X |  |  |  |
| 12 | X | X |  |  |  |  | 88 |  | X |  |  |  |
| 13 | X | X |  |  |  |  | 89 |  | X |  |  |  |
| 14 | X | X |  |  |  |  | 90 |  | X |  |  |  |
| 15 | X | X |  |  |  |  | 91 |  | X |  |  |  |
| 16 | X | X |  |  |  |  | 92 |  | X |  |  |  |
| 17 | X | X |  |  |  |  | 93 |  | X |  |  |  |
| 18 | X | X |  |  |  |  | 94 |  | X |  |  |  |
| 19 | X | X |  |  |  |  | 95 |  | X |  |  |  |
| 20 | X | X |  |  |  |  | 96 |  | X |  |  |  |
| 21 | X | X |  |  |  |  | 97 |  | X |  |  |  |
| 22 | X | X |  |  |  |  | 98 |  | X |  |  |  |
| 23 | X | X |  |  |  |  | 99 |  | X |  |  |  |
| 24 | X | X |  |  |  |  | 100 |  | X |  |  |  |
| 25 | X | X |  |  |  |  | 101 |  | X |  |  |  |
| 26 | X | X |  |  |  |  | 102 |  | X |  |  |  |
| 27 | X | X |  |  |  |  | 103 |  | X |  |  |  |
| 28 | X | X |  |  |  |  | 104 |  | X |  |  |  |
| 29 | X | X |  |  |  |  | 105 |  | X |  |  |  |
| 30 | X | X |  |  |  |  | 106 |  | X |  |  |  |
| 31 | X | X |  |  |  |  | 107 |  | X |  |  |  |
| 32 | X | X |  |  |  |  | 108 |  | X |  |  |  |
| 33 | X | X |  |  |  |  | 109 |  | X |  |  |  |
| 34 | X | X |  |  |  |  | 110 |  | X |  |  |  |
| 35 | X | X |  |  |  |  | 111 |  | X |  |  |  |
| 36 | X | X |  |  |  |  | 112 |  | X |  |  |  |
| 37 | X | X |  |  |  |  | 113 |  | X |  |  |  |
| 38 | X | X |  |  |  |  | 114 |  | X |  |  |  |
| 39 | X | X |  |  |  |  | 115 |  | X |  |  |  |
| 40 | X | X |  |  |  |  | 116 |  | X |  |  |  |
| 41 | X | X |  |  |  |  | 117 |  | X |  |  |  |
| 42 | X | X |  |  |  |  | 118 |  | X |  |  |  |
| 43 | X | X |  |  |  |  | 119 |  | X |  |  |  |
| 44 | X | X |  |  |  |  | 120 |  | X |  |  |  |
| 45 | X | X |  |  |  |  | 121 |  | X |  |  |  |
| 46 | X | X |  |  |  |  | 122 |  | X |  |  |  |
| 47 | X | X |  |  |  |  | 123 |  | X |  |  |  |
| 48 | X | X |  |  |  |  | 124 |  | X |  |  |  |
| 49 | X | X |  |  |  |  | 125 |  | X |  |  |  |
| 50 | X | X |  |  |  |  | 126 |  | X |  |  |  |
| 51 | X | X |  |  |  |  | 127 |  | X |  |  |  |
| 52 | X | X |  |  |  |  | 128 |  | X |  |  |  |
| 53 | X | X |  |  |  |  | 129 |  | X |  |  |  |
| 54 | X | X |  |  |  |  | 130 |  | X |  |  |  |
| 55 | X | X |  |  |  |  | 131 |  | X |  |  |  |
| 56 | X | X |  |  |  |  | 132 |  | X |  |  |  |
| 57 | X | X |  |  |  |  | 133 |  | X |  |  |  |
| 58 | X | X |  |  |  |  | 134 |  | X |  |  |  |
| 59 | X | X |  |  |  |  | 135 |  | X |  |  |  |
| 60 | X | X |  |  |  |  | 136 |  | X |  |  |  |
| 61 | X | X |  |  |  |  | 137 |  | X |  |  |  |
| 62 | X | X |  |  |  |  | 138 |  | X |  |  |  |
| 63 | X | X |  |  |  |  | 139 |  | X |  |  |  |
| 64 | X | X |  |  |  |  | 140 |  | X |  |  |  |
| 65 | X | X |  |  |  |  | 141 |  | X |  |  |  |
| 66 |  | X |  |  |  |  | 142 |  | X |  |  |  |
| 67 |  | X |  |  |  |  | 143 |  | X |  |  |  |
| 68 |  | X |  |  |  |  | 144 |  | X |  |  |  |
| 69 |  | X |  |  |  |  | 145 |  | X |  |  |  |
| 70 |  | X |  |  |  |  | 146 |  | X |  |  |  |
| 71 |  | X |  |  |  |  | 147 |  | X |  |  |  |
| 72 |  | X |  |  |  |  | 148 |  | X |  |  |  |
| 73 |  | X |  |  |  |  | 149 |  | X |  |  |  |
| 74 |  | X |  |  |  |  | 150 |  | X |  |  |  |
| 75 |  | X |  |  |  |  | 151 |  | X |  |  |  |
| 76 |  | X |  |  |  |  | 152 |  | X |  |  |  |
| 77 |  | X |  |  |  |  | 153 |  | X |  |  |  |

CONTENTS

1.0	INTRODUCTION	4

2.0	Scope	5

3.0	NORMATIVE REFERENCES	5

4.0	DESIGN INFORMATION	6

5.0	material properties	10

6.0	design loads	11

- INTRODUCTION

Binak oilfield in Bushehr province is a part of the southern oilfields of Iran, is located 20 km northwest of Genaveh city.

With the aim of increasing production of oil from Binak oilfield, an EPC/EPD Project has been defined by NIOC/NISOC and awarded to Petro Iran Development Company (PEDCO). Also PEDCO (as General Contractor) has assigned the EPC-packages of the Project to "Hirgan Energy - Design and Inspection" JV.

As a part of the Project, a New Gas Compressor Station (adjacent to existing Binak GCS) shall be constructed to gather of 15 MMSCFD (approx.) associated gases and compress & tra	nsfer them to Siahmakan GIS.

GENERAL DEFINITION

The following terms shall be used in this document.

| CLIENT: | National Iranian South Oilfields Company (NISOC) |
| --- | --- |
| PROJECT: | Binak Oilfield Development – Surface Fcilities; New Gas Compressor Station |
| EPD/EPC CONTRACTOR (GC): | Petro Iran Development Company (PEDCO) |
| EPC CONTRACTOR: | Joint Venture of : Hirgan Energy – Design & Inspection (D&I) Companies |
| VENDOR: | The firm or person who will fabricate the equipment or material. |
| EXECUTOR: | Executor is the party which carries out all or part of construction and/or commissioning for the project. |
| THIRD PARTY INSPECTOR (TPI): | The firm appointed by EPD/EPC CONTRACTOR (GC) and approved by CLIENT (in writing) for the inspection of goods. |
| SHALL: | Is used where a provision is mandatory. |
| SHOULD: | Is used where a provision is advisory only. |
| WILL: | Is normally used in connection with the action by CLIENT rather than by an EPC/EPD CONTRACTOR, supplier or VENDOR. |
| MAY: | Is used where a provision is completely discretionary. |

- Scope

This document covers minimum necessary requirements for the design, selection, manufacture and inspection.

- NORMATIVE REFERENCES

## Local Codes and Standards

- IPS-E-PR-905 “Engineering Standard for Process Design of Dryers “

- IPS-E-PR-330 “Engineering Standard for Process Design of Compressed Air Systems”

- INBC Part 6 “Iranian National Building Code”

- INBC Part 7 “Iranian National Building Code”

- INBC Part 9 “Iranian National Building Code”

- INBC Part 10 “Iranian National Building Code”

- Iranian Seismic Design Code for Petroleum Facilities(3rd edition)

## International Codes and Standards

- ASTM “American Society for Testing Materials Relevant Parts”

- API 610 “Centrifugal Pumps for General Refinery Service, 10th Edition”

- ISO 15156”Petroleum and Natural Gas Industries. Materials for use in H2S Containing Environments in Oil and Gas Production.”

- ASCE 7-10 “Minimum Design Loads and Associated Criteria for Buildings and Other Structures-American Society of Civil Engineers.”

- ACI 318 “Building Code Requirements for Reinforced Concrete”, American Concrete Institute.”

- AISC 358 “Prequalified Connections for Special and Intermediate Steel Moment Frames for Seismic Applications. American Institute of Steel Construction, Inc.”

- AISC 360 “Specification for Structural Steel Buildings. American Institute of Steel Construction, Inc.”

## The Project Documents

- BK-GNRAL-PEDCO-000-ST-SP-0001 SPECIFICATION FOR CONCRETE WORK

- BK-GNRAL-PEDCO-000-ST-DC-0001 Structural Design Criteria

- BK-GNRAL-PEDCO-000-CV-SP-0004 Specification For Earth Work

- BK-GCS-PEDCO-120-GT-RT-0001 Geotechnical Investigation Report for

Compressor Station

## Order of Precedence

In case of any conflict between the contents of this document or any discrepancy between this document and other project documents or reference standards, this issue must be reported to the CLIENT. The final decision in this situation will be made by CLIENT.

- DESIGN INFORMATION

## Structure LOCATION

The Capacitor bank and Co2 Room and Transformers room is located in Binak oilfield.

Figure 1- Project Location

## ARCHITECTURAL PLANS

Figure 2 – CAPACITOR BANK AND CO2 ROOM PLAN

Figure 3 – SECTION A-A

Figure 4 – TRANSFORMERS ROOMS PLAN

Figure 5 – SECTION A-A

Figure 6 – DIESEL ROOM PLAN

Figure 7 – SECTION E-E

- material properties

## reinforced concrete

Lean concrete: f’c =150 kg/cm2

Cast in place concrete: f’c =350 kg/cm2

Where f'c is the minimum compressive characteristic strength of a cylinder specimen at 28 days.

Young Modulus of concrete: Ec=4700f'c  MPa

Poisson's Ratio: ν = 0.2

Unit weight of reinforced concrete: 2500 kg/m3

## cement

Cement shall conform to the following specifications for Portland cement:

a) "Standard Specification for Portland Cement" (ASTM C 150). [5.1, 6.1.1]

Cement type shall be considered according to geotechnical investigation report.

Cement used in the work shall correspond to that on which selection of concrete proportions was based. [5.1, 6.1.2]

Fly Ash or other pozzolans shall conform to  ASTM  C  618   "Standard Specification for Coal Fly Ash and Raw or Calcined Natural Pozzolan for Use in Concrete" For more information about other kinds of pozzolans see Iranian national concrete code Publication No.-120 of management and planning organization part 3-6- 4-2. [5.1, 6.1.3]

## STIFFNESS MODIFICATION

For analysis of concrete structure, the following modifications for flexural stiffness of elements are considered.

Columns………………………………..0.7Ig

Beams………………………………….0.35Ig

Wall (Cracked)……………..………….0.35Ig

Slabs………………………….……….0.25Ig

- design loads

## general

Considered loads for concrete structure are as follows.

- Dead Loads.

- Live Loads.

- Earthquake Load.

- Blast load (just for CAPACITOR BANK AND CO2 ROOM PLAN)

- Wind Load.

Considered loads for steel structure (shelter) are as follows.

- Dead Loads.

- Live Loads.

- Snow Load.

- Wind Load.

- Earthquake Load.

- CRANE  load

- Thermal Load

Table 1- Define Load Patterns

| Define Load Patterns |  |  |  |  |
| --- | --- | --- | --- | --- |
| Load Pattern Name | Type | CAPACITOR BANK AND CO2 ROOM | DIESEL ROOM | FIRE-FIGHTING PUMP TRANSFORMER ROOM |
| DEAD | Dead |  |  |  |
| Wall(External walls and parapet) | Dead |  |  |  |
| Live(Live and Live roof) | Live |  |  |  |
| Wind | Wind |  |  |  |
| EX | Quake |  |  |  |
| EY | Quake |  |  |  |
| EV | Quake |  |  |  |
| BR | Live |  |  |  |
| BWX | Live |  |  |  |
| BWY | Live |  |  |  |
| BFX | Live |  |  |  |
| BFY | Live |  |  |  |
| Th | Temperature |  |  |  |
| CRANE | DEAD and LIVE |  |  |  |

## DEAD LOAD

Dead Load is considered as the weight of materials forming a permanent part of the structure plant. The weight of materials of construction incorporated into the building, including but not limited to walls, floors, roofs, ceilings, stairways, built-in partitions, finishes, cladding and other similarly incorporated architectural and structural items, and the weight of fixed service equipment, such as plumbing stacks and risers, electrical feeders, heating, ventilating and air-conditioning systems.

Specific weight of materials which will be used is based on Iranian National Building Code, Part 6, where applicable. Other weights are in accordance with the specifications and/or drawings of vendors and manufacturers.

Here is the calculation of design dead load for floors, walls including External and Internal walls.

Table 2- Calculation of Roof Dead load (for Capacitor bank and Co2 Room)

| NO. | Description | specific weight (kg/m3) | thickness (cm) | kg/m2 |
| --- | --- | --- | --- | --- |
| 1 | Terrazzo Tiles | 2250 | 2.5 | 56.25 |
| 2 | cement mortar | 2100 | 1.5 | 31.5 |
| 3 | Waterproofing Membrane | ------ | ------- | 15.0 |
| 5 | Slab 30 cm | Calculated by Sap | ----- | ----- |
| 6 | Thermal insulation of polystyrene | 100 | 5.0 | 5 |
| 7 | Light Weight Concrete | 1700 | 5.0 | 85 |
|  | SUM |  |  | 192.75 |
|  | Applied to model |  |  | 200 |

Table 3- Calculation of Roof Dead load (for Fire-Fighting Pump Transformer Room and Diesel Room)

| NO. | Description | specific weight (kg/m3) | thickness (cm) | kg/m2 |
| --- | --- | --- | --- | --- |
| 1 | 0.9MM GALVANIZED METAL SHEET | 7850 | 0.09 | 7 |
| 2 | UNP 140 PURLIN | - | - | 8 |
| 7 | Thermal insulation of polystyrene | 100 | 10 | 10 |
| 9 | Roof installation plate | 1300 | 1 | 10 |
|  | SUM |  |  | 35.0 |
|  | Applied to model |  |  | 50 |

Table 4- Calculation of external Wall Dead load

| NO. | Description | specific weight (kg/m3) | thickness (cm) | kg/m2 |
| --- | --- | --- | --- | --- |
| 1 | FACADE FINE BRICK | 2100 | 20 | 420 |
|  |  | SUM |  | 420 |
|  |  | Applied to model |  | 420 |

## LIVE LOAD

Live Load is defined as the weight of all movable loads, including partition walls, personnel, tools, miscellaneous equipment and temporarily stored materials.

Generally where applicable, the live loads shall be in accordance with Iranian National Building Code, Part 6. The Live Loads is generally considered as uniformly distributed over the horizontal projection of the loaded areas, except for the loads with a concentrated nature.

The live load has been considered according to the following table.

Table 5- Live load on structure.

| NO. | Level | kg/m2 |
| --- | --- | --- |
| 1 | Roof (for Fire-Fighting Pump Transformer Room and Diesel Room) | 50 |
| 2 | Roof (for Capacitor bank and Co2 Room) | 150 |

## Snow LOAD

According to Iranian National Building Code No.6 (latest edition) unbalanced snow load have been Considered for roof slope between 4%~60%...in this structure Calculation of this load represents as below:

For Lu < 6       pr = IsPg = 25  Kgm2

## wind LOAD

The wind load according to the sixth topic of the national building regulations is as follows.

Considering that the transformer building is covered from the north side by the electrical room and east side by diesel room and its doors are covered by a metal grid, the main wind directions on the transformer building include the external wind perpendicular to the roof slope and the internal wind blowing in the direction of the roof slope.

- EXTERNAL WIND LOAD

P=Iw.q.Ce.Ct.Cg .Cp.Cd

Iw=1.2

q=According to table 6-10-1, it is equal to 0.68KNm2

Ce=Z100.2≥0.9=0.9

Z=5.85m

Ct=1

Cd=0.85

Table 6- Combined coefficients CpCg

| Slope roof | The body of the building |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 0° to 90° | 1 | 1E | 2 | 2E | 3 | 3E | 4 | 4E | 5 | 5E | 6 | 6E |
|  | -0.85 | -0.9 | -1.3 | -2 | -0.7 | -1 | -0.85 | -0.9 | 0.75 | 1.15 | -0.55 | -0.8 |

Table 7-External wind pressure perpendicular to the roof slope

| Slope roof | External wind pressure perpendicular to the roof slope (KN/m^2) |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 0° to 90° | 1 | 1E | 2 | 2E | 3 | 3E | 4 | 4E | 5 | 5E | 6 | 6E |
|  | -0.55 | -0.56 | -0.81 | -1.25 | -0.45 | -0.65 | -0.55 | -0.56 | 0.5 | 0.75 | -0.35 | -0.5 |

- INTERNAL WIND LOAD

Pi=Iw.q.Ce.Ct.Cgi .Cpi.Cd

Iw=1.2

q=According to table 6-10-1, it is equal to 0.68KNm2

Ce=Z100.2≥0.9=0.9

Z=5.85m

Ct=1

Cgi=2

Cpi=-0.7 to 0.7

Cd=0.85

Pi=-0.9KNm2 to  0.9 KNm2

Considering that the diesel building is covered from the north and east side by the electrical room and west side by transformer room, the main wind directions on the diesel building include the external and the internal wind perpendicular to the roof slope and Part of a brick .

## HORIZONTAL SEISMIC LOAD

According to Iranian Seismic Design Code for Petroleum Facilities (Pub.038-16-3rd edition) the structure shall be designed for earthquake load in two orthogonal directions.

Base level is defined as the level below which the structure does not move relative to the ground during an earthquake. For this structure base level is top of the deck level.

Basic parameters which are used in calculation of earthquake forces are presented below.

Following formula is used for calculations according to Iranian Seismic Design Code for Petroleum Facilities (Pub.038-16-3rd edition)

Vu=SaRuIW

Vu: Basic shear

Sa: mapped spectral response acceleration parameter

I: Importance factor of structure

Ru: Structural system factor

W= effective seismic weight of the structure, including dead loads and other loads, calculated from base level.

Table 8- Basic parameters used for earthquake loads calculation

(CAPACITOR BANK AND CO2 ROOM)

| Height of the structure from the base level (m) | 5.70 |
| --- | --- |
| Importance factor, I | 1.5 |
| Structural system | Special reinforced concrete shear walls |
| Soil type | II |
| A | 0.30 |
| T0.Ts | 0.1,0.5 |
| S0 | 1 |
| S | 1.5 |
| Ru | 5 |
| Ct | 0.05 |
| x | 0.75 |
| Tx&Y (calculation) =Ct.Hx | 0.184 |
| Tx (analysis) – mode 20 | 0.017 |
| Ty (analysis) – mode 2 | 0.066 |
| Tx&Y (select for design) =1.4 Tcalculation | 0.257 |
| B1x=S0+(S-S0+1)(T/T0) | 1.25 |
| B1y=S0+(S-S0+1)(T/T0) | 1.99 |
| Sax | 0.375 |
| Say | 0.597 |
| Kx & Ky →T<0.5 | 1 |
| Cmin=0.044SDSI | 0.165 |
| Cx=SaxRuI | 0.112 |
| Cy=SayRuI | 0.179 |

Table 9- Basic parameters used for earthquake loads calculation

(Diesel Room)

| Height of the structure from the base level (m) | 6.30 |
| --- | --- |
| Importance factor, I | 1.25 |
| Structural system | OCBF system for x direction and OMF system for y direction |
| Soil type | II |
| A | 0.30 |
| T0,Ts | 0.1, 0.5 |
| S0 | 1 |
| S | 1.5 |
| Rux | 3.25 |
| Ruy | 3.5 |
| Ctx | 0.050 |
| xx | 0.75 |
| Cty | 0.072 |
| xy | 0.8 |
| Tx (empirical) =Ct.Hx | 0.198 |
| TY (empirical) =Ct.Hx | 0.313 |
| Tx (analysis) – mode 6 | 0.086 |
| Ty (analysis) – mode1 | 0.760 |
| Tx (select for design) =min⁡(1.4 Tempirical , Tanalysis) | 0.086 |
| Ty (select for design) =min⁡(1.4 Tempirical , Tanalysis) | 0.438 |
| B1y=S+1 | 2.5 |
| B1x=S0+(S-S0+1)(T/T0) | 2.29 |
| Sax | 0.687 |
| SaY | 0.75 |
| Kx & Ky →T<0.5 | 1 |
| Cmin=0.044SDSI | 0.165 |
| Cx=SaxRuI | 0.264 |
| Cy=SayRuI | 0.267 |

Table 10- Basic parameters used for earthquake loads calculation

(TRANSFORMERS ROOM)

| Height of the structure from the base level (m) | 5.20 |
| --- | --- |
| Importance factor, I | 1.25 |
| Structural system | Non-building Structure |
| Soil type | II |
| A | 0.30 |
| T0,Ts | 0.1, 0.5 |
| S0 | 1 |
| S | 1.5 |
| Rux | 3 |
| Ruy | 3 |
| Ctx | 0.050 |
| xx | 0.75 |
| Cty | 0.050 |
| xy | 0.75 |
| Tx (empirical) =Ct.Hx | 0.16 |
| TY (empirical) =Ct.Hx | 0.16 |
| Tx (analysis) – mode 23 | 0.253 |
| Ty (analysis) – mode 1 | 0.396 |
| Tx (select for design) =min⁡(1.4 Tcempirical , Tanalysis) | 0.227 |
| Ty (select for design) =min⁡(1.4 Tempirical , Tanalysis) | 0.227 |
| B1x=S+1 | 2.5 |
| B1y=S+1 | 2.5 |
| Sax | 0.75 |
| Say | 0.75 |
| Kx & Ky →T<0.5 | 1 |
| Cmin=0.044SDSI | 0.165 |
| Cx=SaxRuI | 0.312 |
| Cy=SayRuI | 0.312 |

## BLAST LOAD

According to Appendix IC of IPS-E-CE-500 (ADDITIONAL REQUIREMENTS FOR BLAST RESISTANT BUILDINGS AND STRUCTURES), the blast pressure of exterior walls and roof are as below:

Table 11- Blast Load

| Item | Pr | P0 | t0 |
| --- | --- | --- | --- |
|  | Kpa | Kpa | msec |
| Wall | 172 |  | 20 |
| Roof |  | 69 | 20 |

- Static load equivalent of blast pressure and duration:

Where

- R: required dynamic resistance of structural element, expressed as static load equivalent of blast pressure and duration

- P: peak blast load for the element under consideration

- : Energy absorption factor =

- : Maximum displacement factor  =

- Duration factor =

- Maximum allowable dynamic displacement.

- Duration of blast load base on SG-22.

- : Fundamental period of vibration of structure or element.

Maximum Allowable dynamic displacement

| Structural Component(RC Structure) | Displacement Factor (Xm/Xy) |
| --- | --- |
| Axial compression | 1.5 |
| Flexure | 3 |
| Shear | 1.5 |

Load application for blast design is as follows:

Wall Panel Design

Each wall shall sustain peak reflected pressure (Pr, equivalent static value).

Wall Panel Design below the Ground

Blast pressure for wall below the ground is ko xP (Blast pressure at ground)

Roof Slab Design

Roof slab and beams shall sustain peak overpressure (Pso, equivalent static value).

In all cases related to the design, it was examined and it was concluded that the results of blast loads are more effective than earthquakes

Figure 8- Mode 1 in Blast Load

Figure 9- Mode 2 in Blast Load

Figure 10- Mode 3 in Blast Load

Figure 11- Mode 4 in Blast Load

dynamic increase factor :

fdy=SIF*DIF*fy

fdu=SIF*DIF*fu

f'dc=SIF*DIF*f'c

Table 12- dynamic increase factor

| Material | Concrete |  | Rebar |  | St37 |  | St52 |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | SIF | DIF | SIF | DIF | SIF | DIF | SIF | DIF |
| fdy | - | - | 1.15 | 1.20 | 1.15 | 1.25 | 1.15 | 1.2 |
| fdu | - | - | 1.15 | 1.05 | 1.15 | 1.1 | 1.15 | 1.05 |
| f'dc | 1.1 | 1.15 | - | - | - | - | - | - |

## LOAD COMBINATIONS FOR REINFORCED CONCRETE STRUCTURE

These load combinations will be considered according to the Iranian Seismic Design Code for Petroleum Facilities (Pub.038-16-3rd edition Design)

Table 13- Load combination for design (CAPACITOR BANK AND CO2 ROOM PLAN-earth quake)

| TABLE: Case - Static 1 - Load Assignments |  |  |  |
| --- | --- | --- | --- |
| Case | LoadType | LoadName | LoadSF |
| Text | Text | Text | Unitless |
| 1.2D+1.2WA+L+EX+0.3EY+EV-NL | Load pattern | DEAD | 1.2 |
| 1.2D+1.2WA+L+EX+0.3EY+EV-NL | Load pattern | WALL | 1.2 |
| 1.2D+1.2WA+L+EX+0.3EY+EV-NL | Load pattern | LIVE | 1 |
| 1.2D+1.2WA+L+EX+0.3EY+EV-NL | Load pattern | EQx | 1 |
| 1.2D+1.2WA+L+EX+0.3EY+EV-NL | Load pattern | EQy | 0.3 |
| 1.2D+1.2WA+L+EX+0.3EY+EV-NL | Load pattern | DEAD | 0.15 |
| 1.2D+1.2WA+L+EX-0.3EY+EV-NL | Load pattern | DEAD | 1.2 |
| 1.2D+1.2WA+L+EX-0.3EY+EV-NL | Load pattern | WALL | 1.2 |
| 1.2D+1.2WA+L+EX-0.3EY+EV-NL | Load pattern | LIVE | 1 |
| 1.2D+1.2WA+L+EX-0.3EY+EV-NL | Load pattern | EQx | 1 |
| 1.2D+1.2WA+L+EX-0.3EY+EV-NL | Load pattern | EQy | -0.3 |
| 1.2D+1.2WA+L+EX-0.3EY+EV-NL | Load pattern | DEAD | 0.15 |
| 1.2D+1.2WA+L-EX+0.3EY+EV-NL | Load pattern | DEAD | 1.2 |
| 1.2D+1.2WA+L-EX+0.3EY+EV-NL | Load pattern | WALL | 1.2 |
| 1.2D+1.2WA+L-EX+0.3EY+EV-NL | Load pattern | LIVE | 1 |
| 1.2D+1.2WA+L-EX+0.3EY+EV-NL | Load pattern | EQx | -1 |
| 1.2D+1.2WA+L-EX+0.3EY+EV-NL | Load pattern | EQy | 0.3 |
| 1.2D+1.2WA+L-EX+0.3EY+EV-NL | Load pattern | DEAD | 0.15 |
| 1.2D+1.2WA+L-EX-0.3EY+EV-NL | Load pattern | DEAD | 1.2 |
| 1.2D+1.2WA+L-EX-0.3EY+EV-NL | Load pattern | WALL | 1.2 |
| 1.2D+1.2WA+L-EX-0.3EY+EV-NL | Load pattern | LIVE | 1 |
| 1.2D+1.2WA+L-EX-0.3EY+EV-NL | Load pattern | EQx | -1 |
| 1.2D+1.2WA+L-EX-0.3EY+EV-NL | Load pattern | EQy | -0.3 |
| 1.2D+1.2WA+L-EX-0.3EY+EV-NL | Load pattern | DEAD | 0.15 |
| 1.2D+1.2WA+L+EY+0.3EX+EV-NL | Load pattern | DEAD | 1.2 |
| 1.2D+1.2WA+L+EY+0.3EX+EV-NL | Load pattern | WALL | 1.2 |
| 1.2D+1.2WA+L+EY+0.3EX+EV-NL | Load pattern | LIVE | 1 |
| 1.2D+1.2WA+L+EY+0.3EX+EV-NL | Load pattern | EQy | 1 |
| 1.2D+1.2WA+L+EY+0.3EX+EV-NL | Load pattern | EQx | 0.3 |
| 1.2D+1.2WA+L+EY+0.3EX+EV-NL | Load pattern | DEAD | 0.15 |
| 1.2D+1.2WA+L-EY+0.3EX+EV-NL | Load pattern | DEAD | 1.2 |
| 1.2D+1.2WA+L-EY+0.3EX+EV-NL | Load pattern | WALL | 1.2 |
| 1.2D+1.2WA+L-EY+0.3EX+EV-NL | Load pattern | LIVE | 1 |
| 1.2D+1.2WA+L-EY+0.3EX+EV-NL | Load pattern | EQy | -1 |
| 1.2D+1.2WA+L-EY+0.3EX+EV-NL | Load pattern | EQx | 0.3 |
| 1.2D+1.2WA+L-EY+0.3EX+EV-NL | Load pattern | DEAD | 0.15 |
| 1.2D+1.2WA+L+EY-0.3EX+EV-NL | Load pattern | DEAD | 1.2 |
| 1.2D+1.2WA+L+EY-0.3EX+EV-NL | Load pattern | WALL | 1.2 |
| 1.2D+1.2WA+L+EY-0.3EX+EV-NL | Load pattern | LIVE | 1 |
| 1.2D+1.2WA+L+EY-0.3EX+EV-NL | Load pattern | EQy | 1 |
| 1.2D+1.2WA+L+EY-0.3EX+EV-NL | Load pattern | EQx | -0.3 |
| 1.2D+1.2WA+L+EY-0.3EX+EV-NL | Load pattern | DEAD | 0.15 |
| 1.2D+1.2WA+L-EY-0.3EX+EV-NL | Load pattern | DEAD | 1.2 |
| 1.2D+1.2WA+L-EY-0.3EX+EV-NL | Load pattern | WALL | 1.2 |
| 1.2D+1.2WA+L-EY-0.3EX+EV-NL | Load pattern | LIVE | 1 |
| 1.2D+1.2WA+L-EY-0.3EX+EV-NL | Load pattern | EQy | -1 |
| 1.2D+1.2WA+L-EY-0.3EX+EV-NL | Load pattern | EQx | -0.3 |
| 1.2D+1.2WA+L-EY-0.3EX+EV-NL | Load pattern | DEAD | 0.15 |
| 0.9D+0.9WA+EX+0.3EY+EV-NL | Load pattern | DEAD | 0.9 |
| 0.9D+0.9WA+EX+0.3EY+EV-NL | Load pattern | WALL | 0.9 |
| 0.9D+0.9WA+EX+0.3EY+EV-NL | Load pattern | EQx | 1 |
| 0.9D+0.9WA+EX+0.3EY+EV-NL | Load pattern | EQy | 0.3 |
| 0.9D+0.9WA+EX+0.3EY+EV-NL | Load pattern | DEAD | 0.15 |
| 0.9D+0.9WA-EX+0.3EY+EV-NL | Load pattern | DEAD | 0.9 |
| 0.9D+0.9WA-EX+0.3EY+EV-NL | Load pattern | WALL | 0.9 |
| 0.9D+0.9WA-EX+0.3EY+EV-NL | Load pattern | EQx | -1 |
| 0.9D+0.9WA-EX+0.3EY+EV-NL | Load pattern | EQy | 0.3 |
| 0.9D+0.9WA-EX+0.3EY+EV-NL | Load pattern | DEAD | 0.15 |
| 0.9D+0.9WA-EX-0.3EY+EV-NL | Load pattern | DEAD | 0.9 |
| 0.9D+0.9WA-EX-0.3EY+EV-NL | Load pattern | WALL | 0.9 |
| 0.9D+0.9WA-EX-0.3EY+EV-NL | Load pattern | EQx | -1 |
| 0.9D+0.9WA-EX-0.3EY+EV-NL | Load pattern | EQy | -0.3 |
| 0.9D+0.9WA-EX-0.3EY+EV-NL | Load pattern | DEAD | 0.15 |
| 0.9D+0.9WA+EX-0.3EY+EV-NL | Load pattern | DEAD | 0.9 |
| 0.9D+0.9WA+EX-0.3EY+EV-NL | Load pattern | WALL | 0.9 |
| 0.9D+0.9WA+EX-0.3EY+EV-NL | Load pattern | EQx | 1 |
| 0.9D+0.9WA+EX-0.3EY+EV-NL | Load pattern | EQy | -0.3 |
| 0.9D+0.9WA+EX-0.3EY+EV-NL | Load pattern | DEAD | 0.15 |
| 0.9D+0.9WA+EY+0.3EX+EV-NL | Load pattern | DEAD | 0.9 |
| 0.9D+0.9WA+EY+0.3EX+EV-NL | Load pattern | WALL | 0.9 |
| 0.9D+0.9WA+EY+0.3EX+EV-NL | Load pattern | EQy | 1 |
| 0.9D+0.9WA+EY+0.3EX+EV-NL | Load pattern | EQx | 0.3 |
| 0.9D+0.9WA+EY+0.3EX+EV-NL | Load pattern | DEAD | 0.15 |
| 0.9D+0.9WA-EY+0.3EX+EV-NL | Load pattern | DEAD | 0.9 |
| 0.9D+0.9WA-EY+0.3EX+EV-NL | Load pattern | WALL | 0.9 |
| 0.9D+0.9WA-EY+0.3EX+EV-NL | Load pattern | EQy | -1 |
| 0.9D+0.9WA-EY+0.3EX+EV-NL | Load pattern | EQx | 0.3 |
| 0.9D+0.9WA-EY+0.3EX+EV-NL | Load pattern | DEAD | 0.15 |
| 0.9D+0.9WA+EY-0.3EX+EV-NL | Load pattern | DEAD | 0.9 |
| 0.9D+0.9WA+EY-0.3EX+EV-NL | Load pattern | WALL | 0.9 |
| 0.9D+0.9WA+EY-0.3EX+EV-NL | Load pattern | EQy | 1 |
| 0.9D+0.9WA+EY-0.3EX+EV-NL | Load pattern | EQx | -0.3 |
| 0.9D+0.9WA+EY-0.3EX+EV-NL | Load pattern | DEAD | 0.15 |
| 0.9D+0.9WA-EY-0.3EX+EV-NL | Load pattern | DEAD | 0.9 |
| 0.9D+0.9WA-EY-0.3EX+EV-NL | Load pattern | WALL | 0.9 |
| 0.9D+0.9WA-EY-0.3EX+EV-NL | Load pattern | EQy | -1 |
| 0.9D+0.9WA-EY-0.3EX+EV-NL | Load pattern | EQx | -0.3 |
| 0.9D+0.9WA-EY-0.3EX+EV-NL | Load pattern | DEAD | 0.15 |

Table 14- Load combination for design (CAPACITOR BANK AND CO2 ROOM PLAN-BLAST LOAD)

| TABLE: Case - Static 1 - Load Assignments |  |  |  |
| --- | --- | --- | --- |
| Case | LoadType | LoadName | LoadSF |
| Text | Text | Text | Unitless |
| D+WA+L+6.11826BR-NL | Load pattern | DEAD | 1 |
| D+WA+L+6.11826BR-NL | Load pattern | LIVE | 1 |
| D+WA+L+6.11826BR-NL | Load pattern | BR | 6.1183 |
| D+WA+L+6.11826BR-NL | Load pattern | WALL | 1 |
| D+WA+L+2.65204BR-NL | Load pattern | DEAD | 1 |
| D+WA+L+2.65204BR-NL | Load pattern | LIVE | 1 |
| D+WA+L+2.65204BR-NL | Load pattern | BR | 2.652 |
| D+WA+L+2.65204BR-NL | Load pattern | WALL | 1 |
| D+WA+L+8.61637BR-NL | Load pattern | DEAD | 1 |
| D+WA+L+8.61637BR-NL | Load pattern | LIVE | 1 |
| D+WA+L+8.61637BR-NL | Load pattern | BR | 8.6164 |
| D+WA+L+8.61637BR-NL | Load pattern | WALL | 1 |
| D+WA+L+4.08844BR-NL | Load pattern | DEAD | 1 |
| D+WA+L+4.08844BR-NL | Load pattern | LIVE | 1 |
| D+WA+L+4.08844BR-NL | Load pattern | BR | 4.0884 |
| D+WA+L+4.08844BR-NL | Load pattern | WALL | 1 |
| D+WA+L+8.6BWX-NL | Load pattern | DEAD | 1 |
| D+WA+L+8.6BWX-NL | Load pattern | LIVE | 1 |
| D+WA+L+8.6BWX-NL | Load pattern | BWX | 8.6 |
| D+WA+L+8.6BWX-NL | Load pattern | WALL | 1 |
| D+WA+L+8.6BWY-NL | Load pattern | DEAD | 1 |
| D+WA+L+8.6BWY-NL | Load pattern | LIVE | 1 |
| D+WA+L+8.6BWY-NL | Load pattern | BWY | 8.6 |
| D+WA+L+8.6BWY-NL | Load pattern | WALL | 1 |
| D+WA+L+6.61BWX-NL | Load pattern | DEAD | 1 |
| D+WA+L+6.61BWX-NL | Load pattern | LIVE | 1 |
| D+WA+L+6.61BWX-NL | Load pattern | BWX | 6.61 |
| D+WA+L+6.61BWX-NL | Load pattern | WALL | 1 |
| D+WA+L+6.61BWY-NL | Load pattern | DEAD | 1 |
| D+WA+L+6.61BWY-NL | Load pattern | LIVE | 1 |
| D+WA+L+6.61BWY-NL | Load pattern | BWY | 6.61 |
| D+WA+L+6.61BWY-NL | Load pattern | WALL | 1 |

Table 15- Load combination for design (transformer room)

| TABLE: Case - Static 1 - Load Assignments |  |  |  |
| --- | --- | --- | --- |
| Case | LoadType | LoadName | LoadSF |
| Text | Text | Text | Unitless |
| DEAD | Load pattern | DEAD | 1 |
| LIVE | Load pattern | LIVE | 1 |
| EX | Load pattern | EX | 1 |
| EY | Load pattern | EY | 1 |
| ACASE1 | Load pattern | DEAD | 1.4 |
| ACASE2 | Load pattern | DEAD | 1.2 |
| ACASE2 | Load pattern | LIVE | 0.5 |
| ACASE3 | Load pattern | DEAD | 1.2 |
| ACASE3 | Load pattern | LIVE | 1.6 |
| ACASE4 | Load pattern | DEAD | 1.2 |
| ACASE4 | Load pattern | LIVE | 1 |
| ACASE4 | Load pattern | EX | 1 |
| ACASE4 | Load pattern | EY | 0.3 |
| ACASE5 | Load pattern | DEAD | 1.2 |
| ACASE5 | Load pattern | LIVE | 1 |
| ACASE5 | Load pattern | EX | 1 |
| ACASE5 | Load pattern | EY | -0.3 |
| ACASE6 | Load pattern | DEAD | 1.2 |
| ACASE6 | Load pattern | LIVE | 1 |
| ACASE6 | Load pattern | EX | -1 |
| ACASE6 | Load pattern | EY | 0.3 |
| ACASE7 | Load pattern | DEAD | 1.2 |
| ACASE7 | Load pattern | LIVE | 1 |
| ACASE7 | Load pattern | EX | -1 |
| ACASE7 | Load pattern | EY | -0.3 |
| ACASE8 | Load pattern | DEAD | 1.2 |
| ACASE8 | Load pattern | LIVE | 1 |
| ACASE8 | Load pattern | EY | 1 |
| ACASE8 | Load pattern | EX | 0.3 |
| ACASE9 | Load pattern | DEAD | 1.2 |
| ACASE9 | Load pattern | LIVE | 1 |
| ACASE9 | Load pattern | EY | 1 |
| ACASE9 | Load pattern | EX | -0.3 |
| ACASE10 | Load pattern | DEAD | 1.2 |
| ACASE10 | Load pattern | LIVE | 1 |
| ACASE10 | Load pattern | EY | -1 |
| ACASE10 | Load pattern | EX | 0.3 |
| ACASE11 | Load pattern | DEAD | 1.2 |
| ACASE11 | Load pattern | LIVE | 1 |
| ACASE11 | Load pattern | EY | -1 |
| ACASE11 | Load pattern | EX | -0.3 |
| ACASE12 | Load pattern | DEAD | 0.9 |
| ACASE12 | Load pattern | EX | 1 |
| ACASE12 | Load pattern | EY | 0.3 |
| ACASE13 | Load pattern | DEAD | 0.9 |
| ACASE13 | Load pattern | EX | 1 |
| ACASE13 | Load pattern | EY | -0.3 |
| ACASE14 | Load pattern | DEAD | 0.9 |
| ACASE14 | Load pattern | EX | -1 |
| ACASE14 | Load pattern | EY | 0.3 |
| ACASE15 | Load pattern | DEAD | 0.9 |
| ACASE15 | Load pattern | EX | -1 |
| ACASE15 | Load pattern | EY | -0.3 |
| ACASE16 | Load pattern | DEAD | 0.9 |
| ACASE16 | Load pattern | EY | 1 |
| ACASE16 | Load pattern | EX | 0.3 |
| ACASE17 | Load pattern | DEAD | 0.9 |
| ACASE17 | Load pattern | EY | 1 |
| ACASE17 | Load pattern | EX | -0.3 |
| ACASE18 | Load pattern | DEAD | 0.9 |
| ACASE18 | Load pattern | EY | -1 |
| ACASE18 | Load pattern | EX | 0.3 |
| ACASE19 | Load pattern | DEAD | 0.9 |
| ACASE19 | Load pattern | EY | -1 |
| ACASE19 | Load pattern | EX | -0.3 |
| WB1 | Load pattern | WB1 | 1 |
| WB2 | Load pattern | WB2 | 1 |
| WA | Load pattern | WA | 1 |
| ACASE20 | Load pattern | DEAD | 1.2 |
| ACASE20 | Load pattern | LIVE | 1.6 |
| ACASE20 | Load pattern | WB1 | 0.8 |
| ACASE21 | Load pattern | DEAD | 1.2 |
| ACASE21 | Load pattern | LIVE | 1.6 |
| ACASE21 | Load pattern | WB2 | 0.8 |
| ACASE22 | Load pattern | DEAD | 1.2 |
| ACASE22 | Load pattern | LIVE | 1.6 |
| ACASE22 | Load pattern | WA | 0.8 |
| ACASE23 | Load pattern | DEAD | 1.2 |
| ACASE23 | Load pattern | LIVE | 0.5 |
| ACASE23 | Load pattern | WB1 | 1.6 |
| ACASE24 | Load pattern | DEAD | 1.2 |
| ACASE24 | Load pattern | LIVE | 0.5 |
| ACASE24 | Load pattern | WB2 | 1.6 |
| ACASE25 | Load pattern | DEAD | 1.2 |
| ACASE25 | Load pattern | LIVE | 0.5 |
| ACASE25 | Load pattern | WA | 1.6 |
| ACASE26 | Load pattern | DEAD | 0.9 |
| ACASE26 | Load pattern | WB1 | 1.6 |
| ACASE27 | Load pattern | DEAD | 0.9 |
| ACASE27 | Load pattern | WB2 | 1.6 |
| ACASE28 | Load pattern | DEAD | 0.9 |
| ACASE28 | Load pattern | WA | 1.6 |
| Deflectin1 | Load pattern | DEAD | 1 |
| Deflectin2 | Load pattern | DEAD | 1 |
| Deflectin2 | Load pattern | LIVE | 1 |
| Deflectin3 | Load pattern | DEAD | 1 |
| Deflectin3 | Load pattern | WA | 1 |
| Deflectin4 | Load pattern | DEAD | 1 |
| Deflectin4 | Load pattern | WB1 | 1 |
| Deflectin5 | Load pattern | DEAD | 1 |
| Deflectin5 | Load pattern | WB2 | 1 |

Table 16- Load combination for design (DIESEL ROOM)

| TABLE: Case - Static 1 - Load Assignments |  |  |  |
| --- | --- | --- | --- |
| Case | LoadType | LoadName | LoadSF |
| Text | Text | Text | Unitless |
| DEAD | Load pattern | DEAD | 1 |
| DEAD | Load pattern | CRv | 1 |
| Live | Load pattern | Live | 1 |
| Live | Load pattern | S | 1 |
| EQX | Load pattern | EQX | 1 |
| EQY | Load pattern | EQY | 1 |
| CRv | Load pattern | CRv | 0 |
| TL | Load pattern | TL | 1 |
| NotionalX(DL) | Load pattern | NotionalX(DL) | 1 |
| NotionalY(DL) | Load pattern | NotionalY(DL) | 1 |
| NotionalX(LL) | Load pattern | NotionalX(LL) | 1 |
| NotionalY(LL) | Load pattern | NotionalY(LL) | 1 |
| FL | Load pattern | FL | 1 |
| Ev | Load pattern | DEAD | 0.215 |
| P-DELTA | Load pattern | DEAD | 1.2 |
| P-DELTA | Load pattern | CRv | 1.2 |
| P-DELTA | Load pattern | Live | 1.6 |
| FT | Load pattern | FT | 1 |
| WLXP | Load pattern | WLXP | 1 |
| WLYP | Load pattern | WLYP | 1 |
| S | Load pattern | S | 0 |
| Notionalx(CR) | Load pattern | Notionalx(CR) | 1 |
| Notionaly(CR) | Load pattern | Notionaly(CR) | 1 |
| WALL | Load pattern | WALL | 1 |
| SDA1-NL | Load pattern | DEAD | 1.4 |
| SDA1-NL | Load pattern | CRv | 1.4 |
| SDA1-NL | Load pattern | NotionalX(DL) | 1.4 |
| SDA1-NL | Load pattern | NotionalY(DL) | 1.4 |
| SDA2crane-NL | Load pattern | DEAD | 1.2 |
| SDA2crane-NL | Load pattern | CRv | 1.2 |
| SDA2crane-NL | Load pattern | Live | 1.6 |
| SDA2crane-NL | Load pattern | S | 1.6 |
| SDA2crane-NL | Load pattern | TL | 1.2 |
| SDA2crane-NL | Load pattern | FL | 1.2 |
| SDA2crane-NL | Load pattern | NotionalX(DL) | 1.2 |
| SDA2crane-NL | Load pattern | NotionalY(DL) | 1.2 |
| SDA2crane-NL | Load pattern | NotionalX(LL) | 1.6 |
| SDA2crane-NL | Load pattern | NotionalY(LL) | 1.6 |
| SDA3crane-NL | Load pattern | DEAD | 1.2 |
| SDA3crane-NL | Load pattern | CRv | 1.2 |
| SDA3crane-NL | Load pattern | Live | 1.6 |
| SDA3crane-NL | Load pattern | S | 1.6 |
| SDA3crane-NL | Load pattern | TL | 1.2 |
| SDA3crane-NL | Load pattern | FL | -1.2 |
| SDA3crane-NL | Load pattern | NotionalX(DL) | 1.2 |
| SDA3crane-NL | Load pattern | NotionalY(DL) | 1.2 |
| SDA3crane-NL | Load pattern | NotionalX(LL) | 1.6 |
| SDA3crane-NL | Load pattern | NotionalY(LL) | 1.6 |
| SDA4-NL | Load pattern | DEAD | 1.2 |
| SDA4-NL | Load pattern | CRv | 1.2 |
| SDA4-NL | Load pattern | Live | 1.6 |
| SDA4-NL | Load pattern | S | 1.6 |
| SDA4-NL | Load pattern | TL | 1.2 |
| SDA4-NL | Load pattern | NotionalX(DL) | 1.2 |
| SDA4-NL | Load pattern | NotionalY(DL) | 1.2 |
| SDA4-NL | Load pattern | NotionalX(LL) | 1.6 |
| SDA4-NL | Load pattern | NotionalY(LL) | 1.6 |
| SDA6crane-NL | Load pattern | DEAD | 1.2 |
| SDA6crane-NL | Load pattern | CRv | 1.2 |
| SDA6crane-NL | Load pattern | Live | 1.6 |
| SDA6crane-NL | Load pattern | S | 1.6 |
| SDA6crane-NL | Load pattern | TL | 1.2 |
| SDA6crane-NL | Load pattern | FT | 1.2 |
| SDA6crane-NL | Load pattern | NotionalX(DL) | 1.2 |
| SDA6crane-NL | Load pattern | NotionalY(DL) | 1.2 |
| SDA6crane-NL | Load pattern | NotionalX(LL) | 1.6 |
| SDA6crane-NL | Load pattern | NotionalY(LL) | 1.6 |
| SDA7crane-NL | Load pattern | DEAD | 1.2 |
| SDA7crane-NL | Load pattern | CRv | 1.2 |
| SDA7crane-NL | Load pattern | Live | 1.6 |
| SDA7crane-NL | Load pattern | S | 1.6 |
| SDA7crane-NL | Load pattern | TL | 1.2 |
| SDA7crane-NL | Load pattern | FT | -1.2 |
| SDA7crane-NL | Load pattern | NotionalX(DL) | 1.2 |
| SDA7crane-NL | Load pattern | NotionalY(DL) | 1.2 |
| SDA7crane-NL | Load pattern | NotionalX(LL) | 1.6 |
| SDA7crane-NL | Load pattern | NotionalY(LL) | 1.6 |
| SDA10crane-NL | Load pattern | DEAD | 1.2 |
| SDA10crane-NL | Load pattern | CRv | 1.2 |
| SDA10crane-NL | Load pattern | TL | 1.2 |
| SDA10crane-NL | Load pattern | FL | 1.2 |
| SDA10crane-NL | Load pattern | Live | 1 |
| SDA10crane-NL | Load pattern | S | 1 |
| SDA10crane-NL | Load pattern | WLXP | 1 |
| SDA10crane-NL | Load pattern | NotionalX(DL) | 1.2 |
| SDA10crane-NL | Load pattern | NotionalY(DL) | 1.2 |
| SDA10crane-NL | Load pattern | NotionalX(LL) | 1 |
| SDA10crane-NL | Load pattern | NotionalY(LL) | 1 |
| SDA11crane-NL | Load pattern | DEAD | 1.2 |
| SDA11crane-NL | Load pattern | CRv | 1.2 |
| SDA11crane-NL | Load pattern | TL | 1.2 |
| SDA11crane-NL | Load pattern | FL | -1.2 |
| SDA11crane-NL | Load pattern | Live | 1 |
| SDA11crane-NL | Load pattern | S | 1 |
| SDA11crane-NL | Load pattern | WLXP | 1 |
| SDA11crane-NL | Load pattern | NotionalX(DL) | 1.2 |
| SDA11crane-NL | Load pattern | NotionalY(DL) | 1.2 |
| SDA11crane-NL | Load pattern | NotionalX(LL) | 1 |
| SDA11crane-NL | Load pattern | NotionalY(LL) | 1 |
| SDA12crane-NL | Load pattern | DEAD | 1.2 |
| SDA12crane-NL | Load pattern | CRv | 1.2 |
| SDA12crane-NL | Load pattern | TL | 1.2 |
| SDA12crane-NL | Load pattern | FL | 1.2 |
| SDA12crane-NL | Load pattern | Live | 1 |
| SDA12crane-NL | Load pattern | S | 1 |
| SDA12crane-NL | Load pattern | WLXP | -1 |
| SDA12crane-NL | Load pattern | NotionalX(DL) | 1.2 |
| SDA12crane-NL | Load pattern | NotionalY(DL) | 1.2 |
| SDA12crane-NL | Load pattern | NotionalX(LL) | 1 |
| SDA12crane-NL | Load pattern | NotionalY(LL) | 1 |
| SDA13crane-NL | Load pattern | DEAD | 1.2 |
| SDA13crane-NL | Load pattern | CRv | 1.2 |
| SDA13crane-NL | Load pattern | TL | 1.2 |
| SDA13crane-NL | Load pattern | FL | -1.2 |
| SDA13crane-NL | Load pattern | Live | 1 |
| SDA13crane-NL | Load pattern | S | 1 |
| SDA13crane-NL | Load pattern | WLXP | -1 |
| SDA13crane-NL | Load pattern | NotionalX(DL) | 1.2 |
| SDA13crane-NL | Load pattern | NotionalY(DL) | 1.2 |
| SDA13crane-NL | Load pattern | NotionalX(LL) | 1 |
| SDA13crane-NL | Load pattern | NotionalY(LL) | 1 |
| SDA14-NL | Load pattern | DEAD | 1.2 |
| SDA14-NL | Load pattern | CRv | 1.2 |
| SDA14-NL | Load pattern | TL | 1.2 |
| SDA14-NL | Load pattern | Live | 1 |
| SDA14-NL | Load pattern | S | 1 |
| SDA14-NL | Load pattern | WLXP | 1 |
| SDA14-NL | Load pattern | NotionalX(DL) | 1.2 |
| SDA14-NL | Load pattern | NotionalY(DL) | 1.2 |
| SDA14-NL | Load pattern | NotionalX(LL) | 1 |
| SDA14-NL | Load pattern | NotionalY(LL) | 1 |
| SDA16-NL | Load pattern | DEAD | 1.2 |
| SDA16-NL | Load pattern | CRv | 1.2 |
| SDA16-NL | Load pattern | TL | 1.2 |
| SDA16-NL | Load pattern | Live | 1 |
| SDA16-NL | Load pattern | S | 1 |
| SDA16-NL | Load pattern | WLXP | -1 |
| SDA16-NL | Load pattern | NotionalX(DL) | 1.2 |
| SDA16-NL | Load pattern | NotionalY(DL) | 1.2 |
| SDA16-NL | Load pattern | NotionalX(LL) | 1 |
| SDA16-NL | Load pattern | NotionalY(LL) | 1 |
| SDA18crane-NL | Load pattern | DEAD | 1.2 |
| SDA18crane-NL | Load pattern | CRv | 1.2 |
| SDA18crane-NL | Load pattern | TL | 1.2 |
| SDA18crane-NL | Load pattern | FT | 1.2 |
| SDA18crane-NL | Load pattern | Live | 1 |
| SDA18crane-NL | Load pattern | S | 1 |
| SDA18crane-NL | Load pattern | WLXP | 1 |
| SDA18crane-NL | Load pattern | NotionalX(DL) | 1.2 |
| SDA18crane-NL | Load pattern | NotionalY(DL) | 1.2 |
| SDA18crane-NL | Load pattern | NotionalX(LL) | 1 |
| SDA18crane-NL | Load pattern | NotionalY(LL) | 1 |
| SDA19crane-NL | Load pattern | DEAD | 1.2 |
| SDA19crane-NL | Load pattern | CRv | 1.2 |
| SDA19crane-NL | Load pattern | TL | 1.2 |
| SDA19crane-NL | Load pattern | FT | -1.2 |
| SDA19crane-NL | Load pattern | Live | 1 |
| SDA19crane-NL | Load pattern | S | 1 |
| SDA19crane-NL | Load pattern | WLXP | 1 |
| SDA19crane-NL | Load pattern | NotionalX(DL) | 1.2 |
| SDA19crane-NL | Load pattern | NotionalY(DL) | 1.2 |
| SDA19crane-NL | Load pattern | NotionalX(LL) | 1 |
| SDA19crane-NL | Load pattern | NotionalY(LL) | 1 |
| SDA20crane-NL | Load pattern | DEAD | 1.2 |
| SDA20crane-NL | Load pattern | CRv | 1.2 |
| SDA20crane-NL | Load pattern | TL | 1.2 |
| SDA20crane-NL | Load pattern | FT | 1.2 |
| SDA20crane-NL | Load pattern | Live | 1 |
| SDA20crane-NL | Load pattern | S | 1 |
| SDA20crane-NL | Load pattern | WLXP | -1 |
| SDA20crane-NL | Load pattern | NotionalX(DL) | 1.2 |
| SDA20crane-NL | Load pattern | NotionalY(DL) | 1.2 |
| SDA20crane-NL | Load pattern | NotionalX(LL) | 1 |
| SDA20crane-NL | Load pattern | NotionalY(LL) | 1 |
| SDA21crane-NL | Load pattern | DEAD | 1.2 |
| SDA21crane-NL | Load pattern | CRv | 1.2 |
| SDA21crane-NL | Load pattern | TL | 1.2 |
| SDA21crane-NL | Load pattern | FT | -1.2 |
| SDA21crane-NL | Load pattern | Live | 1 |
| SDA21crane-NL | Load pattern | S | 1 |
| SDA21crane-NL | Load pattern | WLXP | -1 |
| SDA21crane-NL | Load pattern | NotionalX(DL) | 1.2 |
| SDA21crane-NL | Load pattern | NotionalY(DL) | 1.2 |
| SDA21crane-NL | Load pattern | NotionalX(LL) | 1 |
| SDA21crane-NL | Load pattern | NotionalY(LL) | 1 |
| SDA22-NL | Load pattern | DEAD | 1.2 |
| SDA22-NL | Load pattern | CRv | 1.2 |
| SDA22-NL | Load pattern | TL | 1.2 |
| SDA22-NL | Load pattern | Live | 1 |
| SDA22-NL | Load pattern | S | 1 |
| SDA22-NL | Load pattern | WLXP | 1 |
| SDA22-NL | Load pattern | NotionalX(DL) | 1.2 |
| SDA22-NL | Load pattern | NotionalY(DL) | 1.2 |
| SDA22-NL | Load pattern | NotionalX(LL) | 1 |
| SDA22-NL | Load pattern | NotionalY(LL) | 1 |
| SDA24-NL | Load pattern | DEAD | 1.2 |
| SDA24-NL | Load pattern | CRv | 1.2 |
| SDA24-NL | Load pattern | TL | 1.2 |
| SDA24-NL | Load pattern | Live | 1 |
| SDA24-NL | Load pattern | S | 1 |
| SDA24-NL | Load pattern | WLXP | -1 |
| SDA24-NL | Load pattern | NotionalX(DL) | 1.2 |
| SDA24-NL | Load pattern | NotionalY(DL) | 1.2 |
| SDA24-NL | Load pattern | NotionalX(LL) | 1 |
| SDA24-NL | Load pattern | NotionalY(LL) | 1 |
| SDA10-1crane-NL | Load pattern | DEAD | 1.2 |
| SDA10-1crane-NL | Load pattern | CRv | 1.2 |
| SDA10-1crane-NL | Load pattern | TL | 1.2 |
| SDA10-1crane-NL | Load pattern | FL | 1.2 |
| SDA10-1crane-NL | Load pattern | Live | 1 |
| SDA10-1crane-NL | Load pattern | S | 1 |
| SDA10-1crane-NL | Load pattern | WLYP | 1 |
| SDA10-1crane-NL | Load pattern | NotionalX(DL) | 1.2 |
| SDA10-1crane-NL | Load pattern | NotionalY(DL) | 1.2 |
| SDA10-1crane-NL | Load pattern | NotionalX(LL) | 1 |
| SDA10-1crane-NL | Load pattern | NotionalY(LL) | 1 |
| SDA11-1crane-NL | Load pattern | DEAD | 1.2 |
| SDA11-1crane-NL | Load pattern | CRv | 1.2 |
| SDA11-1crane-NL | Load pattern | TL | 1.2 |
| SDA11-1crane-NL | Load pattern | FL | -1.2 |
| SDA11-1crane-NL | Load pattern | Live | 1 |
| SDA11-1crane-NL | Load pattern | S | 1 |
| SDA11-1crane-NL | Load pattern | WLYP | 1 |
| SDA11-1crane-NL | Load pattern | NotionalX(DL) | 1.2 |
| SDA11-1crane-NL | Load pattern | NotionalY(DL) | 1.2 |
| SDA11-1crane-NL | Load pattern | NotionalX(LL) | 1 |
| SDA11-1crane-NL | Load pattern | NotionalY(LL) | 1 |
| SDA12-1crane-NL | Load pattern | DEAD | 1.2 |
| SDA12-1crane-NL | Load pattern | CRv | 1.2 |
| SDA12-1crane-NL | Load pattern | TL | 1.2 |
| SDA12-1crane-NL | Load pattern | FL | 1.2 |
| SDA12-1crane-NL | Load pattern | Live | 1 |
| SDA12-1crane-NL | Load pattern | S | 1 |
| SDA12-1crane-NL | Load pattern | WLYP | -1 |
| SDA12-1crane-NL | Load pattern | NotionalX(DL) | 1.2 |
| SDA12-1crane-NL | Load pattern | NotionalY(DL) | 1.2 |
| SDA12-1crane-NL | Load pattern | NotionalX(LL) | 1 |
| SDA12-1crane-NL | Load pattern | NotionalY(LL) | 1 |
| SDA13-1crane-NL | Load pattern | DEAD | 1.2 |
| SDA13-1crane-NL | Load pattern | CRv | 1.2 |
| SDA13-1crane-NL | Load pattern | TL | 1.2 |
| SDA13-1crane-NL | Load pattern | FL | -1.2 |
| SDA13-1crane-NL | Load pattern | Live | 1 |
| SDA13-1crane-NL | Load pattern | S | 1 |
| SDA13-1crane-NL | Load pattern | WLYP | -1 |
| SDA13-1crane-NL | Load pattern | NotionalX(DL) | 1.2 |
| SDA13-1crane-NL | Load pattern | NotionalY(DL) | 1.2 |
| SDA13-1crane-NL | Load pattern | NotionalX(LL) | 1 |
| SDA13-1crane-NL | Load pattern | NotionalY(LL) | 1 |
| SDA14-1-NL | Load pattern | DEAD | 1.2 |
| SDA14-1-NL | Load pattern | CRv | 1.2 |
| SDA14-1-NL | Load pattern | TL | 1.2 |
| SDA14-1-NL | Load pattern | Live | 1 |
| SDA14-1-NL | Load pattern | S | 1 |
| SDA14-1-NL | Load pattern | WLYP | 1 |
| SDA14-1-NL | Load pattern | NotionalX(DL) | 1.2 |
| SDA14-1-NL | Load pattern | NotionalY(DL) | 1.2 |
| SDA14-1-NL | Load pattern | NotionalX(LL) | 1 |
| SDA14-1-NL | Load pattern | NotionalY(LL) | 1 |
| SDA16-1-NL | Load pattern | DEAD | 1.2 |
| SDA16-1-NL | Load pattern | CRv | 1.2 |
| SDA16-1-NL | Load pattern | TL | 1.2 |
| SDA16-1-NL | Load pattern | Live | 1 |
| SDA16-1-NL | Load pattern | S | 1 |
| SDA16-1-NL | Load pattern | WLYP | -1 |
| SDA16-1-NL | Load pattern | NotionalX(DL) | 1.2 |
| SDA16-1-NL | Load pattern | NotionalY(DL) | 1.2 |
| SDA16-1-NL | Load pattern | NotionalX(LL) | 1 |
| SDA16-1-NL | Load pattern | NotionalY(LL) | 1 |
| SDA18-1crane-NL | Load pattern | DEAD | 1.2 |
| SDA18-1crane-NL | Load pattern | CRv | 1.2 |
| SDA18-1crane-NL | Load pattern | TL | 1.2 |
| SDA18-1crane-NL | Load pattern | FT | 1.2 |
| SDA18-1crane-NL | Load pattern | Live | 1 |
| SDA18-1crane-NL | Load pattern | S | 1 |
| SDA18-1crane-NL | Load pattern | WLYP | 1 |
| SDA18-1crane-NL | Load pattern | NotionalX(DL) | 1.2 |
| SDA18-1crane-NL | Load pattern | NotionalY(DL) | 1.2 |
| SDA18-1crane-NL | Load pattern | NotionalX(LL) | 1 |
| SDA18-1crane-NL | Load pattern | NotionalY(LL) | 1 |
| SDA19-1crane-NL | Load pattern | DEAD | 1.2 |
| SDA19-1crane-NL | Load pattern | CRv | 1.2 |
| SDA19-1crane-NL | Load pattern | TL | 1.2 |
| SDA19-1crane-NL | Load pattern | FT | -1.2 |
| SDA19-1crane-NL | Load pattern | Live | 1 |
| SDA19-1crane-NL | Load pattern | S | 1 |
| SDA19-1crane-NL | Load pattern | WLYP | 1 |
| SDA19-1crane-NL | Load pattern | NotionalX(DL) | 1.2 |
| SDA19-1crane-NL | Load pattern | NotionalY(DL) | 1.2 |
| SDA19-1crane-NL | Load pattern | NotionalX(LL) | 1 |
| SDA19-1crane-NL | Load pattern | NotionalY(LL) | 1 |
| SDA20-1crane-NL | Load pattern | DEAD | 1.2 |
| SDA20-1crane-NL | Load pattern | CRv | 1.2 |
| SDA20-1crane-NL | Load pattern | TL | 1.2 |
| SDA20-1crane-NL | Load pattern | FT | 1.2 |
| SDA20-1crane-NL | Load pattern | Live | 1 |
| SDA20-1crane-NL | Load pattern | S | 1 |
| SDA20-1crane-NL | Load pattern | WLYP | -1 |
| SDA20-1crane-NL | Load pattern | NotionalX(DL) | 1.2 |
| SDA20-1crane-NL | Load pattern | NotionalY(DL) | 1.2 |
| SDA20-1crane-NL | Load pattern | NotionalX(LL) | 1 |
| SDA20-1crane-NL | Load pattern | NotionalY(LL) | 1 |
| SDA21-1crane-NL | Load pattern | DEAD | 1.2 |
| SDA21-1crane-NL | Load pattern | CRv | 1.2 |
| SDA21-1crane-NL | Load pattern | TL | 1.2 |
| SDA21-1crane-NL | Load pattern | FT | -1.2 |
| SDA21-1crane-NL | Load pattern | Live | 1 |
| SDA21-1crane-NL | Load pattern | S | 1 |
| SDA21-1crane-NL | Load pattern | WLYP | -1 |
| SDA21-1crane-NL | Load pattern | NotionalX(DL) | 1.2 |
| SDA21-1crane-NL | Load pattern | NotionalY(DL) | 1.2 |
| SDA21-1crane-NL | Load pattern | NotionalX(LL) | 1 |
| SDA21-1crane-NL | Load pattern | NotionalY(LL) | 1 |
| SDA22-1-NL | Load pattern | DEAD | 1.2 |
| SDA22-1-NL | Load pattern | CRv | 1.2 |
| SDA22-1-NL | Load pattern | TL | 1.2 |
| SDA22-1-NL | Load pattern | Live | 1 |
| SDA22-1-NL | Load pattern | S | 1 |
| SDA22-1-NL | Load pattern | WLYP | 1 |
| SDA22-1-NL | Load pattern | NotionalX(DL) | 1.2 |
| SDA22-1-NL | Load pattern | NotionalY(DL) | 1.2 |
| SDA22-1-NL | Load pattern | NotionalX(LL) | 1 |
| SDA22-1-NL | Load pattern | NotionalY(LL) | 1 |
| SDA24-1-NL | Load pattern | DEAD | 1.2 |
| SDA24-1-NL | Load pattern | CRv | 1.2 |
| SDA24-1-NL | Load pattern | TL | 1.2 |
| SDA24-1-NL | Load pattern | Live | 1 |
| SDA24-1-NL | Load pattern | S | 1 |
| SDA24-1-NL | Load pattern | WLYP | -1 |
| SDA24-1-NL | Load pattern | NotionalX(DL) | 1.2 |
| SDA24-1-NL | Load pattern | NotionalY(DL) | 1.2 |
| SDA24-1-NL | Load pattern | NotionalX(LL) | 1 |
| SDA24-1-NL | Load pattern | NotionalY(LL) | 1 |
| SDA26crane-NL | Load pattern | DEAD | 1.2 |
| SDA26crane-NL | Load pattern | CRv | 1.2 |
| SDA26crane-NL | Load pattern | TL | 1.2 |
| SDA26crane-NL | Load pattern | FL | 1.2 |
| SDA26crane-NL | Load pattern | WLXP | 0.5 |
| SDA26crane-NL | Load pattern | NotionalX(DL) | 1.2 |
| SDA26crane-NL | Load pattern | NotionalY(DL) | 1.2 |
| SDA27crane-NL | Load pattern | DEAD | 1.2 |
| SDA27crane-NL | Load pattern | CRv | 1.2 |
| SDA27crane-NL | Load pattern | TL | 1.2 |
| SDA27crane-NL | Load pattern | FL | -1.2 |
| SDA27crane-NL | Load pattern | WLXP | 0.5 |
| SDA27crane-NL | Load pattern | NotionalX(DL) | 1.2 |
| SDA27crane-NL | Load pattern | NotionalY(DL) | 1.2 |
| SDA28crane-NL | Load pattern | DEAD | 1.2 |
| SDA28crane-NL | Load pattern | CRv | 1.2 |
| SDA28crane-NL | Load pattern | TL | 1.2 |
| SDA28crane-NL | Load pattern | FL | 1.2 |
| SDA28crane-NL | Load pattern | WLXP | -0.5 |
| SDA28crane-NL | Load pattern | NotionalX(DL) | 1.2 |
| SDA28crane-NL | Load pattern | NotionalY(DL) | 1.2 |
| SDA29crane-NL | Load pattern | DEAD | 1.2 |
| SDA29crane-NL | Load pattern | CRv | 1.2 |
| SDA29crane-NL | Load pattern | TL | 1.2 |
| SDA29crane-NL | Load pattern | FL | -1.2 |
| SDA29crane-NL | Load pattern | WLXP | -0.5 |
| SDA29crane-NL | Load pattern | NotionalX(DL) | 1.2 |
| SDA29crane-NL | Load pattern | NotionalY(DL) | 1.2 |
| SDA30-NL | Load pattern | DEAD | 1.2 |
| SDA30-NL | Load pattern | CRv | 1.2 |
| SDA30-NL | Load pattern | TL | 1.2 |
| SDA30-NL | Load pattern | WLXP | 0.5 |
| SDA30-NL | Load pattern | NotionalX(DL) | 1.2 |
| SDA30-NL | Load pattern | NotionalY(DL) | 1.2 |
| SDA32-NL | Load pattern | DEAD | 1.2 |
| SDA32-NL | Load pattern | CRv | 1.2 |
| SDA32-NL | Load pattern | TL | 1.2 |
| SDA32-NL | Load pattern | WLXP | -0.5 |
| SDA32-NL | Load pattern | NotionalX(DL) | 1.2 |
| SDA32-NL | Load pattern | NotionalY(DL) | 1.2 |
| SDA34crane-NL | Load pattern | DEAD | 1.2 |
| SDA34crane-NL | Load pattern | CRv | 1.2 |
| SDA34crane-NL | Load pattern | TL | 1.2 |
| SDA34crane-NL | Load pattern | FT | 1.2 |
| SDA34crane-NL | Load pattern | WLXP | 0.5 |
| SDA34crane-NL | Load pattern | NotionalX(DL) | 1.2 |
| SDA34crane-NL | Load pattern | NotionalY(DL) | 1.2 |
| SDA35crane-NL | Load pattern | DEAD | 1.2 |
| SDA35crane-NL | Load pattern | CRv | 1.2 |
| SDA35crane-NL | Load pattern | TL | 1.2 |
| SDA35crane-NL | Load pattern | FT | -1.2 |
| SDA35crane-NL | Load pattern | WLXP | 0.5 |
| SDA35crane-NL | Load pattern | NotionalX(DL) | 1.2 |
| SDA35crane-NL | Load pattern | NotionalY(DL) | 1.2 |
| SDA36crane-NL | Load pattern | DEAD | 1.2 |
| SDA36crane-NL | Load pattern | CRv | 1.2 |
| SDA36crane-NL | Load pattern | TL | 1.2 |
| SDA36crane-NL | Load pattern | FT | 1.2 |
| SDA36crane-NL | Load pattern | WLXP | -0.5 |
| SDA36crane-NL | Load pattern | NotionalX(DL) | 1.2 |
| SDA36crane-NL | Load pattern | NotionalY(DL) | 1.2 |
| SDA37crane-NL | Load pattern | DEAD | 1.2 |
| SDA37crane-NL | Load pattern | CRv | 1.2 |
| SDA37crane-NL | Load pattern | TL | 1.2 |
| SDA37crane-NL | Load pattern | FT | -1.2 |
| SDA37crane-NL | Load pattern | WLXP | -0.5 |
| SDA37crane-NL | Load pattern | NotionalX(DL) | 1.2 |
| SDA37crane-NL | Load pattern | NotionalY(DL) | 1.2 |
| SDA38-NL | Load pattern | DEAD | 1.2 |
| SDA38-NL | Load pattern | CRv | 1.2 |
| SDA38-NL | Load pattern | TL | 1.2 |
| SDA38-NL | Load pattern | WLXP | 0.5 |
| SDA38-NL | Load pattern | NotionalX(DL) | 1.2 |
| SDA38-NL | Load pattern | NotionalY(DL) | 1.2 |
| SDA40-NL | Load pattern | DEAD | 1.2 |
| SDA40-NL | Load pattern | CRv | 1.2 |
| SDA40-NL | Load pattern | TL | 1.2 |
| SDA40-NL | Load pattern | WLXP | -0.5 |
| SDA40-NL | Load pattern | NotionalX(DL) | 1.2 |
| SDA40-NL | Load pattern | NotionalY(DL) | 1.2 |
| SDA26-1crane-NL | Load pattern | DEAD | 1.2 |
| SDA26-1crane-NL | Load pattern | CRv | 1.2 |
| SDA26-1crane-NL | Load pattern | TL | 1.2 |
| SDA26-1crane-NL | Load pattern | FL | 1.2 |
| SDA26-1crane-NL | Load pattern | WLYP | 0.5 |
| SDA26-1crane-NL | Load pattern | NotionalX(DL) | 1.2 |
| SDA26-1crane-NL | Load pattern | NotionalY(DL) | 1.2 |
| SDA27-1crane-NL | Load pattern | DEAD | 1.2 |
| SDA27-1crane-NL | Load pattern | CRv | 1.2 |
| SDA27-1crane-NL | Load pattern | TL | 1.2 |
| SDA27-1crane-NL | Load pattern | FL | -1.2 |
| SDA27-1crane-NL | Load pattern | WLYP | 0.5 |
| SDA27-1crane-NL | Load pattern | NotionalX(DL) | 1.2 |
| SDA27-1crane-NL | Load pattern | NotionalY(DL) | 1.2 |
| SDA28-1crane-NL | Load pattern | DEAD | 1.2 |
| SDA28-1crane-NL | Load pattern | CRv | 1.2 |
| SDA28-1crane-NL | Load pattern | TL | 1.2 |
| SDA28-1crane-NL | Load pattern | FL | 1.2 |
| SDA28-1crane-NL | Load pattern | WLYP | -0.5 |
| SDA28-1crane-NL | Load pattern | NotionalX(DL) | 1.2 |
| SDA28-1crane-NL | Load pattern | NotionalY(DL) | 1.2 |
| SDA29-1crane-NL | Load pattern | DEAD | 1.2 |
| SDA29-1crane-NL | Load pattern | CRv | 1.2 |
| SDA29-1crane-NL | Load pattern | TL | 1.2 |
| SDA29-1crane-NL | Load pattern | FL | -1.2 |
| SDA29-1crane-NL | Load pattern | WLYP | -0.5 |
| SDA29-1crane-NL | Load pattern | NotionalX(DL) | 1.2 |
| SDA29-1crane-NL | Load pattern | NotionalY(DL) | 1.2 |
| SDA30-1-NL | Load pattern | DEAD | 1.2 |
| SDA30-1-NL | Load pattern | CRv | 1.2 |
| SDA30-1-NL | Load pattern | TL | 1.2 |
| SDA30-1-NL | Load pattern | WLYP | 0.5 |
| SDA30-1-NL | Load pattern | NotionalX(DL) | 1.2 |
| SDA30-1-NL | Load pattern | NotionalY(DL) | 1.2 |
| SDA32-1-NL | Load pattern | DEAD | 1.2 |
| SDA32-1-NL | Load pattern | CRv | 1.2 |
| SDA32-1-NL | Load pattern | TL | 1.2 |
| SDA32-1-NL | Load pattern | WLYP | -0.5 |
| SDA32-1-NL | Load pattern | NotionalX(DL) | 1.2 |
| SDA32-1-NL | Load pattern | NotionalY(DL) | 1.2 |
| SDA34-1crane-NL | Load pattern | DEAD | 1.2 |
| SDA34-1crane-NL | Load pattern | CRv | 1.2 |
| SDA34-1crane-NL | Load pattern | TL | 1.2 |
| SDA34-1crane-NL | Load pattern | FT | 1.2 |
| SDA34-1crane-NL | Load pattern | WLYP | 0.5 |
| SDA34-1crane-NL | Load pattern | NotionalX(DL) | 1.2 |
| SDA34-1crane-NL | Load pattern | NotionalY(DL) | 1.2 |
| SDA35-1crane-NL | Load pattern | DEAD | 1.2 |
| SDA35-1crane-NL | Load pattern | CRv | 1.2 |
| SDA35-1crane-NL | Load pattern | TL | 1.2 |
| SDA35-1crane-NL | Load pattern | FT | -1.2 |
| SDA35-1crane-NL | Load pattern | WLYP | 0.5 |
| SDA35-1crane-NL | Load pattern | NotionalX(DL) | 1.2 |
| SDA35-1crane-NL | Load pattern | NotionalY(DL) | 1.2 |
| SDA36-1crane-NL | Load pattern | DEAD | 1.2 |
| SDA36-1crane-NL | Load pattern | CRv | 1.2 |
| SDA36-1crane-NL | Load pattern | TL | 1.2 |
| SDA36-1crane-NL | Load pattern | FT | 1.2 |
| SDA36-1crane-NL | Load pattern | WLYP | -0.5 |
| SDA36-1crane-NL | Load pattern | NotionalX(DL) | 1.2 |
| SDA36-1crane-NL | Load pattern | NotionalY(DL) | 1.2 |
| SDA37-1crane-NL | Load pattern | DEAD | 1.2 |
| SDA37-1crane-NL | Load pattern | CRv | 1.2 |
| SDA37-1crane-NL | Load pattern | TL | 1.2 |
| SDA37-1crane-NL | Load pattern | FT | -1.2 |
| SDA37-1crane-NL | Load pattern | WLYP | -0.5 |
| SDA37-1crane-NL | Load pattern | NotionalX(DL) | 1.2 |
| SDA37-1crane-NL | Load pattern | NotionalY(DL) | 1.2 |
| SDA38-1-NL | Load pattern | DEAD | 1.2 |
| SDA38-1-NL | Load pattern | CRv | 1.2 |
| SDA38-1-NL | Load pattern | TL | 1.2 |
| SDA38-1-NL | Load pattern | WLYP | 0.5 |
| SDA38-1-NL | Load pattern | NotionalX(DL) | 1.2 |
| SDA38-1-NL | Load pattern | NotionalY(DL) | 1.2 |
| SDA40-1-NL | Load pattern | DEAD | 1.2 |
| SDA40-1-NL | Load pattern | CRv | 1.2 |
| SDA40-1-NL | Load pattern | TL | 1.2 |
| SDA40-1-NL | Load pattern | WLYP | -0.5 |
| SDA40-1-NL | Load pattern | NotionalX(DL) | 1.2 |
| SDA40-1-NL | Load pattern | NotionalY(DL) | 1.2 |
| SDA42crane-NL | Load pattern | DEAD | 0.9 |
| SDA42crane-NL | Load pattern | CRv | 0.9 |
| SDA42crane-NL | Load pattern | TL | 1.2 |
| SDA42crane-NL | Load pattern | FL | 1.2 |
| SDA42crane-NL | Load pattern | WLXP | 1 |
| SDA42crane-NL | Load pattern | NotionalX(DL) | 0.9 |
| SDA42crane-NL | Load pattern | NotionalY(DL) | 0.9 |
| SDA43crane-NL | Load pattern | DEAD | 0.9 |
| SDA43crane-NL | Load pattern | CRv | 0.9 |
| SDA43crane-NL | Load pattern | TL | 1.2 |
| SDA43crane-NL | Load pattern | FL | -1.2 |
| SDA43crane-NL | Load pattern | WLXP | 1 |
| SDA43crane-NL | Load pattern | NotionalX(DL) | 0.9 |
| SDA43crane-NL | Load pattern | NotionalY(DL) | 0.9 |
| SDA44crane-NL | Load pattern | DEAD | 0.9 |
| SDA44crane-NL | Load pattern | CRv | 0.9 |
| SDA44crane-NL | Load pattern | TL | 1.2 |
| SDA44crane-NL | Load pattern | FL | -1.2 |
| SDA44crane-NL | Load pattern | WLXP | -1 |
| SDA44crane-NL | Load pattern | NotionalX(DL) | 0.9 |
| SDA44crane-NL | Load pattern | NotionalY(DL) | 0.9 |
| SDA45crane-NL | Load pattern | DEAD | 0.9 |
| SDA45crane-NL | Load pattern | CRv | 0.9 |
| SDA45crane-NL | Load pattern | TL | 1.2 |
| SDA45crane-NL | Load pattern | FL | 1.2 |
| SDA45crane-NL | Load pattern | WLXP | -1 |
| SDA45crane-NL | Load pattern | NotionalX(DL) | 0.9 |
| SDA45crane-NL | Load pattern | NotionalY(DL) | 0.9 |
| SDA46-NL | Load pattern | DEAD | 0.9 |
| SDA46-NL | Load pattern | CRv | 0.9 |
| SDA46-NL | Load pattern | TL | 1.2 |
| SDA46-NL | Load pattern | WLXP | 1 |
| SDA46-NL | Load pattern | NotionalX(DL) | 0.9 |
| SDA46-NL | Load pattern | NotionalY(DL) | 0.9 |
| SDA48-NL | Load pattern | DEAD | 0.9 |
| SDA48-NL | Load pattern | CRv | 0.9 |
| SDA48-NL | Load pattern | TL | 1.2 |
| SDA48-NL | Load pattern | WLXP | -1 |
| SDA48-NL | Load pattern | NotionalX(DL) | 0.9 |
| SDA48-NL | Load pattern | NotionalY(DL) | 0.9 |
| SDA50crane-NL | Load pattern | DEAD | 0.9 |
| SDA50crane-NL | Load pattern | CRv | 0.9 |
| SDA50crane-NL | Load pattern | TL | 1.2 |
| SDA50crane-NL | Load pattern | FT | 1.2 |
| SDA50crane-NL | Load pattern | WLXP | 1 |
| SDA50crane-NL | Load pattern | NotionalX(DL) | 0.9 |
| SDA50crane-NL | Load pattern | NotionalY(DL) | 0.9 |
| SDA51crane-NL | Load pattern | DEAD | 0.9 |
| SDA51crane-NL | Load pattern | CRv | 0.9 |
| SDA51crane-NL | Load pattern | TL | 1.2 |
| SDA51crane-NL | Load pattern | FT | -1.2 |
| SDA51crane-NL | Load pattern | WLXP | 1 |
| SDA51crane-NL | Load pattern | NotionalX(DL) | 0.9 |
| SDA51crane-NL | Load pattern | NotionalY(DL) | 0.9 |
| SDA52crane-NL | Load pattern | DEAD | 0.9 |
| SDA52crane-NL | Load pattern | CRv | 0.9 |
| SDA52crane-NL | Load pattern | TL | 1.2 |
| SDA52crane-NL | Load pattern | FT | -1.2 |
| SDA52crane-NL | Load pattern | WLXP | -1 |
| SDA52crane-NL | Load pattern | NotionalX(DL) | 0.9 |
| SDA52crane-NL | Load pattern | NotionalY(DL) | 0.9 |
| SDA53crane-NL | Load pattern | DEAD | 0.9 |
| SDA53crane-NL | Load pattern | CRv | 0.9 |
| SDA53crane-NL | Load pattern | TL | 1.2 |
| SDA53crane-NL | Load pattern | FT | 1.2 |
| SDA53crane-NL | Load pattern | WLXP | -1 |
| SDA53crane-NL | Load pattern | NotionalX(DL) | 0.9 |
| SDA53crane-NL | Load pattern | NotionalY(DL) | 0.9 |
| SDA54-NL | Load pattern | DEAD | 0.9 |
| SDA54-NL | Load pattern | CRv | 0.9 |
| SDA54-NL | Load pattern | TL | 1.2 |
| SDA54-NL | Load pattern | WLXP | 1 |
| SDA54-NL | Load pattern | NotionalX(DL) | 0.9 |
| SDA54-NL | Load pattern | NotionalY(DL) | 0.9 |
| SDA56-NL | Load pattern | DEAD | 0.9 |
| SDA56-NL | Load pattern | CRv | 0.9 |
| SDA56-NL | Load pattern | TL | 1.2 |
| SDA56-NL | Load pattern | WLXP | -1 |
| SDA56-NL | Load pattern | NotionalX(DL) | 0.9 |
| SDA56-NL | Load pattern | NotionalY(DL) | 0.9 |
| SDA42-1crane-NL | Load pattern | DEAD | 0.9 |
| SDA42-1crane-NL | Load pattern | CRv | 0.9 |
| SDA42-1crane-NL | Load pattern | TL | 1.2 |
| SDA42-1crane-NL | Load pattern | FL | 1.2 |
| SDA42-1crane-NL | Load pattern | WLYP | 1 |
| SDA42-1crane-NL | Load pattern | NotionalX(DL) | 0.9 |
| SDA42-1crane-NL | Load pattern | NotionalY(DL) | 0.9 |
| SDA43-1crane-NL | Load pattern | DEAD | 0.9 |
| SDA43-1crane-NL | Load pattern | CRv | 0.9 |
| SDA43-1crane-NL | Load pattern | TL | 1.2 |
| SDA43-1crane-NL | Load pattern | FL | -1.2 |
| SDA43-1crane-NL | Load pattern | WLYP | 1 |
| SDA43-1crane-NL | Load pattern | NotionalX(DL) | 0.9 |
| SDA43-1crane-NL | Load pattern | NotionalY(DL) | 0.9 |
| SDA44-1crane-NL | Load pattern | DEAD | 0.9 |
| SDA44-1crane-NL | Load pattern | CRv | 0.9 |
| SDA44-1crane-NL | Load pattern | TL | 1.2 |
| SDA44-1crane-NL | Load pattern | FL | -1.2 |
| SDA44-1crane-NL | Load pattern | WLYP | -1 |
| SDA44-1crane-NL | Load pattern | NotionalX(DL) | 0.9 |
| SDA44-1crane-NL | Load pattern | NotionalY(DL) | 0.9 |
| SDA45-1crane-NL | Load pattern | DEAD | 0.9 |
| SDA45-1crane-NL | Load pattern | CRv | 0.9 |
| SDA45-1crane-NL | Load pattern | TL | 1.2 |
| SDA45-1crane-NL | Load pattern | FL | 1.2 |
| SDA45-1crane-NL | Load pattern | WLYP | -1 |
| SDA45-1crane-NL | Load pattern | NotionalX(DL) | 0.9 |
| SDA45-1crane-NL | Load pattern | NotionalY(DL) | 0.9 |
| SDA46-1-NL | Load pattern | DEAD | 0.9 |
| SDA46-1-NL | Load pattern | CRv | 0.9 |
| SDA46-1-NL | Load pattern | TL | 1.2 |
| SDA46-1-NL | Load pattern | WLYP | 1 |
| SDA46-1-NL | Load pattern | NotionalX(DL) | 0.9 |
| SDA46-1-NL | Load pattern | NotionalY(DL) | 0.9 |
| SDA48-1-NL | Load pattern | DEAD | 0.9 |
| SDA48-1-NL | Load pattern | CRv | 0.9 |
| SDA48-1-NL | Load pattern | TL | 1.2 |
| SDA48-1-NL | Load pattern | WLYP | -1 |
| SDA48-1-NL | Load pattern | NotionalX(DL) | 0.9 |
| SDA48-1-NL | Load pattern | NotionalY(DL) | 0.9 |
| SDA50-1crane-NL | Load pattern | DEAD | 0.9 |
| SDA50-1crane-NL | Load pattern | CRv | 0.9 |
| SDA50-1crane-NL | Load pattern | TL | 1.2 |
| SDA50-1crane-NL | Load pattern | FT | 1.2 |
| SDA50-1crane-NL | Load pattern | WLYP | 1 |
| SDA50-1crane-NL | Load pattern | NotionalX(DL) | 0.9 |
| SDA50-1crane-NL | Load pattern | NotionalY(DL) | 0.9 |
| SDA51-1crane-NL | Load pattern | DEAD | 0.9 |
| SDA51-1crane-NL | Load pattern | CRv | 0.9 |
| SDA51-1crane-NL | Load pattern | TL | 1.2 |
| SDA51-1crane-NL | Load pattern | FT | -1.2 |
| SDA51-1crane-NL | Load pattern | WLYP | 1 |
| SDA51-1crane-NL | Load pattern | NotionalX(DL) | 0.9 |
| SDA51-1crane-NL | Load pattern | NotionalY(DL) | 0.9 |
| SDA52-1crane-NL | Load pattern | DEAD | 0.9 |
| SDA52-1crane-NL | Load pattern | CRv | 0.9 |
| SDA52-1crane-NL | Load pattern | TL | 1.2 |
| SDA52-1crane-NL | Load pattern | FT | -1.2 |
| SDA52-1crane-NL | Load pattern | WLYP | -1 |
| SDA52-1crane-NL | Load pattern | NotionalX(DL) | 0.9 |
| SDA52-1crane-NL | Load pattern | NotionalY(DL) | 0.9 |
| SDA53-1crane-NL | Load pattern | DEAD | 0.9 |
| SDA53-1crane-NL | Load pattern | CRv | 0.9 |
| SDA53-1crane-NL | Load pattern | TL | 1.2 |
| SDA53-1crane-NL | Load pattern | FT | 1.2 |
| SDA53-1crane-NL | Load pattern | WLYP | -1 |
| SDA53-1crane-NL | Load pattern | NotionalX(DL) | 0.9 |
| SDA53-1crane-NL | Load pattern | NotionalY(DL) | 0.9 |
| SDA54-1-NL | Load pattern | DEAD | 0.9 |
| SDA54-1-NL | Load pattern | CRv | 0.9 |
| SDA54-1-NL | Load pattern | TL | 1.2 |
| SDA54-1-NL | Load pattern | WLYP | 1 |
| SDA54-1-NL | Load pattern | NotionalX(DL) | 0.9 |
| SDA54-1-NL | Load pattern | NotionalY(DL) | 0.9 |
| SDA56-1-NL | Load pattern | DEAD | 0.9 |
| SDA56-1-NL | Load pattern | CRv | 0.9 |
| SDA56-1-NL | Load pattern | TL | 1.2 |
| SDA56-1-NL | Load pattern | WLYP | -1 |
| SDA56-1-NL | Load pattern | NotionalX(DL) | 0.9 |
| SDA56-1-NL | Load pattern | NotionalY(DL) | 0.9 |
| SDD58-NL | Load pattern | DEAD | 1.2 |
| SDD58-NL | Load pattern | CRv | 1.2 |
| SDD58-NL | Load pattern | TL | 1.2 |
| SDD58-NL | Load pattern | Live | 1 |
| SDD58-NL | Load pattern | S | 1 |
| SDD58-NL | Load pattern | EQX | 1 |
| SDD58-NL | Load pattern | EQY | 0.3 |
| SDD58-NL | Load pattern | DEAD | 0.215 |
| SDD58-NL | Load pattern | NotionalX(DL) | 1.2 |
| SDD58-NL | Load pattern | NotionalY(DL) | 1.2 |
| SDD58-NL | Load pattern | NotionalX(LL) | 1 |
| SDD58-NL | Load pattern | NotionalY(LL) | 1 |
| SDD59-NL | Load pattern | DEAD | 1.2 |
| SDD59-NL | Load pattern | CRv | 1.2 |
| SDD59-NL | Load pattern | TL | 1.2 |
| SDD59-NL | Load pattern | Live | 1 |
| SDD59-NL | Load pattern | S | 1 |
| SDD59-NL | Load pattern | EQX | -1 |
| SDD59-NL | Load pattern | EQY | 0.3 |
| SDD59-NL | Load pattern | DEAD | 0.215 |
| SDD59-NL | Load pattern | NotionalX(DL) | 1.2 |
| SDD59-NL | Load pattern | NotionalY(DL) | 1.2 |
| SDD59-NL | Load pattern | NotionalX(LL) | 1 |
| SDD59-NL | Load pattern | NotionalY(LL) | 1 |
| SDD60-NL | Load pattern | DEAD | 1.2 |
| SDD60-NL | Load pattern | CRv | 1.2 |
| SDD60-NL | Load pattern | TL | 1.2 |
| SDD60-NL | Load pattern | Live | 1 |
| SDD60-NL | Load pattern | S | 1 |
| SDD60-NL | Load pattern | EQX | 1 |
| SDD60-NL | Load pattern | EQY | -0.3 |
| SDD60-NL | Load pattern | DEAD | 0.215 |
| SDD60-NL | Load pattern | NotionalX(DL) | 1.2 |
| SDD60-NL | Load pattern | NotionalY(DL) | 1.2 |
| SDD60-NL | Load pattern | NotionalX(LL) | 1 |
| SDD60-NL | Load pattern | NotionalY(LL) | 1 |
| SDD61-NL | Load pattern | DEAD | 1.2 |
| SDD61-NL | Load pattern | CRv | 1.2 |
| SDD61-NL | Load pattern | TL | 1.2 |
| SDD61-NL | Load pattern | Live | 1 |
| SDD61-NL | Load pattern | S | 1 |
| SDD61-NL | Load pattern | EQX | -1 |
| SDD61-NL | Load pattern | EQY | -0.3 |
| SDD61-NL | Load pattern | DEAD | 0.215 |
| SDD61-NL | Load pattern | NotionalX(DL) | 1.2 |
| SDD61-NL | Load pattern | NotionalY(DL) | 1.2 |
| SDD61-NL | Load pattern | NotionalX(LL) | 1 |
| SDD61-NL | Load pattern | NotionalY(LL) | 1 |
| SDD62-NL | Load pattern | DEAD | 1.2 |
| SDD62-NL | Load pattern | CRv | 1.2 |
| SDD62-NL | Load pattern | TL | 1.2 |
| SDD62-NL | Load pattern | Live | 1 |
| SDD62-NL | Load pattern | S | 1 |
| SDD62-NL | Load pattern | EQY | 1 |
| SDD62-NL | Load pattern | EQX | 0.3 |
| SDD62-NL | Load pattern | DEAD | 0.215 |
| SDD62-NL | Load pattern | NotionalX(DL) | 1.2 |
| SDD62-NL | Load pattern | NotionalY(DL) | 1.2 |
| SDD62-NL | Load pattern | NotionalX(LL) | 1 |
| SDD62-NL | Load pattern | NotionalY(LL) | 1 |
| SDD63-NL | Load pattern | DEAD | 1.2 |
| SDD63-NL | Load pattern | CRv | 1.2 |
| SDD63-NL | Load pattern | TL | 1.2 |
| SDD63-NL | Load pattern | Live | 1 |
| SDD63-NL | Load pattern | S | 1 |
| SDD63-NL | Load pattern | EQY | -1 |
| SDD63-NL | Load pattern | EQX | 0.3 |
| SDD63-NL | Load pattern | DEAD | 0.215 |
| SDD63-NL | Load pattern | NotionalX(DL) | 1.2 |
| SDD63-NL | Load pattern | NotionalY(DL) | 1.2 |
| SDD63-NL | Load pattern | NotionalX(LL) | 1 |
| SDD63-NL | Load pattern | NotionalY(LL) | 1 |
| SDD64-NL | Load pattern | DEAD | 1.2 |
| SDD64-NL | Load pattern | CRv | 1.2 |
| SDD64-NL | Load pattern | TL | 1.2 |
| SDD64-NL | Load pattern | Live | 1 |
| SDD64-NL | Load pattern | S | 1 |
| SDD64-NL | Load pattern | EQY | 1 |
| SDD64-NL | Load pattern | EQX | -0.3 |
| SDD64-NL | Load pattern | DEAD | 0.215 |
| SDD64-NL | Load pattern | NotionalX(DL) | 1.2 |
| SDD64-NL | Load pattern | NotionalY(DL) | 1.2 |
| SDD64-NL | Load pattern | NotionalX(LL) | 1 |
| SDD64-NL | Load pattern | NotionalY(LL) | 1 |
| SDD65-NL | Load pattern | DEAD | 1.2 |
| SDD65-NL | Load pattern | CRv | 1.2 |
| SDD65-NL | Load pattern | TL | 1.2 |
| SDD65-NL | Load pattern | Live | 1 |
| SDD65-NL | Load pattern | S | 1 |
| SDD65-NL | Load pattern | EQY | -1 |
| SDD65-NL | Load pattern | EQX | -0.3 |
| SDD65-NL | Load pattern | DEAD | 0.215 |
| SDD65-NL | Load pattern | NotionalX(DL) | 1.2 |
| SDD65-NL | Load pattern | NotionalY(DL) | 1.2 |
| SDD65-NL | Load pattern | NotionalX(LL) | 1 |
| SDD65-NL | Load pattern | NotionalY(LL) | 1 |
| SDD66-NL | Load pattern | DEAD | 0.9 |
| SDD66-NL | Load pattern | CRv | 0.9 |
| SDD66-NL | Load pattern | TL | 1 |
| SDD66-NL | Load pattern | EQX | 1 |
| SDD66-NL | Load pattern | EQY | 0.3 |
| SDD66-NL | Load pattern | DEAD | 0.215 |
| SDD66-NL | Load pattern | NotionalX(DL) | 0.9 |
| SDD66-NL | Load pattern | NotionalY(DL) | 0.9 |
| SDD67-NL | Load pattern | DEAD | 0.9 |
| SDD67-NL | Load pattern | CRv | 0.9 |
| SDD67-NL | Load pattern | TL | 1 |
| SDD67-NL | Load pattern | EQX | -1 |
| SDD67-NL | Load pattern | EQY | 0.3 |
| SDD67-NL | Load pattern | DEAD | 0.215 |
| SDD67-NL | Load pattern | NotionalX(DL) | 0.9 |
| SDD67-NL | Load pattern | NotionalY(DL) | 0.9 |
| SDD68-NL | Load pattern | DEAD | 0.9 |
| SDD68-NL | Load pattern | CRv | 0.9 |
| SDD68-NL | Load pattern | TL | 1 |
| SDD68-NL | Load pattern | EQX | 1 |
| SDD68-NL | Load pattern | EQY | -0.3 |
| SDD68-NL | Load pattern | DEAD | 0.215 |
| SDD68-NL | Load pattern | NotionalX(DL) | 0.9 |
| SDD68-NL | Load pattern | NotionalY(DL) | 0.9 |
| SDD69-NL | Load pattern | DEAD | 0.9 |
| SDD69-NL | Load pattern | CRv | 0.9 |
| SDD69-NL | Load pattern | TL | 1 |
| SDD69-NL | Load pattern | EQX | -1 |
| SDD69-NL | Load pattern | EQY | -0.3 |
| SDD69-NL | Load pattern | DEAD | 0.215 |
| SDD69-NL | Load pattern | NotionalX(DL) | 0.9 |
| SDD69-NL | Load pattern | NotionalY(DL) | 0.9 |
| SDD70-NL | Load pattern | DEAD | 0.9 |
| SDD70-NL | Load pattern | CRv | 0.9 |
| SDD70-NL | Load pattern | TL | 1 |
| SDD70-NL | Load pattern | EQY | 1 |
| SDD70-NL | Load pattern | EQX | 0.3 |
| SDD70-NL | Load pattern | DEAD | 0.215 |
| SDD70-NL | Load pattern | NotionalX(DL) | 0.9 |
| SDD70-NL | Load pattern | NotionalY(DL) | 0.9 |
| SDD71-NL | Load pattern | DEAD | 0.9 |
| SDD71-NL | Load pattern | CRv | 0.9 |
| SDD71-NL | Load pattern | TL | 1 |
| SDD71-NL | Load pattern | EQY | -1 |
| SDD71-NL | Load pattern | EQX | 0.3 |
| SDD71-NL | Load pattern | DEAD | 0.215 |
| SDD71-NL | Load pattern | NotionalX(DL) | 0.9 |
| SDD71-NL | Load pattern | NotionalY(DL) | 0.9 |
| SDD72-NL | Load pattern | DEAD | 0.9 |
| SDD72-NL | Load pattern | CRv | 0.9 |
| SDD72-NL | Load pattern | TL | 1 |
| SDD72-NL | Load pattern | EQY | 1 |
| SDD72-NL | Load pattern | EQX | -0.3 |
| SDD72-NL | Load pattern | DEAD | 0.215 |
| SDD72-NL | Load pattern | NotionalX(DL) | 0.9 |
| SDD72-NL | Load pattern | NotionalY(DL) | 0.9 |
| SDD73-NL | Load pattern | DEAD | 0.9 |
| SDD73-NL | Load pattern | CRv | 0.9 |
| SDD73-NL | Load pattern | TL | 1 |
| SDD73-NL | Load pattern | EQY | -1 |
| SDD73-NL | Load pattern | EQX | -0.3 |
| SDD73-NL | Load pattern | DEAD | 0.215 |
| SDD73-NL | Load pattern | NotionalX(DL) | 0.9 |
| SDD73-NL | Load pattern | NotionalY(DL) | 0.9 |
| ASDA74-NL | Load pattern | DEAD | 1 |
| ASDA74-NL | Load pattern | CRv | 1 |
| ASDA74-NL | Load pattern | NotionalX(DL) | 1 |
| ASDA74-NL | Load pattern | NotionalY(DL) | 1 |
| ASDA75crane-NL | Load pattern | DEAD | 1 |
| ASDA75crane-NL | Load pattern | CRv | 1 |
| ASDA75crane-NL | Load pattern | Live | 1 |
| ASDA75crane-NL | Load pattern | S | 1 |
| ASDA75crane-NL | Load pattern | TL | 1 |
| ASDA75crane-NL | Load pattern | FL | 1 |
| ASDA75crane-NL | Load pattern | NotionalX(DL) | 1 |
| ASDA75crane-NL | Load pattern | NotionalY(DL) | 1 |
| ASDA75crane-NL | Load pattern | NotionalX(LL) | 1 |
| ASDA75crane-NL | Load pattern | NotionalY(LL) | 1 |
| ASDA76crane-NL | Load pattern | DEAD | 1 |
| ASDA76crane-NL | Load pattern | CRv | 1 |
| ASDA76crane-NL | Load pattern | Live | 1 |
| ASDA76crane-NL | Load pattern | S | 1 |
| ASDA76crane-NL | Load pattern | TL | 1 |
| ASDA76crane-NL | Load pattern | FL | -1 |
| ASDA76crane-NL | Load pattern | NotionalX(DL) | 1 |
| ASDA76crane-NL | Load pattern | NotionalY(DL) | 1 |
| ASDA76crane-NL | Load pattern | NotionalX(LL) | 1 |
| ASDA76crane-NL | Load pattern | NotionalY(LL) | 1 |
| ASDA78-NL | Load pattern | DEAD | 1 |
| ASDA78-NL | Load pattern | CRv | 1 |
| ASDA78-NL | Load pattern | Live | 1 |
| ASDA78-NL | Load pattern | S | 1 |
| ASDA78-NL | Load pattern | TL | 1 |
| ASDA78-NL | Load pattern | NotionalX(DL) | 1 |
| ASDA78-NL | Load pattern | NotionalY(DL) | 1 |
| ASDA78-NL | Load pattern | NotionalX(LL) | 1 |
| ASDA78-NL | Load pattern | NotionalY(LL) | 1 |
| ASDA79crane-NL | Load pattern | DEAD | 1 |
| ASDA79crane-NL | Load pattern | CRv | 1 |
| ASDA79crane-NL | Load pattern | Live | 1 |
| ASDA79crane-NL | Load pattern | S | 1 |
| ASDA79crane-NL | Load pattern | TL | 1 |
| ASDA79crane-NL | Load pattern | FT | 1 |
| ASDA79crane-NL | Load pattern | NotionalX(DL) | 1 |
| ASDA79crane-NL | Load pattern | NotionalY(DL) | 1 |
| ASDA79crane-NL | Load pattern | NotionalX(LL) | 1 |
| ASDA79crane-NL | Load pattern | NotionalY(LL) | 1 |
| ASDA80crane-NL | Load pattern | DEAD | 1 |
| ASDA80crane-NL | Load pattern | CRv | 1 |
| ASDA80crane-NL | Load pattern | Live | 1 |
| ASDA80crane-NL | Load pattern | S | 1 |
| ASDA80crane-NL | Load pattern | TL | 1 |
| ASDA80crane-NL | Load pattern | FT | -1 |
| ASDA80crane-NL | Load pattern | NotionalX(DL) | 1 |
| ASDA80crane-NL | Load pattern | NotionalY(DL) | 1 |
| ASDA80crane-NL | Load pattern | NotionalX(LL) | 1 |
| ASDA80crane-NL | Load pattern | NotionalY(LL) | 1 |
| ASDA82-NL | Load pattern | DEAD | 1 |
| ASDA82-NL | Load pattern | CRv | 1 |
| ASDA82-NL | Load pattern | Live | 1 |
| ASDA82-NL | Load pattern | S | 1 |
| ASDA82-NL | Load pattern | TL | 1 |
| ASDA82-NL | Load pattern | NotionalX(DL) | 1 |
| ASDA82-NL | Load pattern | NotionalY(DL) | 1 |
| ASDA82-NL | Load pattern | NotionalX(LL) | 1 |
| ASDA82-NL | Load pattern | NotionalY(LL) | 1 |
| ASDA83crane-NL | Load pattern | DEAD | 1 |
| ASDA83crane-NL | Load pattern | CRv | 1 |
| ASDA83crane-NL | Load pattern | TL | 1 |
| ASDA83crane-NL | Load pattern | FL | 1 |
| ASDA83crane-NL | Load pattern | WLXP | 0.6 |
| ASDA83crane-NL | Load pattern | NotionalX(DL) | 1 |
| ASDA83crane-NL | Load pattern | NotionalY(DL) | 1 |
| ASDA84crane-NL | Load pattern | DEAD | 1 |
| ASDA84crane-NL | Load pattern | CRv | 1 |
| ASDA84crane-NL | Load pattern | TL | 1 |
| ASDA84crane-NL | Load pattern | FL | -1 |
| ASDA84crane-NL | Load pattern | WLXP | 0.6 |
| ASDA84crane-NL | Load pattern | NotionalX(DL) | 1 |
| ASDA84crane-NL | Load pattern | NotionalY(DL) | 1 |
| ASDA85crane-NL | Load pattern | DEAD | 1 |
| ASDA85crane-NL | Load pattern | CRv | 1 |
| ASDA85crane-NL | Load pattern | TL | 1 |
| ASDA85crane-NL | Load pattern | FL | 1 |
| ASDA85crane-NL | Load pattern | WLXP | -0.6 |
| ASDA85crane-NL | Load pattern | NotionalX(DL) | 1 |
| ASDA85crane-NL | Load pattern | NotionalY(DL) | 1 |
| ASDA86crane-NL | Load pattern | DEAD | 1 |
| ASDA86crane-NL | Load pattern | CRv | 1 |
| ASDA86crane-NL | Load pattern | TL | 1 |
| ASDA86crane-NL | Load pattern | FL | -1 |
| ASDA86crane-NL | Load pattern | WLXP | -0.6 |
| ASDA86crane-NL | Load pattern | NotionalX(DL) | 1 |
| ASDA86crane-NL | Load pattern | NotionalY(DL) | 1 |
| ASDA87-NL | Load pattern | DEAD | 1 |
| ASDA87-NL | Load pattern | CRv | 1 |
| ASDA87-NL | Load pattern | TL | 1 |
| ASDA87-NL | Load pattern | WLXP | 0.6 |
| ASDA87-NL | Load pattern | NotionalX(DL) | 1 |
| ASDA87-NL | Load pattern | NotionalY(DL) | 1 |
| ASDA89-NL | Load pattern | DEAD | 1 |
| ASDA89-NL | Load pattern | CRv | 1 |
| ASDA89-NL | Load pattern | TL | 1 |
| ASDA89-NL | Load pattern | WLXP | -0.6 |
| ASDA89-NL | Load pattern | NotionalX(DL) | 1 |
| ASDA89-NL | Load pattern | NotionalY(DL) | 1 |
| ASDA91crane-NL | Load pattern | DEAD | 1 |
| ASDA91crane-NL | Load pattern | CRv | 1 |
| ASDA91crane-NL | Load pattern | TL | 1 |
| ASDA91crane-NL | Load pattern | FT | 1 |
| ASDA91crane-NL | Load pattern | WLXP | 0.6 |
| ASDA91crane-NL | Load pattern | NotionalX(DL) | 1 |
| ASDA91crane-NL | Load pattern | NotionalY(DL) | 1 |
| ASDA92crane-NL | Load pattern | DEAD | 1 |
| ASDA92crane-NL | Load pattern | CRv | 1 |
| ASDA92crane-NL | Load pattern | TL | 1 |
| ASDA92crane-NL | Load pattern | FT | -1 |
| ASDA92crane-NL | Load pattern | WLXP | 0.6 |
| ASDA92crane-NL | Load pattern | NotionalX(DL) | 1 |
| ASDA92crane-NL | Load pattern | NotionalY(DL) | 1 |
| ASDA93crane-NL | Load pattern | DEAD | 1 |
| ASDA93crane-NL | Load pattern | CRv | 1 |
| ASDA93crane-NL | Load pattern | TL | 1 |
| ASDA93crane-NL | Load pattern | FT | 1 |
| ASDA93crane-NL | Load pattern | WLXP | -0.6 |
| ASDA93crane-NL | Load pattern | NotionalX(DL) | 1 |
| ASDA93crane-NL | Load pattern | NotionalY(DL) | 1 |
| ASDA94crane-NL | Load pattern | DEAD | 1 |
| ASDA94crane-NL | Load pattern | CRv | 1 |
| ASDA94crane-NL | Load pattern | TL | 1 |
| ASDA94crane-NL | Load pattern | FT | -1 |
| ASDA94crane-NL | Load pattern | WLXP | -0.6 |
| ASDA94crane-NL | Load pattern | NotionalX(DL) | 1 |
| ASDA94crane-NL | Load pattern | NotionalY(DL) | 1 |
| ASDA95-NL | Load pattern | DEAD | 1 |
| ASDA95-NL | Load pattern | CRv | 1 |
| ASDA95-NL | Load pattern | TL | 1 |
| ASDA95-NL | Load pattern | WLXP | 0.6 |
| ASDA95-NL | Load pattern | NotionalX(DL) | 1 |
| ASDA95-NL | Load pattern | NotionalY(DL) | 1 |
| ASDA97-NL | Load pattern | DEAD | 1 |
| ASDA97-NL | Load pattern | CRv | 1 |
| ASDA97-NL | Load pattern | TL | 1 |
| ASDA97-NL | Load pattern | WLXP | -0.6 |
| ASDA97-NL | Load pattern | NotionalX(DL) | 1 |
| ASDA97-NL | Load pattern | NotionalY(DL) | 1 |
| ASDA83-1crane-NL | Load pattern | DEAD | 1 |
| ASDA83-1crane-NL | Load pattern | CRv | 1 |
| ASDA83-1crane-NL | Load pattern | TL | 1 |
| ASDA83-1crane-NL | Load pattern | FL | 1 |
| ASDA83-1crane-NL | Load pattern | WLYP | 0.6 |
| ASDA83-1crane-NL | Load pattern | NotionalX(DL) | 1 |
| ASDA83-1crane-NL | Load pattern | NotionalY(DL) | 1 |
| ASDA84-1crane-NL | Load pattern | DEAD | 1 |
| ASDA84-1crane-NL | Load pattern | CRv | 1 |
| ASDA84-1crane-NL | Load pattern | TL | 1 |
| ASDA84-1crane-NL | Load pattern | FL | -1 |
| ASDA84-1crane-NL | Load pattern | WLYP | 0.6 |
| ASDA84-1crane-NL | Load pattern | NotionalX(DL) | 1 |
| ASDA84-1crane-NL | Load pattern | NotionalY(DL) | 1 |
| ASDA85-1crane-NL | Load pattern | DEAD | 1 |
| ASDA85-1crane-NL | Load pattern | CRv | 1 |
| ASDA85-1crane-NL | Load pattern | TL | 1 |
| ASDA85-1crane-NL | Load pattern | FL | 1 |
| ASDA85-1crane-NL | Load pattern | WLYP | -0.6 |
| ASDA85-1crane-NL | Load pattern | NotionalX(DL) | 1 |
| ASDA85-1crane-NL | Load pattern | NotionalY(DL) | 1 |
| ASDA86-1crane-NL | Load pattern | DEAD | 1 |
| ASDA86-1crane-NL | Load pattern | CRv | 1 |
| ASDA86-1crane-NL | Load pattern | TL | 1 |
| ASDA86-1crane-NL | Load pattern | FL | -1 |
| ASDA86-1crane-NL | Load pattern | WLYP | -0.6 |
| ASDA86-1crane-NL | Load pattern | NotionalX(DL) | 1 |
| ASDA86-1crane-NL | Load pattern | NotionalY(DL) | 1 |
| ASDA87-1-NL | Load pattern | DEAD | 1 |
| ASDA87-1-NL | Load pattern | CRv | 1 |
| ASDA87-1-NL | Load pattern | TL | 1 |
| ASDA87-1-NL | Load pattern | WLYP | 0.6 |
| ASDA87-1-NL | Load pattern | NotionalX(DL) | 1 |
| ASDA87-1-NL | Load pattern | NotionalY(DL) | 1 |
| ASDA89-1-NL | Load pattern | DEAD | 1 |
| ASDA89-1-NL | Load pattern | CRv | 1 |
| ASDA89-1-NL | Load pattern | TL | 1 |
| ASDA89-1-NL | Load pattern | WLYP | -0.6 |
| ASDA89-1-NL | Load pattern | NotionalX(DL) | 1 |
| ASDA89-1-NL | Load pattern | NotionalY(DL) | 1 |
| ASDA91-1crane-NL | Load pattern | DEAD | 1 |
| ASDA91-1crane-NL | Load pattern | CRv | 1 |
| ASDA91-1crane-NL | Load pattern | TL | 1 |
| ASDA91-1crane-NL | Load pattern | FT | 1 |
| ASDA91-1crane-NL | Load pattern | WLYP | 0.6 |
| ASDA91-1crane-NL | Load pattern | NotionalX(DL) | 1 |
| ASDA91-1crane-NL | Load pattern | NotionalY(DL) | 1 |
| ASDA92-1crane-NL | Load pattern | DEAD | 1 |
| ASDA92-1crane-NL | Load pattern | CRv | 1 |
| ASDA92-1crane-NL | Load pattern | TL | 1 |
| ASDA92-1crane-NL | Load pattern | FT | -1 |
| ASDA92-1crane-NL | Load pattern | WLYP | 0.6 |
| ASDA92-1crane-NL | Load pattern | NotionalX(DL) | 1 |
| ASDA92-1crane-NL | Load pattern | NotionalY(DL) | 1 |
| ASDA93-1crane-NL | Load pattern | DEAD | 1 |
| ASDA93-1crane-NL | Load pattern | CRv | 1 |
| ASDA93-1crane-NL | Load pattern | TL | 1 |
| ASDA93-1crane-NL | Load pattern | FT | 1 |
| ASDA93-1crane-NL | Load pattern | WLYP | -0.6 |
| ASDA93-1crane-NL | Load pattern | NotionalX(DL) | 1 |
| ASDA93-1crane-NL | Load pattern | NotionalY(DL) | 1 |
| ASDA94-1crane-NL | Load pattern | DEAD | 1 |
| ASDA94-1crane-NL | Load pattern | CRv | 1 |
| ASDA94-1crane-NL | Load pattern | TL | 1 |
| ASDA94-1crane-NL | Load pattern | FT | -1 |
| ASDA94-1crane-NL | Load pattern | WLYP | -0.6 |
| ASDA94-1crane-NL | Load pattern | NotionalX(DL) | 1 |
| ASDA94-1crane-NL | Load pattern | NotionalY(DL) | 1 |
| ASDA95-1-NL | Load pattern | DEAD | 1 |
| ASDA95-1-NL | Load pattern | CRv | 1 |
| ASDA95-1-NL | Load pattern | TL | 1 |
| ASDA95-1-NL | Load pattern | WLYP | 0.6 |
| ASDA95-1-NL | Load pattern | NotionalX(DL) | 1 |
| ASDA95-1-NL | Load pattern | NotionalY(DL) | 1 |
| ASDA97-1-NL | Load pattern | DEAD | 1 |
| ASDA97-1-NL | Load pattern | CRv | 1 |
| ASDA97-1-NL | Load pattern | TL | 1 |
| ASDA97-1-NL | Load pattern | WLYP | -0.6 |
| ASDA97-1-NL | Load pattern | NotionalX(DL) | 1 |
| ASDA97-1-NL | Load pattern | NotionalY(DL) | 1 |
| ASDA99crane-NL | Load pattern | DEAD | 1 |
| ASDA99crane-NL | Load pattern | CRv | 1 |
| ASDA99crane-NL | Load pattern | TL | 1 |
| ASDA99crane-NL | Load pattern | FL | 1 |
| ASDA99crane-NL | Load pattern | WLXP | 0.6 |
| ASDA99crane-NL | Load pattern | Live | 0.75 |
| ASDA99crane-NL | Load pattern | S | 0.75 |
| ASDA99crane-NL | Load pattern | NotionalX(DL) | 1 |
| ASDA99crane-NL | Load pattern | NotionalY(DL) | 1 |
| ASDA99crane-NL | Load pattern | NotionalX(LL) | 0.75 |
| ASDA99crane-NL | Load pattern | NotionalY(LL) | 0.75 |
| ASDA100crane-NL | Load pattern | DEAD | 1 |
| ASDA100crane-NL | Load pattern | CRv | 1 |
| ASDA100crane-NL | Load pattern | TL | 1 |
| ASDA100crane-NL | Load pattern | FL | -1 |
| ASDA100crane-NL | Load pattern | WLXP | 0.6 |
| ASDA100crane-NL | Load pattern | Live | 0.75 |
| ASDA100crane-NL | Load pattern | S | 0.75 |
| ASDA100crane-NL | Load pattern | NotionalX(DL) | 1 |
| ASDA100crane-NL | Load pattern | NotionalY(DL) | 1 |
| ASDA100crane-NL | Load pattern | NotionalX(LL) | 0.75 |
| ASDA100crane-NL | Load pattern | NotionalY(LL) | 0.75 |
| ASDA101crane-NL | Load pattern | DEAD | 1 |
| ASDA101crane-NL | Load pattern | CRv | 1 |
| ASDA101crane-NL | Load pattern | TL | 1 |
| ASDA101crane-NL | Load pattern | FL | 1 |
| ASDA101crane-NL | Load pattern | WLXP | -0.6 |
| ASDA101crane-NL | Load pattern | Live | 0.75 |
| ASDA101crane-NL | Load pattern | S | 0.75 |
| ASDA101crane-NL | Load pattern | NotionalX(DL) | 1 |
| ASDA101crane-NL | Load pattern | NotionalY(DL) | 1 |
| ASDA101crane-NL | Load pattern | NotionalX(LL) | 0.75 |
| ASDA101crane-NL | Load pattern | NotionalY(LL) | 0.75 |
| ASDA102crane-NL | Load pattern | DEAD | 1 |
| ASDA102crane-NL | Load pattern | CRv | 1 |
| ASDA102crane-NL | Load pattern | TL | 1 |
| ASDA102crane-NL | Load pattern | FL | -1 |
| ASDA102crane-NL | Load pattern | WLXP | -0.6 |
| ASDA102crane-NL | Load pattern | Live | 0.75 |
| ASDA102crane-NL | Load pattern | S | 0.75 |
| ASDA102crane-NL | Load pattern | NotionalX(DL) | 1 |
| ASDA102crane-NL | Load pattern | NotionalY(DL) | 1 |
| ASDA102crane-NL | Load pattern | NotionalX(LL) | 0.75 |
| ASDA102crane-NL | Load pattern | NotionalY(LL) | 0.75 |
| ASDA103-NL | Load pattern | DEAD | 1 |
| ASDA103-NL | Load pattern | CRv | 1 |
| ASDA103-NL | Load pattern | TL | 1 |
| ASDA103-NL | Load pattern | WLXP | 0.6 |
| ASDA103-NL | Load pattern | Live | 0.75 |
| ASDA103-NL | Load pattern | S | 0.75 |
| ASDA103-NL | Load pattern | NotionalX(DL) | 1 |
| ASDA103-NL | Load pattern | NotionalY(DL) | 1 |
| ASDA103-NL | Load pattern | NotionalX(LL) | 0.75 |
| ASDA103-NL | Load pattern | NotionalY(LL) | 0.75 |
| ASDA105-NL | Load pattern | DEAD | 1 |
| ASDA105-NL | Load pattern | CRv | 1 |
| ASDA105-NL | Load pattern | TL | 1 |
| ASDA105-NL | Load pattern | WLXP | -0.6 |
| ASDA105-NL | Load pattern | Live | 0.75 |
| ASDA105-NL | Load pattern | S | 0.75 |
| ASDA105-NL | Load pattern | NotionalX(DL) | 1 |
| ASDA105-NL | Load pattern | NotionalY(DL) | 1 |
| ASDA105-NL | Load pattern | NotionalX(LL) | 0.75 |
| ASDA105-NL | Load pattern | NotionalY(LL) | 0.75 |
| ASDA107crane-NL | Load pattern | DEAD | 1 |
| ASDA107crane-NL | Load pattern | CRv | 1 |
| ASDA107crane-NL | Load pattern | TL | 1 |
| ASDA107crane-NL | Load pattern | FT | 1 |
| ASDA107crane-NL | Load pattern | WLXP | 0.6 |
| ASDA107crane-NL | Load pattern | Live | 0.75 |
| ASDA107crane-NL | Load pattern | S | 0.75 |
| ASDA107crane-NL | Load pattern | NotionalX(DL) | 1 |
| ASDA107crane-NL | Load pattern | NotionalY(DL) | 1 |
| ASDA107crane-NL | Load pattern | NotionalX(LL) | 0.75 |
| ASDA107crane-NL | Load pattern | NotionalY(LL) | 0.75 |
| ASDA108crane-NL | Load pattern | DEAD | 1 |
| ASDA108crane-NL | Load pattern | CRv | 1 |
| ASDA108crane-NL | Load pattern | TL | 1 |
| ASDA108crane-NL | Load pattern | FT | -1 |
| ASDA108crane-NL | Load pattern | WLXP | 0.6 |
| ASDA108crane-NL | Load pattern | Live | 0.75 |
| ASDA108crane-NL | Load pattern | S | 0.75 |
| ASDA108crane-NL | Load pattern | NotionalX(DL) | 1 |
| ASDA108crane-NL | Load pattern | NotionalY(DL) | 1 |
| ASDA108crane-NL | Load pattern | NotionalX(LL) | 0.75 |
| ASDA108crane-NL | Load pattern | NotionalY(LL) | 0.75 |
| ASDA109crane-NL | Load pattern | DEAD | 1 |
| ASDA109crane-NL | Load pattern | CRv | 1 |
| ASDA109crane-NL | Load pattern | TL | 1 |
| ASDA109crane-NL | Load pattern | FT | 1 |
| ASDA109crane-NL | Load pattern | WLXP | -0.6 |
| ASDA109crane-NL | Load pattern | Live | 0.75 |
| ASDA109crane-NL | Load pattern | S | 0.75 |
| ASDA109crane-NL | Load pattern | NotionalX(DL) | 1 |
| ASDA109crane-NL | Load pattern | NotionalY(DL) | 1 |
| ASDA109crane-NL | Load pattern | NotionalX(LL) | 0.75 |
| ASDA109crane-NL | Load pattern | NotionalY(LL) | 0.75 |
| ASDA110crane-NL | Load pattern | DEAD | 1 |
| ASDA110crane-NL | Load pattern | CRv | 1 |
| ASDA110crane-NL | Load pattern | TL | 1 |
| ASDA110crane-NL | Load pattern | FT | -1 |
| ASDA110crane-NL | Load pattern | WLXP | -0.6 |
| ASDA110crane-NL | Load pattern | Live | 0.75 |
| ASDA110crane-NL | Load pattern | S | 0.75 |
| ASDA110crane-NL | Load pattern | NotionalX(DL) | 1 |
| ASDA110crane-NL | Load pattern | NotionalY(DL) | 1 |
| ASDA110crane-NL | Load pattern | NotionalX(LL) | 0.75 |
| ASDA110crane-NL | Load pattern | NotionalY(LL) | 0.75 |
| ASDA111-NL | Load pattern | DEAD | 1 |
| ASDA111-NL | Load pattern | CRv | 1 |
| ASDA111-NL | Load pattern | TL | 1 |
| ASDA111-NL | Load pattern | WLXP | 0.6 |
| ASDA111-NL | Load pattern | Live | 0.75 |
| ASDA111-NL | Load pattern | S | 0.75 |
| ASDA111-NL | Load pattern | NotionalX(DL) | 1 |
| ASDA111-NL | Load pattern | NotionalY(DL) | 1 |
| ASDA111-NL | Load pattern | NotionalX(LL) | 0.75 |
| ASDA111-NL | Load pattern | NotionalY(LL) | 0.75 |
| ASDA113-NL | Load pattern | DEAD | 1 |
| ASDA113-NL | Load pattern | CRv | 1 |
| ASDA113-NL | Load pattern | TL | 1 |
| ASDA113-NL | Load pattern | WLXP | -0.6 |
| ASDA113-NL | Load pattern | Live | 0.75 |
| ASDA113-NL | Load pattern | S | 0.75 |
| ASDA113-NL | Load pattern | NotionalX(DL) | 1 |
| ASDA113-NL | Load pattern | NotionalY(DL) | 1 |
| ASDA113-NL | Load pattern | NotionalX(LL) | 0.75 |
| ASDA113-NL | Load pattern | NotionalY(LL) | 0.75 |
| ASDA99-1crane-NL | Load pattern | DEAD | 1 |
| ASDA99-1crane-NL | Load pattern | CRv | 1 |
| ASDA99-1crane-NL | Load pattern | TL | 1 |
| ASDA99-1crane-NL | Load pattern | FL | 1 |
| ASDA99-1crane-NL | Load pattern | WLYP | 0.6 |
| ASDA99-1crane-NL | Load pattern | Live | 0.75 |
| ASDA99-1crane-NL | Load pattern | S | 0.75 |
| ASDA99-1crane-NL | Load pattern | NotionalX(DL) | 1 |
| ASDA99-1crane-NL | Load pattern | NotionalY(DL) | 1 |
| ASDA99-1crane-NL | Load pattern | NotionalX(LL) | 0.75 |
| ASDA99-1crane-NL | Load pattern | NotionalY(LL) | 0.75 |
| ASDA100-1crane-NL | Load pattern | DEAD | 1 |
| ASDA100-1crane-NL | Load pattern | CRv | 1 |
| ASDA100-1crane-NL | Load pattern | TL | 1 |
| ASDA100-1crane-NL | Load pattern | FL | -1 |
| ASDA100-1crane-NL | Load pattern | WLYP | 0.6 |
| ASDA100-1crane-NL | Load pattern | Live | 0.75 |
| ASDA100-1crane-NL | Load pattern | S | 0.75 |
| ASDA100-1crane-NL | Load pattern | NotionalX(DL) | 1 |
| ASDA100-1crane-NL | Load pattern | NotionalY(DL) | 1 |
| ASDA100-1crane-NL | Load pattern | NotionalX(LL) | 0.75 |
| ASDA100-1crane-NL | Load pattern | NotionalY(LL) | 0.75 |
| ASDA101-1crane-NL | Load pattern | DEAD | 1 |
| ASDA101-1crane-NL | Load pattern | CRv | 1 |
| ASDA101-1crane-NL | Load pattern | TL | 1 |
| ASDA101-1crane-NL | Load pattern | FL | 1 |
| ASDA101-1crane-NL | Load pattern | WLYP | -0.6 |
| ASDA101-1crane-NL | Load pattern | Live | 0.75 |
| ASDA101-1crane-NL | Load pattern | S | 0.75 |
| ASDA101-1crane-NL | Load pattern | NotionalX(DL) | 1 |
| ASDA101-1crane-NL | Load pattern | NotionalY(DL) | 1 |
| ASDA101-1crane-NL | Load pattern | NotionalX(LL) | 0.75 |
| ASDA101-1crane-NL | Load pattern | NotionalY(LL) | 0.75 |
| ASDA102-1crane-NL | Load pattern | DEAD | 1 |
| ASDA102-1crane-NL | Load pattern | CRv | 1 |
| ASDA102-1crane-NL | Load pattern | TL | 1 |
| ASDA102-1crane-NL | Load pattern | FL | -1 |
| ASDA102-1crane-NL | Load pattern | WLYP | -0.6 |
| ASDA102-1crane-NL | Load pattern | Live | 0.75 |
| ASDA102-1crane-NL | Load pattern | S | 0.75 |
| ASDA102-1crane-NL | Load pattern | NotionalX(DL) | 1 |
| ASDA102-1crane-NL | Load pattern | NotionalY(DL) | 1 |
| ASDA102-1crane-NL | Load pattern | NotionalX(LL) | 0.75 |
| ASDA102-1crane-NL | Load pattern | NotionalY(LL) | 0.75 |
| ASDA103-1-NL | Load pattern | DEAD | 1 |
| ASDA103-1-NL | Load pattern | CRv | 1 |
| ASDA103-1-NL | Load pattern | TL | 1 |
| ASDA103-1-NL | Load pattern | WLYP | 0.6 |
| ASDA103-1-NL | Load pattern | Live | 0.75 |
| ASDA103-1-NL | Load pattern | S | 0.75 |
| ASDA103-1-NL | Load pattern | NotionalX(DL) | 1 |
| ASDA103-1-NL | Load pattern | NotionalY(DL) | 1 |
| ASDA103-1-NL | Load pattern | NotionalX(LL) | 0.75 |
| ASDA103-1-NL | Load pattern | NotionalY(LL) | 0.75 |
| ASDA105-1-NL | Load pattern | DEAD | 1 |
| ASDA105-1-NL | Load pattern | CRv | 1 |
| ASDA105-1-NL | Load pattern | TL | 1 |
| ASDA105-1-NL | Load pattern | WLYP | -0.6 |
| ASDA105-1-NL | Load pattern | Live | 0.75 |
| ASDA105-1-NL | Load pattern | S | 0.75 |
| ASDA105-1-NL | Load pattern | NotionalX(DL) | 1 |
| ASDA105-1-NL | Load pattern | NotionalY(DL) | 1 |
| ASDA105-1-NL | Load pattern | NotionalX(LL) | 0.75 |
| ASDA105-1-NL | Load pattern | NotionalY(LL) | 0.75 |
| ASDA107-1crane-NL | Load pattern | DEAD | 1 |
| ASDA107-1crane-NL | Load pattern | CRv | 1 |
| ASDA107-1crane-NL | Load pattern | TL | 1 |
| ASDA107-1crane-NL | Load pattern | FT | 1 |
| ASDA107-1crane-NL | Load pattern | WLYP | 0.6 |
| ASDA107-1crane-NL | Load pattern | Live | 0.75 |
| ASDA107-1crane-NL | Load pattern | S | 0.75 |
| ASDA107-1crane-NL | Load pattern | NotionalX(DL) | 1 |
| ASDA107-1crane-NL | Load pattern | NotionalY(DL) | 1 |
| ASDA107-1crane-NL | Load pattern | NotionalX(LL) | 0.75 |
| ASDA107-1crane-NL | Load pattern | NotionalY(LL) | 0.75 |
| ASDA108-1crane-NL | Load pattern | DEAD | 1 |
| ASDA108-1crane-NL | Load pattern | CRv | 1 |
| ASDA108-1crane-NL | Load pattern | TL | 1 |
| ASDA108-1crane-NL | Load pattern | FT | -1 |
| ASDA108-1crane-NL | Load pattern | WLYP | 0.6 |
| ASDA108-1crane-NL | Load pattern | Live | 0.75 |
| ASDA108-1crane-NL | Load pattern | S | 0.75 |
| ASDA108-1crane-NL | Load pattern | NotionalX(DL) | 1 |
| ASDA108-1crane-NL | Load pattern | NotionalY(DL) | 1 |
| ASDA108-1crane-NL | Load pattern | NotionalX(LL) | 0.75 |
| ASDA108-1crane-NL | Load pattern | NotionalY(LL) | 0.75 |
| ASDA109-1crane-NL | Load pattern | DEAD | 1 |
| ASDA109-1crane-NL | Load pattern | CRv | 1 |
| ASDA109-1crane-NL | Load pattern | TL | 1 |
| ASDA109-1crane-NL | Load pattern | FT | 1 |
| ASDA109-1crane-NL | Load pattern | WLYP | -0.6 |
| ASDA109-1crane-NL | Load pattern | Live | 0.75 |
| ASDA109-1crane-NL | Load pattern | S | 0.75 |
| ASDA109-1crane-NL | Load pattern | NotionalX(DL) | 1 |
| ASDA109-1crane-NL | Load pattern | NotionalY(DL) | 1 |
| ASDA109-1crane-NL | Load pattern | NotionalX(LL) | 0.75 |
| ASDA109-1crane-NL | Load pattern | NotionalY(LL) | 0.75 |
| ASDA110-1crane-NL | Load pattern | DEAD | 1 |
| ASDA110-1crane-NL | Load pattern | CRv | 1 |
| ASDA110-1crane-NL | Load pattern | TL | 1 |
| ASDA110-1crane-NL | Load pattern | FT | -1 |
| ASDA110-1crane-NL | Load pattern | WLYP | -0.6 |
| ASDA110-1crane-NL | Load pattern | Live | 0.75 |
| ASDA110-1crane-NL | Load pattern | S | 0.75 |
| ASDA110-1crane-NL | Load pattern | NotionalX(DL) | 1 |
| ASDA110-1crane-NL | Load pattern | NotionalY(DL) | 1 |
| ASDA110-1crane-NL | Load pattern | NotionalX(LL) | 0.75 |
| ASDA110-1crane-NL | Load pattern | NotionalY(LL) | 0.75 |
| ASDA111-1-NL | Load pattern | DEAD | 1 |
| ASDA111-1-NL | Load pattern | CRv | 1 |
| ASDA111-1-NL | Load pattern | TL | 1 |
| ASDA111-1-NL | Load pattern | WLYP | 0.6 |
| ASDA111-1-NL | Load pattern | Live | 0.75 |
| ASDA111-1-NL | Load pattern | S | 0.75 |
| ASDA111-1-NL | Load pattern | NotionalX(DL) | 1 |
| ASDA111-1-NL | Load pattern | NotionalY(DL) | 1 |
| ASDA111-1-NL | Load pattern | NotionalX(LL) | 0.75 |
| ASDA111-1-NL | Load pattern | NotionalY(LL) | 0.75 |
| ASDA113-1-NL | Load pattern | DEAD | 1 |
| ASDA113-1-NL | Load pattern | CRv | 1 |
| ASDA113-1-NL | Load pattern | TL | 1 |
| ASDA113-1-NL | Load pattern | WLYP | -0.6 |
| ASDA113-1-NL | Load pattern | Live | 0.75 |
| ASDA113-1-NL | Load pattern | S | 0.75 |
| ASDA113-1-NL | Load pattern | NotionalX(DL) | 1 |
| ASDA113-1-NL | Load pattern | NotionalY(DL) | 1 |
| ASDA113-1-NL | Load pattern | NotionalX(LL) | 0.75 |
| ASDA113-1-NL | Load pattern | NotionalY(LL) | 0.75 |
| ASDA115crane-NL | Load pattern | DEAD | 0.6 |
| ASDA115crane-NL | Load pattern | CRv | 0.6 |
| ASDA115crane-NL | Load pattern | TL | 1 |
| ASDA115crane-NL | Load pattern | FL | 1 |
| ASDA115crane-NL | Load pattern | WLXP | 0.6 |
| ASDA115crane-NL | Load pattern | NotionalX(DL) | 0.6 |
| ASDA115crane-NL | Load pattern | NotionalY(DL) | 0.6 |
| ASDA116crane-NL | Load pattern | DEAD | 0.6 |
| ASDA116crane-NL | Load pattern | CRv | 0.6 |
| ASDA116crane-NL | Load pattern | TL | 1 |
| ASDA116crane-NL | Load pattern | FL | -1 |
| ASDA116crane-NL | Load pattern | WLXP | 0.6 |
| ASDA116crane-NL | Load pattern | NotionalX(DL) | 0.6 |
| ASDA116crane-NL | Load pattern | NotionalY(DL) | 0.6 |
| ASDA117crane-NL | Load pattern | DEAD | 0.6 |
| ASDA117crane-NL | Load pattern | CRv | 0.6 |
| ASDA117crane-NL | Load pattern | TL | 1 |
| ASDA117crane-NL | Load pattern | FL | 1 |
| ASDA117crane-NL | Load pattern | WLXP | -0.6 |
| ASDA117crane-NL | Load pattern | NotionalX(DL) | 0.6 |
| ASDA117crane-NL | Load pattern | NotionalY(DL) | 0.6 |
| ASDA118crane-NL | Load pattern | DEAD | 0.6 |
| ASDA118crane-NL | Load pattern | CRv | 0.6 |
| ASDA118crane-NL | Load pattern | TL | 1 |
| ASDA118crane-NL | Load pattern | FL | -1 |
| ASDA118crane-NL | Load pattern | WLXP | -0.6 |
| ASDA118crane-NL | Load pattern | NotionalX(DL) | 0.6 |
| ASDA118crane-NL | Load pattern | NotionalY(DL) | 0.6 |
| ASDA119-NL | Load pattern | DEAD | 0.6 |
| ASDA119-NL | Load pattern | CRv | 0.6 |
| ASDA119-NL | Load pattern | TL | 1 |
| ASDA119-NL | Load pattern | WLXP | 0.6 |
| ASDA119-NL | Load pattern | NotionalX(DL) | 0.6 |
| ASDA119-NL | Load pattern | NotionalY(DL) | 0.6 |
| ASDA121-NL | Load pattern | DEAD | 0.6 |
| ASDA121-NL | Load pattern | CRv | 0.6 |
| ASDA121-NL | Load pattern | TL | 1 |
| ASDA121-NL | Load pattern | WLXP | -0.6 |
| ASDA121-NL | Load pattern | NotionalX(DL) | 0.6 |
| ASDA121-NL | Load pattern | NotionalY(DL) | 0.6 |
| ASDA123crane-NL | Load pattern | DEAD | 0.6 |
| ASDA123crane-NL | Load pattern | CRv | 0.6 |
| ASDA123crane-NL | Load pattern | TL | 1 |
| ASDA123crane-NL | Load pattern | FT | 1 |
| ASDA123crane-NL | Load pattern | WLXP | 0.6 |
| ASDA123crane-NL | Load pattern | NotionalX(DL) | 0.6 |
| ASDA123crane-NL | Load pattern | NotionalY(DL) | 0.6 |
| ASDA124crane-NL | Load pattern | DEAD | 0.6 |
| ASDA124crane-NL | Load pattern | CRv | 0.6 |
| ASDA124crane-NL | Load pattern | TL | 1 |
| ASDA124crane-NL | Load pattern | FT | -1 |
| ASDA124crane-NL | Load pattern | WLXP | 0.6 |
| ASDA124crane-NL | Load pattern | NotionalX(DL) | 0.6 |
| ASDA124crane-NL | Load pattern | NotionalY(DL) | 0.6 |
| ASDA125crane-NL | Load pattern | DEAD | 0.6 |
| ASDA125crane-NL | Load pattern | CRv | 0.6 |
| ASDA125crane-NL | Load pattern | TL | 1 |
| ASDA125crane-NL | Load pattern | FT | 1 |
| ASDA125crane-NL | Load pattern | WLXP | -0.6 |
| ASDA125crane-NL | Load pattern | NotionalX(DL) | 0.6 |
| ASDA125crane-NL | Load pattern | NotionalY(DL) | 0.6 |
| ASDA126crane-NL | Load pattern | DEAD | 0.6 |
| ASDA126crane-NL | Load pattern | CRv | 0.6 |
| ASDA126crane-NL | Load pattern | TL | 1 |
| ASDA126crane-NL | Load pattern | FT | -1 |
| ASDA126crane-NL | Load pattern | WLXP | -0.6 |
| ASDA126crane-NL | Load pattern | NotionalX(DL) | 0.6 |
| ASDA126crane-NL | Load pattern | NotionalY(DL) | 0.6 |
| ASDA127-NL | Load pattern | DEAD | 0.6 |
| ASDA127-NL | Load pattern | CRv | 0.6 |
| ASDA127-NL | Load pattern | TL | 1 |
| ASDA127-NL | Load pattern | WLXP | 0.6 |
| ASDA127-NL | Load pattern | NotionalX(DL) | 0.6 |
| ASDA127-NL | Load pattern | NotionalY(DL) | 0.6 |
| ASDA129-NL | Load pattern | DEAD | 0.6 |
| ASDA129-NL | Load pattern | CRv | 0.6 |
| ASDA129-NL | Load pattern | TL | 1 |
| ASDA129-NL | Load pattern | WLXP | -0.6 |
| ASDA129-NL | Load pattern | NotionalX(DL) | 0.6 |
| ASDA129-NL | Load pattern | NotionalY(DL) | 0.6 |
| ASDA115-1crane-NL | Load pattern | DEAD | 0.6 |
| ASDA115-1crane-NL | Load pattern | CRv | 0.6 |
| ASDA115-1crane-NL | Load pattern | TL | 1 |
| ASDA115-1crane-NL | Load pattern | FL | 1 |
| ASDA115-1crane-NL | Load pattern | WLYP | 0.6 |
| ASDA115-1crane-NL | Load pattern | NotionalX(DL) | 0.6 |
| ASDA115-1crane-NL | Load pattern | NotionalY(DL) | 0.6 |
| ASDA116-1crane-NL | Load pattern | DEAD | 0.6 |
| ASDA116-1crane-NL | Load pattern | CRv | 0.6 |
| ASDA116-1crane-NL | Load pattern | TL | 1 |
| ASDA116-1crane-NL | Load pattern | FL | -1 |
| ASDA116-1crane-NL | Load pattern | WLYP | 0.6 |
| ASDA116-1crane-NL | Load pattern | NotionalX(DL) | 0.6 |
| ASDA116-1crane-NL | Load pattern | NotionalY(DL) | 0.6 |
| ASDA117-1crane-NL | Load pattern | DEAD | 0.6 |
| ASDA117-1crane-NL | Load pattern | CRv | 0.6 |
| ASDA117-1crane-NL | Load pattern | TL | 1 |
| ASDA117-1crane-NL | Load pattern | FL | 1 |
| ASDA117-1crane-NL | Load pattern | WLYP | -0.6 |
| ASDA117-1crane-NL | Load pattern | NotionalX(DL) | 0.6 |
| ASDA117-1crane-NL | Load pattern | NotionalY(DL) | 0.6 |
| ASDA118-1crane-NL | Load pattern | DEAD | 0.6 |
| ASDA118-1crane-NL | Load pattern | CRv | 0.6 |
| ASDA118-1crane-NL | Load pattern | TL | 1 |
| ASDA118-1crane-NL | Load pattern | FL | -1 |
| ASDA118-1crane-NL | Load pattern | WLYP | -0.6 |
| ASDA118-1crane-NL | Load pattern | NotionalX(DL) | 0.6 |
| ASDA118-1crane-NL | Load pattern | NotionalY(DL) | 0.6 |
| ASDA119-1-NL | Load pattern | DEAD | 0.6 |
| ASDA119-1-NL | Load pattern | CRv | 0.6 |
| ASDA119-1-NL | Load pattern | TL | 1 |
| ASDA119-1-NL | Load pattern | WLYP | 0.6 |
| ASDA119-1-NL | Load pattern | NotionalX(DL) | 0.6 |
| ASDA119-1-NL | Load pattern | NotionalY(DL) | 0.6 |
| ASDA121-1-NL | Load pattern | DEAD | 0.6 |
| ASDA121-1-NL | Load pattern | CRv | 0.6 |
| ASDA121-1-NL | Load pattern | TL | 1 |
| ASDA121-1-NL | Load pattern | WLYP | -0.6 |
| ASDA121-1-NL | Load pattern | NotionalX(DL) | 0.6 |
| ASDA121-1-NL | Load pattern | NotionalY(DL) | 0.6 |
| ASDA123-1crane-NL | Load pattern | DEAD | 0.6 |
| ASDA123-1crane-NL | Load pattern | CRv | 0.6 |
| ASDA123-1crane-NL | Load pattern | TL | 1 |
| ASDA123-1crane-NL | Load pattern | FT | 1 |
| ASDA123-1crane-NL | Load pattern | WLYP | 0.6 |
| ASDA123-1crane-NL | Load pattern | NotionalX(DL) | 0.6 |
| ASDA123-1crane-NL | Load pattern | NotionalY(DL) | 0.6 |
| ASDA124-1crane-NL | Load pattern | DEAD | 0.6 |
| ASDA124-1crane-NL | Load pattern | CRv | 0.6 |
| ASDA124-1crane-NL | Load pattern | TL | 1 |
| ASDA124-1crane-NL | Load pattern | FT | -1 |
| ASDA124-1crane-NL | Load pattern | WLYP | 0.6 |
| ASDA124-1crane-NL | Load pattern | NotionalX(DL) | 0.6 |
| ASDA124-1crane-NL | Load pattern | NotionalY(DL) | 0.6 |
| ASDA125-1crane-NL | Load pattern | DEAD | 0.6 |
| ASDA125-1crane-NL | Load pattern | CRv | 0.6 |
| ASDA125-1crane-NL | Load pattern | TL | 1 |
| ASDA125-1crane-NL | Load pattern | FT | 1 |
| ASDA125-1crane-NL | Load pattern | WLYP | -0.6 |
| ASDA125-1crane-NL | Load pattern | NotionalX(DL) | 0.6 |
| ASDA125-1crane-NL | Load pattern | NotionalY(DL) | 0.6 |
| ASDA126-1crane-NL | Load pattern | DEAD | 0.6 |
| ASDA126-1crane-NL | Load pattern | CRv | 0.6 |
| ASDA126-1crane-NL | Load pattern | TL | 1 |
| ASDA126-1crane-NL | Load pattern | FT | -1 |
| ASDA126-1crane-NL | Load pattern | WLYP | -0.6 |
| ASDA126-1crane-NL | Load pattern | NotionalX(DL) | 0.6 |
| ASDA126-1crane-NL | Load pattern | NotionalY(DL) | 0.6 |
| ASDA127-1-NL | Load pattern | DEAD | 0.6 |
| ASDA127-1-NL | Load pattern | CRv | 0.6 |
| ASDA127-1-NL | Load pattern | TL | 1 |
| ASDA127-1-NL | Load pattern | WLYP | 0.6 |
| ASDA127-1-NL | Load pattern | NotionalX(DL) | 0.6 |
| ASDA127-1-NL | Load pattern | NotionalY(DL) | 0.6 |
| ASDA129-1-NL | Load pattern | DEAD | 0.6 |
| ASDA129-1-NL | Load pattern | CRv | 0.6 |
| ASDA129-1-NL | Load pattern | TL | 1 |
| ASDA129-1-NL | Load pattern | WLYP | -0.6 |
| ASDA129-1-NL | Load pattern | NotionalX(DL) | 0.6 |
| ASDA129-1-NL | Load pattern | NotionalY(DL) | 0.6 |
| ASDD131-NL | Load pattern | DEAD | 1 |
| ASDD131-NL | Load pattern | CRv | 1 |
| ASDD131-NL | Load pattern | TL | 1 |
| ASDD131-NL | Load pattern | EQX | 0.7 |
| ASDD131-NL | Load pattern | EQY | 0.21 |
| ASDD131-NL | Load pattern | DEAD | 0.215 |
| ASDD131-NL | Load pattern | NotionalX(DL) | 1 |
| ASDD131-NL | Load pattern | NotionalY(DL) | 1 |
| ASDD132-NL | Load pattern | DEAD | 1 |
| ASDD132-NL | Load pattern | CRv | 1 |
| ASDD132-NL | Load pattern | TL | 1 |
| ASDD132-NL | Load pattern | EQX | -0.7 |
| ASDD132-NL | Load pattern | EQY | 0.21 |
| ASDD132-NL | Load pattern | DEAD | 0.215 |
| ASDD132-NL | Load pattern | NotionalX(DL) | 1 |
| ASDD132-NL | Load pattern | NotionalY(DL) | 1 |
| ASDD133-NL | Load pattern | DEAD | 1 |
| ASDD133-NL | Load pattern | CRv | 1 |
| ASDD133-NL | Load pattern | TL | 1 |
| ASDD133-NL | Load pattern | EQX | 0.7 |
| ASDD133-NL | Load pattern | EQY | -0.21 |
| ASDD133-NL | Load pattern | DEAD | 0.215 |
| ASDD133-NL | Load pattern | NotionalX(DL) | 1 |
| ASDD133-NL | Load pattern | NotionalY(DL) | 1 |
| ASDD134-NL | Load pattern | DEAD | 1 |
| ASDD134-NL | Load pattern | CRv | 1 |
| ASDD134-NL | Load pattern | TL | 1 |
| ASDD134-NL | Load pattern | EQX | -0.7 |
| ASDD134-NL | Load pattern | EQY | -0.21 |
| ASDD134-NL | Load pattern | DEAD | 0.215 |
| ASDD134-NL | Load pattern | NotionalX(DL) | 1 |
| ASDD134-NL | Load pattern | NotionalY(DL) | 1 |
| ASDD135-NL | Load pattern | DEAD | 1 |
| ASDD135-NL | Load pattern | CRv | 1 |
| ASDD135-NL | Load pattern | TL | 1 |
| ASDD135-NL | Load pattern | EQY | 0.7 |
| ASDD135-NL | Load pattern | EQX | 0.21 |
| ASDD135-NL | Load pattern | DEAD | 0.215 |
| ASDD135-NL | Load pattern | NotionalX(DL) | 1 |
| ASDD135-NL | Load pattern | NotionalY(DL) | 1 |
| ASDD136-NL | Load pattern | DEAD | 1 |
| ASDD136-NL | Load pattern | CRv | 1 |
| ASDD136-NL | Load pattern | TL | 1 |
| ASDD136-NL | Load pattern | EQY | -0.7 |
| ASDD136-NL | Load pattern | EQX | 0.21 |
| ASDD136-NL | Load pattern | DEAD | 0.215 |
| ASDD136-NL | Load pattern | NotionalX(DL) | 1 |
| ASDD136-NL | Load pattern | NotionalY(DL) | 1 |
| ASDD137-NL | Load pattern | DEAD | 1 |
| ASDD137-NL | Load pattern | CRv | 1 |
| ASDD137-NL | Load pattern | TL | 1 |
| ASDD137-NL | Load pattern | EQY | 0.7 |
| ASDD137-NL | Load pattern | EQX | -0.21 |
| ASDD137-NL | Load pattern | DEAD | 0.215 |
| ASDD137-NL | Load pattern | NotionalX(DL) | 1 |
| ASDD137-NL | Load pattern | NotionalY(DL) | 1 |
| ASDD138-NL | Load pattern | DEAD | 1 |
| ASDD138-NL | Load pattern | CRv | 1 |
| ASDD138-NL | Load pattern | TL | 1 |
| ASDD138-NL | Load pattern | EQY | -0.7 |
| ASDD138-NL | Load pattern | EQX | -0.21 |
| ASDD138-NL | Load pattern | DEAD | 0.215 |
| ASDD138-NL | Load pattern | NotionalX(DL) | 1 |
| ASDD138-NL | Load pattern | NotionalY(DL) | 1 |
| ASDD139-NL | Load pattern | DEAD | 1 |
| ASDD139-NL | Load pattern | CRv | 1 |
| ASDD139-NL | Load pattern | TL | 1 |
| ASDD139-NL | Load pattern | EQX | 0.525 |
| ASDD139-NL | Load pattern | EQY | 0.1575 |
| ASDD139-NL | Load pattern | Live | 0.75 |
| ASDD139-NL | Load pattern | S | 0.75 |
| ASDD139-NL | Load pattern | DEAD | 0.215 |
| ASDD139-NL | Load pattern | NotionalX(DL) | 1 |
| ASDD139-NL | Load pattern | NotionalY(DL) | 1 |
| ASDD139-NL | Load pattern | NotionalX(LL) | 0.75 |
| ASDD139-NL | Load pattern | NotionalY(LL) | 0.75 |
| ASDD140-NL | Load pattern | DEAD | 1 |
| ASDD140-NL | Load pattern | CRv | 1 |
| ASDD140-NL | Load pattern | TL | 1 |
| ASDD140-NL | Load pattern | EQX | -0.525 |
| ASDD140-NL | Load pattern | EQY | 0.1575 |
| ASDD140-NL | Load pattern | Live | 0.75 |
| ASDD140-NL | Load pattern | S | 0.75 |
| ASDD140-NL | Load pattern | DEAD | 0.215 |
| ASDD140-NL | Load pattern | NotionalX(DL) | 1 |
| ASDD140-NL | Load pattern | NotionalY(DL) | 1 |
| ASDD140-NL | Load pattern | NotionalX(LL) | 0.75 |
| ASDD140-NL | Load pattern | NotionalY(LL) | 0.75 |
| ASDD141-NL | Load pattern | DEAD | 1 |
| ASDD141-NL | Load pattern | CRv | 1 |
| ASDD141-NL | Load pattern | TL | 1 |
| ASDD141-NL | Load pattern | EQX | 0.525 |
| ASDD141-NL | Load pattern | EQY | -0.1575 |
| ASDD141-NL | Load pattern | Live | 0.75 |
| ASDD141-NL | Load pattern | S | 0.75 |
| ASDD141-NL | Load pattern | DEAD | 0.215 |
| ASDD141-NL | Load pattern | NotionalX(DL) | 1 |
| ASDD141-NL | Load pattern | NotionalY(DL) | 1 |
| ASDD141-NL | Load pattern | NotionalX(LL) | 0.75 |
| ASDD141-NL | Load pattern | NotionalY(LL) | 0.75 |
| ASDD142-NL | Load pattern | DEAD | 1 |
| ASDD142-NL | Load pattern | CRv | 1 |
| ASDD142-NL | Load pattern | TL | 1 |
| ASDD142-NL | Load pattern | EQX | -0.525 |
| ASDD142-NL | Load pattern | EQY | -0.1575 |
| ASDD142-NL | Load pattern | Live | 0.75 |
| ASDD142-NL | Load pattern | S | 0.75 |
| ASDD142-NL | Load pattern | DEAD | 0.215 |
| ASDD142-NL | Load pattern | NotionalY(DL) | 1 |
| ASDD142-NL | Load pattern | NotionalX(DL) | 1 |
| ASDD142-NL | Load pattern | NotionalX(LL) | 0.75 |
| ASDD142-NL | Load pattern | NotionalY(LL) | 0.75 |
| ASDD143-NL | Load pattern | DEAD | 1 |
| ASDD143-NL | Load pattern | CRv | 1 |
| ASDD143-NL | Load pattern | TL | 1 |
| ASDD143-NL | Load pattern | EQY | 0.525 |
| ASDD143-NL | Load pattern | EQX | 0.1575 |
| ASDD143-NL | Load pattern | Live | 0.75 |
| ASDD143-NL | Load pattern | S | 0.75 |
| ASDD143-NL | Load pattern | DEAD | 0.215 |
| ASDD143-NL | Load pattern | NotionalX(DL) | 1 |
| ASDD143-NL | Load pattern | NotionalY(DL) | 1 |
| ASDD143-NL | Load pattern | NotionalX(LL) | 0.75 |
| ASDD143-NL | Load pattern | NotionalY(LL) | 0.75 |
| ASDD144-NL | Load pattern | DEAD | 1 |
| ASDD144-NL | Load pattern | CRv | 1 |
| ASDD144-NL | Load pattern | TL | 1 |
| ASDD144-NL | Load pattern | EQY | -0.525 |
| ASDD144-NL | Load pattern | EQX | 0.1575 |
| ASDD144-NL | Load pattern | Live | 0.75 |
| ASDD144-NL | Load pattern | S | 0.75 |
| ASDD144-NL | Load pattern | DEAD | 0.215 |
| ASDD144-NL | Load pattern | NotionalX(DL) | 1 |
| ASDD144-NL | Load pattern | NotionalY(DL) | 1 |
| ASDD144-NL | Load pattern | NotionalX(LL) | 0.75 |
| ASDD144-NL | Load pattern | NotionalY(LL) | 0.75 |
| ASDD145-NL | Load pattern | DEAD | 1 |
| ASDD145-NL | Load pattern | CRv | 1 |
| ASDD145-NL | Load pattern | TL | 1 |
| ASDD145-NL | Load pattern | EQY | 0.525 |
| ASDD145-NL | Load pattern | EQX | -0.1575 |
| ASDD145-NL | Load pattern | Live | 0.75 |
| ASDD145-NL | Load pattern | S | 0.75 |
| ASDD145-NL | Load pattern | DEAD | 0.215 |
| ASDD145-NL | Load pattern | NotionalX(DL) | 1 |
| ASDD145-NL | Load pattern | NotionalY(DL) | 1 |
| ASDD145-NL | Load pattern | NotionalX(LL) | 0.75 |
| ASDD145-NL | Load pattern | NotionalY(LL) | 0.75 |
| ASDD146-NL | Load pattern | DEAD | 1 |
| ASDD146-NL | Load pattern | CRv | 1 |
| ASDD146-NL | Load pattern | TL | 1 |
| ASDD146-NL | Load pattern | EQY | -0.525 |
| ASDD146-NL | Load pattern | EQX | -0.1575 |
| ASDD146-NL | Load pattern | Live | 0.75 |
| ASDD146-NL | Load pattern | S | 0.75 |
| ASDD146-NL | Load pattern | DEAD | 0.215 |
| ASDD146-NL | Load pattern | NotionalX(DL) | 1 |
| ASDD146-NL | Load pattern | NotionalY(DL) | 1 |
| ASDD146-NL | Load pattern | NotionalX(LL) | 0.75 |
| ASDD146-NL | Load pattern | NotionalY(LL) | 0.75 |
| ASDD147-NL | Load pattern | DEAD | 0.6 |
| ASDD147-NL | Load pattern | CRv | 0.6 |
| ASDD147-NL | Load pattern | TL | 1 |
| ASDD147-NL | Load pattern | EQX | 0.7 |
| ASDD147-NL | Load pattern | EQY | 0.21 |
| ASDD147-NL | Load pattern | DEAD | 0.215 |
| ASDD147-NL | Load pattern | NotionalX(DL) | 0.6 |
| ASDD147-NL | Load pattern | NotionalY(DL) | 0.6 |
| ASDD148-NL | Load pattern | DEAD | 0.6 |
| ASDD148-NL | Load pattern | CRv | 0.6 |
| ASDD148-NL | Load pattern | TL | 1 |
| ASDD148-NL | Load pattern | EQX | -0.7 |
| ASDD148-NL | Load pattern | EQY | 0.21 |
| ASDD148-NL | Load pattern | DEAD | 0.215 |
| ASDD148-NL | Load pattern | NotionalX(DL) | 0.6 |
| ASDD148-NL | Load pattern | NotionalY(DL) | 0.6 |
| ASDD149-NL | Load pattern | DEAD | 0.6 |
| ASDD149-NL | Load pattern | CRv | 0.6 |
| ASDD149-NL | Load pattern | TL | 1 |
| ASDD149-NL | Load pattern | EQX | 0.7 |
| ASDD149-NL | Load pattern | EQY | -0.21 |
| ASDD149-NL | Load pattern | DEAD | 0.215 |
| ASDD149-NL | Load pattern | NotionalX(DL) | 0.6 |
| ASDD149-NL | Load pattern | NotionalY(DL) | 0.6 |
| ASDD150-NL | Load pattern | DEAD | 0.6 |
| ASDD150-NL | Load pattern | CRv | 0.6 |
| ASDD150-NL | Load pattern | TL | 1 |
| ASDD150-NL | Load pattern | EQX | -0.7 |
| ASDD150-NL | Load pattern | EQY | -0.21 |
| ASDD150-NL | Load pattern | DEAD | 0.215 |
| ASDD150-NL | Load pattern | NotionalX(DL) | 0.6 |
| ASDD150-NL | Load pattern | NotionalY(DL) | 0.6 |
| ASDD151-NL | Load pattern | DEAD | 0.6 |
| ASDD151-NL | Load pattern | CRv | 0.6 |
| ASDD151-NL | Load pattern | TL | 1 |
| ASDD151-NL | Load pattern | EQY | 0.7 |
| ASDD151-NL | Load pattern | EQX | 0.21 |
| ASDD151-NL | Load pattern | DEAD | 0.215 |
| ASDD151-NL | Load pattern | NotionalX(DL) | 0.6 |
| ASDD151-NL | Load pattern | NotionalY(DL) | 0.6 |
| ASDD152-NL | Load pattern | DEAD | 0.6 |
| ASDD152-NL | Load pattern | CRv | 0.6 |
| ASDD152-NL | Load pattern | TL | 1 |
| ASDD152-NL | Load pattern | EQY | -0.7 |
| ASDD152-NL | Load pattern | EQX | 0.21 |
| ASDD152-NL | Load pattern | DEAD | 0.215 |
| ASDD152-NL | Load pattern | NotionalX(DL) | 0.6 |
| ASDD152-NL | Load pattern | NotionalY(DL) | 0.6 |
| ASDD153-NL | Load pattern | DEAD | 0.6 |
| ASDD153-NL | Load pattern | CRv | 0.6 |
| ASDD153-NL | Load pattern | TL | 1 |
| ASDD153-NL | Load pattern | EQY | 0.7 |
| ASDD153-NL | Load pattern | EQX | -0.21 |
| ASDD153-NL | Load pattern | DEAD | 0.215 |
| ASDD153-NL | Load pattern | NotionalX(DL) | 0.6 |
| ASDD153-NL | Load pattern | NotionalY(DL) | 0.6 |
| ASDD154-NL | Load pattern | DEAD | 0.6 |
| ASDD154-NL | Load pattern | CRv | 0.6 |
| ASDD154-NL | Load pattern | TL | 1 |
| ASDD154-NL | Load pattern | EQY | -0.7 |
| ASDD154-NL | Load pattern | EQX | -0.21 |
| ASDD154-NL | Load pattern | DEAD | 0.215 |
| ASDD154-NL | Load pattern | NotionalX(DL) | 0.6 |
| ASDD154-NL | Load pattern | NotionalY(DL) | 0.6 |
| beam vertical def-NL | Load pattern | DEAD | 1 |
| beam vertical def-NL | Load pattern | CRv | 1 |
| beam vertical def-NL | Load pattern | Live | 1 |
| beam vertical def-NL | Load pattern | S | 1 |
| beam vertical def-NL | Load pattern | S | 0 |
| beam vertical def-NL | Load pattern | WALL | 1 |
| beam vertical def-NL | Load pattern | TL | 1 |

Figure 12- 3D MODEL OF CAPACITOR BANK AND CO2 ROOM

Figure 13- 3D MODEL OF TRANSFORMERS ROOM

Figure 14- 3D MODEL OF DIESEL ROOM

## CAPACITOR BANK AND CO2 ROOM design

## Wall design (CAPACITOR BANK AND CO2 ROOM)

Figure 15- MAX M11 (ton-m)

Figure 16- MIN M11 (ton-m)

Figure 17- MAX M22 (ton-m)

Figure 18- MIN M22 (ton-m)

Figure 19- MAX V23 (ton)

Figure 20- MIN V23 (ton)

Figure 21- MAX V13 (ton)

Figure 22- MIN V13 (ton)

Table 17- WALL RESULTANT FORCES (CAPACITOR BANK AND CO2 ROOM )

| RESULTANT FORCES |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| LOAD | M11(ton-m) |  | M22(ton-m) |  | V (ton) |
|  | MAX (+) | MAX (-) | MAX (+) | MAX (-) | MAX |
| Blast load | 7.6 | -6.8 | 14.5 | -18.0 | 15.5 |

Table 18- WALL DESIGN (CAPACITOR BANK AND CO2 ROOM)

b

d

fy

fc

Ø con

Mu(kg.cm)

100

24

5520

442

0.9

760000

Ru

=

(

Mu

/

Øbd

^

2

)

m=fy/(0.85*fc)

pb=0.85*ß*(fc/fy)*(6100/6100+fy)

p max=0.75*pb

chek-(

p<p,max)

chek

-

(

p

>

p

,

min

)

-

p

,

min

=

(14

/Fy)/2

?

As=

pbd

USE

0.030369997

0.022777498

ok

6.50

USE

Ø

16

@

20

=

10.00

ok

Specifications

Wall Design

(

M

11

)

14.69257386

14.66049383

0.002709831

Table 19- WALL DESIGN (CAPACITOR BANK AND CO2 ROOM)

b

d

fy

fc

Ø con

Mu(kg.cm)

100

24

5520

442

0.9

1800000

Ru

=

(

Mu

/

Øbd

^

2

)

m=fy/(0.85*fc)

pb=0.85*ß*(fc/fy)*(6100/6100+fy)

p max=0.75*pb

chek-(

p<p,max)

chek

-

(

p

>

p

,

min

)

-

p

,

min

=

(14/

Fy)/2

?

As=

pbd

USE

0.030369997

0.022777498

ok

15.70

USE

Ø

20

@

20

=

15.70

ok

Specifications

Wall  Design

(

M

22

)

14.69257386

34.72222222

0.00661136

Vu=15.5 ton

Vn=Vc+Vs

Vc=f'c6bwd=44.261000*240=265932.32N=26.59 ton

Vu>0.5Vc=13.295

USE∅8@400x400mm

Vs=Av.fy.ds=50.24*552*240400=16639.48*4=66557.95 N=6.65 ton

Vn=26.59+6.65=33.24 ton.>15.5 ton. →O.K

## slab DESIGN (CAPACITOR BANK AND CO2 ROOM)

Figure 23- MAX M11 (ton-m)

Figure 24- MIN M11 (ton-m)

Figure 25- MAX M22 (ton-m)

Figure 26- MINM22 (ton-m)

| RESULTANT FORCES |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| LOAD | M11(ton-m) |  | M22(ton-m) |  |
|  | MAX (+) | MAX (-) | MAX (+) | MAX (-) |
| Blast load | 3.5 | -1.0 | 11.37 | 7.0 |

Table 20- SLAB DESIGN (CAPACITOR BANK AND CO2 ROOM)

b

d

fy

fc

Ø con

Mu (kg.cm)

100

24

5520

442

0.9

350000

Ru

=

(

Mu

/

Øbd

^

2

)

m=fy/(0.85*fc)

pb=0.85*ß*(fc/fy)*(6100/6100+fy)

p max=0.75*pb

chek-(

p<p,max)

chek

-

(

p

>

p

,

min

)

-

p

,

min

=

(14/Fy)/2

As=

1.3Pbd

USE

Specifications

Slab  Design

(

M

11

)

14.69257386

6.75154321

0.001234297

0.030369997

0.022777498

ok

3.8510066

USE

Ø

16

@

20=10

No

Table 21- SLAB DESIGN (CAPACITOR BANK AND CO2 ROOM)

b

d

fy

fc

Ø con

Mu (kg.cm)

100

24

5520

442

0.9

1137000

Ru

=

(

Mu

/

Øbd

^

2

)

m=fy/(0.85*fc)

pb=0.85*ß*(fc/fy)*(6100/6100+fy)

p max=0.75*pb

chek-(

p<p,max)

chek

-

(

p

>

p

,

min

)

-

p

,

min

=

(14/Fy)/2

As=

Pbd

USE

Specifications

Slab  Design

(

M

22

)

14.69257386

21.9328703

0.004096634

0.030369997

0.022777498

ok

9.83192287

USE

Ø

16

@

20=10

oK

## settlement of the FOUNDATION (CAPACITOR BANK AND CO2 ROOM)

Table 22- FOUNDATION DISPLACEMENTS- BLAST LOAD -cm (CAPACITOR BANK AND CO2 ROOM)

| TABLE: Nodal Displacements |  |  |  |  |
| --- | --- | --- | --- | --- |
| JOINT | OUTPUT CASE | CASE TYPE | STEP TYPE | U3 |
| 29 | D+WA+L+8.6BWY-NL | LinStatic | MAX | -2.80 |

The maximum settlement of the foundation =2.8 cm <5cm – O.K

## Foundation design for resultant forces (CAPACITOR BANK AND CO2 ROOM)

- The characteristic of the soil under the foundation according to the geotechnical report no. BK-GCS-PEDCO-120-GT-RT-0001 is as follows.

- Table 23- SUBSTRATE REACTION MODULUS

| (kg/cm3) Substrate reaction modulus |  |  |  | B(m) |
| --- | --- | --- | --- | --- |
| L/B=10 | L/B=5 | L/B=2 | L/B=1 |  |
| 1.09 | 1.14 | 1.33 | 1.69 | 1.0 |
| 0.77 | 0.78 | 0.85 | 1.00 | 2.0 |
| 0.64 | 0.65 | 0.69 | 0.78 | 3.0 |
| 0.57 | 0.57 | 0.60 | 0.68 | 4.0 |
| 0.53 | 0.53 | 0.55 | 0.61 | 5.0 |

Table 24- LOAD COMBINATION FOR SOIL CONTROL. (CAPACITOR BANK AND CO2 ROOM)

Figure 27- DEFORMED SHAPE (ENV COM – CM)

e maximum deformation of the foundation is 2.5 cm, the deformation shown is much less than 5 cm.

Figure 28- SOIL STRESS UNDER THE FOUNDATION

The maximum soil stress under the foundation is 2.5 kg/cm^2.

Figure 29- X DIRECTION REINFORCEMENT DESIGN

Figure 30- Y DIRECTION REINFORCEMENT DESIGN

Use Ø16@15cm

## DRIFT CONTROL (capaciotr bank)

The design lateral displacement (nonlinear) at level 𝑥 shall be calculated from Equation below according to Iranian Seismic Design Code for Petroleum Facilities (Pub.038-16-3rd edition).

δx=CdδxeI

𝛿𝑥𝑒= elastic lateral displacement at level 𝑥, according to lateral load distribution from Equivalent Lateral Load Procedure or Modal Response Spectrum Analysis.

Stiffness modification for drift calculation:

Flat slabs & plates = 0.25 Ig

Beams = 0.35 Ig

Columns =0.7 Ig

Wall =0.35 Ig

Table 25- Drift Control (cm)

## transformer ROOM design

## WALL design (transformer room)

| MAX M11(+) | MAX M11(-) |
| --- | --- |
| MAX M22(+) | MAX M22(-) |

Figure 31- MAX WALL RESULTANT FORCES-ENVELOPE COMBO-(ton-m)

Table 26- WALL RESULTANT FORCES (Transformer room)

| RESULTANT FORCES |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| LOAD | M11(ton-m) |  | M22(ton-m) |  | V (ton) |
|  | MAX (+) | MAX (-) | MAX (+) | MAX (-) | MAX |
| Envelope | 1.4 | -1.4 | 4.0 | -4.0 | 3.00 |

Table 27- WALL DESIGN (TRANSFORMER ROOM)

b

d

fy

fc

Ø con

Mu(kg.cm)

100

20

4000

350

0.9

140000

Ru

=

(

Mu

/

Øbd

^

2

)

m=fy/(0.85*fc)

pb=0.85*ß*(fc/fy)*(6100/6100+fy)

p max=0.75*pb

chek-(

p<p,max)

chek

-

(

p

>

p

,

min

)

-

p

,

min

=

(14

/Fy)/2

As

=

1.3

pbd

USE

0.038181621

0.028636216

ok

2.34

USE

Ø

12@

25

=

4.52

no

Specifications

Wall Design

-

M

11

13.44537815

3.888888888

0.000978661

Table 28- WALL DESIGN (TRANSFORMER ROOM)(for base bar )

b

d

fy

fc

Ø con

Mu(kg.cm)

100

20

4000

350

0.9

400000

Ru

=

(

Mu

/

Øbd

^

2

)

m=fy/(0.85*fc)

pb=0.85*ß*(fc/fy)*(6100/6100+fy)

p max=0.75*pb

chek-(

p<p,max)

chek

-

(

p

>

p

,

min

)

-

p

,

min

=

(14/Fy)/2

As=

pbd

USE

0.038181621

0.028636216

ok

5.662

USE

Ø

16@

25

=

8.0

OK

Specifications

Wall Design

-

M

22

13.44537815

11.1111111

0.00283168

Vu=3.00 ton

Vn=Vc+Vs

Vc=f'c6bwd=3561000*200=197202.65N=19.72 ton

Vu=3.00 ton<0.5Vc=9.86 ton→O.K

## PURLIN design (transformer room)

Figure 32- PURLIN DESIGN –Z180**2.5

## PURLIN Deformed control (transformer room)

Table 29- LOAD COMBINATION FOR PURLIN DEFORMED CONTROL (TRANSFORMER ROOM)

Table 30- PURLIN DEFORMATION CONTROL (TRANSFORMER ROOM)

| Def<L/240 | L/240 | Length(cm) | Deformation(cm) | Load combination |
| --- | --- | --- | --- | --- |
| O.K | 1.875 | 450 | 1.08 | Deflection 5 |

## FOUNDATION design (transformer room)

The characteristic of the soil under the foundation according to the geotechnical report no. BK-GCS-PEDCO-120-GT-RT-0001 is as follows.

Table 31- SUBSTRATE REACTION MODULUS

| (kg/cm3) Substrate reaction modulus |  |  |  | B(m) |
| --- | --- | --- | --- | --- |
| L/B=10 | L/B=5 | L/B=2 | L/B=1 |  |
| 1.09 | 1.14 | 1.33 | 1.69 | 1.0 |
| 0.77 | 0.78 | 0.85 | 1.00 | 2.0 |
| 0.64 | 0.65 | 0.69 | 0.78 | 3.0 |
| 0.57 | 0.57 | 0.60 | 0.68 | 4.0 |
| 0.53 | 0.53 | 0.55 | 0.61 | 5.0 |

Table 32- LOAD COMBINATION FOR SOIL CONTROL. (TRANSFORMER ROOM)

| TABLE: Load Cases 06 - Loads Applied |  |  |
| --- | --- | --- |
| LoadCase | LoadPat | SF |
| Text | Text | Unitless |
| COMB1-NL | DEAD | 1 |
| COMB1-NL | LIVE | 0.75 |
| COMB1-NL | WB2 | 0.75 |
| COMB2-NL | DEAD | 1 |
| COMB2-NL | LIVE | 0.75 |
| COMB2-NL | WB1 | 0.75 |
| COMB3-NL | DEAD | 1 |
| COMB3-NL | LIVE | 0.75 |
| COMB3-NL | WA | 0.75 |
| COMB4-NL | DEAD | 1 |
| COMB4-NL | WB1 | 1 |
| COMB5-NL | DEAD | 1 |
| COMB5-NL | WB2 | 1 |
| COMB6-NL | DEAD | 1 |
| COMB6-NL | WA | 1 |
| COMB7-NL | DEAD | 1 |
| COMB7-NL | LIVE | 0.75 |
| COMB8-NL | DEAD | 1 |
| COMB8-NL | LIVE | 1 |
| COMB9-NL | DEAD | 0.6 |
| COMB9-NL | EX | 0.7 |
| COMB9-NL | EY | 0.21 |
| COMB10-NL | DEAD | 0.6 |
| COMB10-NL | EY | 0.7 |
| COMB10-NL | EX | 0.3 |
| COMB13-NL | DEAD | 0.6 |
| COMB13-NL | WB1 | 1 |
| COMB14-NL | DEAD | 0.6 |
| COMB14-NL | WB2 | 1 |
| COMB15-NL | DEAD | 0.6 |
| COMB15-NL | WA | 1 |
| COMB16-NL | DEAD | 1 |
| COMB16-NL | LIVE | 0.75 |
| COMB16-NL | EX | 0.525 |
| COMB16-NL | EY | 0.1575 |
| COMB18-NL | DEAD | 1 |
| COMB18-NL | LIVE | 0.75 |
| COMB18-NL | EY | 0.525 |
| COMB18-NL | EX | 0.1575 |
| COMB20-NL | DEAD | 1 |
| COMB20-NL | EY | 0.7 |
| COMB20-NL | EX | 0.21 |
| COMB22-NL | DEAD | 1 |
| COMB22-NL | EX | 0.7 |
| COMB22-NL | EY | 0.21 |
| COMB91-NL | DEAD | 0.6 |
| COMB91-NL | EX | -0.7 |
| COMB91-NL | EY | 0.21 |
| COMB92-NL | DEAD | 0.6 |
| COMB92-NL | EX | -0.7 |
| COMB92-NL | EY | -0.21 |
| COMB93-NL | DEAD | 0.6 |
| COMB93-NL | EX | 0.7 |
| COMB93-NL | EY | -0.21 |
| COMB101-NL | DEAD | 0.6 |
| COMB101-NL | EY | -0.7 |
| COMB101-NL | EX | 0.3 |
| COMB102-NL | DEAD | 0.6 |
| COMB102-NL | EY | -0.7 |
| COMB102-NL | EX | -0.3 |
| COMB103-NL | DEAD | 0.6 |
| COMB103-NL | EY | 0.7 |
| COMB103-NL | EX | -0.3 |
| COMB161-NL | DEAD | 1 |
| COMB161-NL | LIVE | 0.75 |
| COMB161-NL | EX | -0.525 |
| COMB161-NL | EY | 0.1575 |
| COMB162-NL | DEAD | 1 |
| COMB162-NL | LIVE | 0.75 |
| COMB162-NL | EX | 0.525 |
| COMB162-NL | EY | -0.1575 |
| COMB163-NL | DEAD | 1 |
| COMB163-NL | LIVE | 0.75 |
| COMB163-NL | EX | -0.525 |
| COMB163-NL | EY | -0.1575 |
| COMB181-NL | DEAD | 1 |
| COMB181-NL | LIVE | 0.75 |
| COMB181-NL | EY | 0.525 |
| COMB181-NL | EX | -0.1575 |
| COMB182-NL | DEAD | 1 |
| COMB182-NL | LIVE | 0.75 |
| COMB182-NL | EY | -0.525 |
| COMB182-NL | EX | 0.1575 |
| COMB183-NL | DEAD | 1 |
| COMB183-NL | LIVE | 0.75 |
| COMB183-NL | EY | -0.525 |
| COMB183-NL | EX | -0.1575 |
| COMB201-NL | DEAD | 1 |
| COMB201-NL | EY | -0.7 |
| COMB201-NL | EX | 0.21 |
| COMB202-NL | DEAD | 1 |
| COMB202-NL | EY | -0.7 |
| COMB202-NL | EX | -0.21 |
| COMB203-NL | DEAD | 1 |
| COMB203-NL | EY | 0.7 |
| COMB203-NL | EX | -0.21 |
| COMB221-NL | DEAD | 1 |
| COMB221-NL | EX | -0.7 |
| COMB221-NL | EY | 0.21 |
| COMB222-NL | DEAD | 1 |
| COMB222-NL | EX | 0.7 |
| COMB222-NL | EY | -0.21 |
| COMB223-NL | DEAD | 1 |
| COMB223-NL | EX | -0.7 |
| COMB223-NL | EY | -0.21 |

Figure 33- DEFORMED SHAPE (ENV COM – CM)

he maximum deformation of the foundation is 0.7 cm, the deformation shown is much less than 5 cm.

Figure 34- SOIL STRESS UNDER THE FOUNDATION

The maximum soil stress under the foundation is 1 kg/cm^2.

Figure 35- X DIRECTION REINFORCEMENT DESIGN

Use Ø16@20cm

Figure 36- Y DIRECTION REINFORCEMENT DESIGN

Use Ø16@20cm

## DIESEL ROOM design

## Vertical seismic component:

The vertical seismic load effect, 𝐸𝑣, shall be determined in accordance with the following Equation 6):

𝐸𝑣 = 0.2SDS𝐷

SDS = Design, 5% damped, spectral response acceleration parameter (g) at short periods (0.2 sec).

D = effect of dead load

Loads case name: EQZ=0.2×0.75×W=0.15×W

-Ev : Vertical seismic load applied at model:

Figure 37- applied Ev load

Ev applied at model as a portion of dead load as above.

This Earthquake coefficient will apply in SAP2000 model to be multiplied in W (seismic weight of structure) that will compute automatically by SAP2000 software by "mass source multiplier" definition as below:

1Dead+Crv and+0.2 Live Load

Ev applied at model as a portion of dead load as above.

## CRANE  load

Distribution of crane load is as below:

Capacity: 2000 kg

At critical condition maximum force is 1500 and 450 kg on each wheel of crane.

Kvs =1.25 (according to INBC no.6)

case 1   : FT=0.2×1500×1.25=375 kg     Fl=0.1×1500×1.25=187.5 kg

case 2 : FT=0.2×450×1.25=112.5kg     Fl=0.1×450×1.25=56.25 kg

Mentioned load applied in two case (assumed critical condition on left & right side)

Figure 38- applied CRv load

## Thermal Load of structure (TLst)

According to “Specification for Civil and Structural Design Criteria”. Maximum temperature of 28 ºC shall be considered for computing the thermal load in all components of shelter.

## Flextural design of crane beam

According to below output from sap software maximum crane beam moment under critical load combination is 42052.76 kg.cm :

∅Mn=0.9xZxFy=0.9x2400x677=1462320  kg.cm

Mu=42052.76kg.cm

s=42052.761462320=0.03 <1 ok

Figure 39- Moment 3-3 critical load combination on crane beam

## Deflection CONTROL:

Maximum beam deflection under crane live load on shelter is:

δ=PL348EI=3900*645^348*2.01*106*17145=0.63   cm < 0.645 ok

L1000=6451000=0.645 cm

## Drift control (WIND) :

Maximum displacement according to above output from sap model under critical service load combination with wind load case is about 1.11 cm which is less than allowable drift.

allowable drift is  555200=2.77 cm

According to “Civil & Structural Design Criteria”, horizontal displacements shall not exceed H/200.

The maximum displacement is less than H/200, so the displacement values are acceptable.

Figure 40- Deformed shape (maximum Drift critical Wx)

## Drift Control According to Iranian Seismic Design Code for petroleum facilities (038)

According to “Iranian seismic design code (Code.038)” table 4-8 ,drift shall not exceed 0.02.

The maximum driftt is less than 0.01, so the displacement values are acceptable.

The deflection at level x (δx) (in. or mm) used to compute the design story drift, Δ, shall be determined in accordance with the following equation:

Maximum displacement by EY load case is 4.15 cm which Reduced stiffness values used in the direct analysis method are not intended for use in beam vertical deflection, drift, and period of structure.

δx=CdδxeI=3×4.9×0.81.25=9.4cm ,    ∆=9.4555=0.016<0.02  ok

Driftallowable = According to table4-8 of Iranian seismic Design code (code No.038) is 0.02hsx

hsx=is the story height below level x

## Design Results

The steel structure is checked in accordance with LRFD method. Frame analysis and Structural checks are based on the 3D model that covers all the Load Combinations. All members designed by SAP2000, and code requirements have been checked accordingly. The following figures show the members ratios which are obtained from SAP2000 model analysis and design. All the acceptable ratios for beams & columns have been considered less than 1.0.

Figure 41- Steel Design Output

## COLUMN DESIGN

## BEAM DESIGN

## brace DESIGN

## CONNECTIONS (rafter conection)

Current Date: 4/16/2024 9:53 AM

Units system: Metric

File name: C:\Users\n.razani\Desktop\Ram Connection\RAFTER TO COL.rcnx

Steel connections

Results

Connection name	:	MEP_BS_APEX_EU_3/8_PL_2B_1B1/2

Connection ID	:	2

Family: Beam splice (BS)

Type: Moment end plate

Design code: AISC 360-16 LRFD

DEMANDS

Description	Ru	Pu	Mu	PufTop	PufBot	Load type

[T]	[T]	[T*m]	[T]	[T]

DL	0.00	0.00	0.00	0.00	0.00	Design

GEOMETRIC CONSIDERATIONS

Dimensions	Unit	Value	Min. value	Max. value	Sta.	References

tsmin = max(twb*(Fyb/Fys), (hst/0.56)*(Fys/E)1/2)

= max(0.8[cm]*(3515.33[kg/cm2]/2531.04[kg/cm2]), (11.2[cm]/0.56)*(2531.04[kg/cm2]/2.04E+06[kg/cm2])1/2)

= 1.111[cm]	DG4 Eq. 3.15,

AISC 358-10 Eq. 6.10-9,

Eq. 6.10-10

Vertical edge distance	[cm]	5.50	3.04	15.24		Sec. J3.5

Lemin = edmin + C2

= 3.035[cm] + 0[cm]

= 3.035[cm]	Tables J3.4,

J3.5

Lemax = min(12*tp, 6 [in])

= min(12*2.5[cm], 6 [in])

= 15.24[cm]	Sec. J3.5

Horizontal edge distance	[cm]	5.50	3.04	15.24		Sec. J3.5

Lemin = edmin + C2

= 3.035[cm] + 0[cm]

= 3.035[cm]	Tables J3.4,

J3.5

Lemax = min(12*tp, 6 [in])

= min(12*2.5[cm], 6 [in])

= 15.24[cm]	Sec. J3.5

Vertical bolt spacing (external flange)	[cm]	14.72	6.40	--		Sec. J3.3

smin = 8/3*d

= 8/3*2.4[cm]

= 6.4[cm]	Sec. J3.3

Vertical bolt spacing (internal flange)	[cm]	15.52	6.40	--		Sec. J3.3

smin = 8/3*d

= 8/3*2.4[cm]

= 6.4[cm]	Sec. J3.3

Horizontal center-to-center spacing (gage)	[cm]	14.00	6.40	20.00		Sec. J3.3,

DG4 Sec. 2.4,

DG4 Sec. 2.1,

2.4,

DG16 Sec. 2.5

gmin = Max(8/3*d, 2*k1c + 2*d, twb + 2*w + dh)

= Max(8/3*2.4[cm], 2*0[cm] + 2*2.4[cm], 0.8[cm] + 2*0.953[cm] + 2.718[cm])

= 6.4[cm]	Sec. J3.3,

DG4 Sec. 2.4

gmax = bfb

= 20[cm]	DG4 Sec. 2.1,

2.4,

DG16 Sec. 2.5

Outer bolt distance (external flange)	[cm]	5.70	3.67	--		DG4 Sec. 2.1

d< = 1 [in]2.4[cm]<

= 1 [in]True

pfmin = d + 1/2 [in]

= 2.4[cm] + 1/2 [in]

= 3.67[cm]	DG4 Sec. 2.1

Inner bolt distance (external flange)	[cm]	7.80	3.67	--		DG4 Sec. 2.1

d< = 1 [in]2.4[cm]<

= 1 [in]True

pfmin = d + 1/2 [in]

= 2.4[cm] + 1/2 [in]

= 3.67[cm]	DG4 Sec. 2.1

Outer bolt distance (internal flange)	[cm]	6.50	3.67	--		DG4 Sec. 2.1

d< = 1 [in]2.4[cm]<

= 1 [in]True

pfmin = d + 1/2 [in]

= 2.4[cm] + 1/2 [in]

= 3.67[cm]	DG4 Sec. 2.1

Inner bolt distance (internal flange)	[cm]	7.80	3.67	--		DG4 Sec. 2.1

d< = 1 [in]2.4[cm]<

= 1 [in]True

pfmin = d + 1/2 [in]

= 2.4[cm] + 1/2 [in]

= 3.67[cm]	DG4 Sec. 2.1

Bolt diameter	[cm]	2.40	--	3.81		DG4 Sec. 1.1

dbmax = 1.5 [in]	DG4 Sec. 1.1

- Use CJP weld for the end plate stiffener

Beam

Web	[1/16in]	6	3	--		table J2.4

wmin = wmin

= 0.004763	table J2.4

WARNINGS

- The connection does not comply with the section depth limits (AISC Design Guide 16 - Table 4-7)

DESIGN CHECK

Verification	Unit	Capacity	Demand	Ctrl EQ	Ratio	References

Moment end plate (external flange)

Flexural yielding	[Ton*m]	42.99	0.00	DL	0.00	DG16 Sec 2.5

s = 0.5*(bp*g)1/2

= 0.5*(25[cm]*14[cm])1/2

= 9.354[cm]	DG16 Table 3-2

pfi = min(pfi, s)

= min(7.8[cm], 9.354[cm])

= 7.8[cm]	DG16 Table 4-2

s> = de9.354[cm]>

= 5.5[cm]True

Yp = bp/2*(h1*(1/pfi + 1/s) + h0*(1/pf0 + 1/(2*s))) + 2/g*(h1*(pfi + s) + h0*(de + pf0))

= 25[cm]/2*(23.984[cm]*(1/7.8[cm] + 1/9.354[cm]) + 38.706[cm]*(1/5.7[cm] + 1/(2*9.354[cm]))) + 2/14[cm]*

(23.984[cm]*(7.8[cm] + 9.354[cm]) + 38.706[cm]*(5.5[cm] + 5.7[cm]))

= 301.935[cm]	DG16 Table 4-3

Mpl = Fyp*tp2*Yp

= 2531.04[kg/cm2]*2.5[cm]2*301.935[cm]

= 47.763[T*m]	DG16 Sec 2.5

IsFlushConnectionFalse

r = 1	DG16 Sec 2.5

Mn = b*Mpl/r

= 0.9*47.763[T*m]/1

= 42.987[T*m]	DG16 Sec 2.5

No prying bolt moment strength	[Ton*m]	26.39	0.00	DL	0.00	DG16 Sec 2.5

Pt = Ab*Fnt

= 4.524[cm2]*6327.63[kg/cm2]

= 28.625[T]	DG16 Sec 2.5

Mnp = 2*Pt*(dn)

= 2*28.625[T]*(61.468[cm])

= 35.191[T*m]	DG16 Sec 2.5

Mn = *Mnp

= 0.75*35.191[T*m]

= 26.393[T*m]	DG16 Sec 2.5

Bolts shear	[Ton]	51.53	0.00	DL	0.00	Tables (7-1..14)

Rn = *Fnv*Ab

= 0.75*3796.58[kg/cm2]*4.524[cm2]

= 12.881[T]	Eq. J3-1

Rn = C*Rn

= 4*12.881[T]

= 51.526[T]	Tables (7-1..14)

Bolt bearing under shear load	[Ton]	164.07	0.00	DL	0.00	Eq. J3-6

Lc-end = Max(0.0, Le - dh/2)

= Max(0.0, 5.5[cm] - 2.718[cm]/2)

= 4.141[cm]	Sec. J3.10

Lc-spa = Max(0.0, s - dh)

= Max(0.0, 14.722[cm] - 2.718[cm])

= 12.005[cm]	Sec. J3.10

Rn = *(min(k1*Lc-end, k2*d) + min(k1*Lc-spa, k2*d)*(n - 1))*tp*Fu*nc

= 0.75*(min(1.2*4.141[cm], 2.4*2.4[cm]) + min(1.2*12.005[cm], 2.4*2.4[cm])*(2 - 1))*2.5[cm]*4077.78[kg/cm2]*2

= 164.072[T]	Eq. J3-6

Shear yielding	[Ton]	85.42	0.00	DL	0.00	DG4 Eq. 3.12

Rn = *0.6*Fyp*bp*tp

= 0.9*0.6*2531.04[kg/cm2]*25[cm]*2.5[cm]

= 85.423[T]	DG4 Eq. 3.12

Shear rupture	[Ton]	88.30	0.00	DL	0.00	DG4 Eq 3.14,

AISC 358 Eq. 6.9-12,

DG4 Eq. 3.13

Lh = dh + 1/16 [in]

= 2.718[cm] + 1/16 [in]

= 2.876[cm]	Sec. D3-2

An = (bp - 2*Lh)*tp

= (25[cm] - 2*2.876[cm])*2.5[cm]

= 48.119[cm2]	DG4 Eq 3.14,

AISC 358 Eq. 6.9-12

Rn = *0.6*Fup*An

= 0.75*0.6*4077.78[kg/cm2]*48.119[cm2]

= 88.298[T]	DG4 Eq. 3.13

Moment end plate (internal flange)

Flexural yielding	[Ton*m]	42.62	0.00	DL	0.00	DG16 Sec 2.5

s = 0.5*(bp*g)1/2

= 0.5*(25[cm]*14[cm])1/2

= 9.354[cm]	DG16 Table 3-2

pfi = min(pfi, s)

= min(7.8[cm], 9.354[cm])

= 7.8[cm]	DG16 Table 4-2

s> = de9.354[cm]>

= 5.5[cm]True

Yp = bp/2*(h1*(1/pfi + 1/s) + h0*(1/pf0 + 1/(2*s))) + 2/g*(h1*(pfi + s) + h0*(de + pf0))

= 25[cm]/2*(23.984[cm]*(1/7.8[cm] + 1/9.354[cm]) + 39.506[cm]*(1/6.5[cm] + 1/(2*9.354[cm]))) + 2/14[cm]*

(23.984[cm]*(7.8[cm] + 9.354[cm]) + 39.506[cm]*(5.5[cm] + 6.5[cm]))

= 299.356[cm]	DG16 Table 4-3

Mpl = Fyp*tp2*Yp

= 2531.04[kg/cm2]*2.5[cm]2*299.356[cm]

= 47.355[T*m]	DG16 Sec 2.5

IsFlushConnectionFalse

r = 1	DG16 Sec 2.5

Mn = b*Mpl/r

= 0.9*47.355[T*m]/1

= 42.62[T*m]	DG16 Sec 2.5

No prying bolt moment strength	[Ton*m]	26.74	0.00	DL	0.00	DG16 Sec 2.5

Pt = Ab*Fnt

= 4.524[cm2]*6327.63[kg/cm2]

= 28.625[T]	DG16 Sec 2.5

Mnp = 2*Pt*(dn)

= 2*28.625[T]*(62.268[cm])

= 35.649[T*m]	DG16 Sec 2.5

Mn = *Mnp

= 0.75*35.649[T*m]

= 26.737[T*m]	DG16 Sec 2.5

Bolts shear	[Ton]	51.53	0.00	DL	0.00	Tables (7-1..14)

Rn = *Fnv*Ab

= 0.75*3796.58[kg/cm2]*4.524[cm2]

= 12.881[T]	Eq. J3-1

Rn = C*Rn

= 4*12.881[T]

= 51.526[T]	Tables (7-1..14)

Bolt bearing under shear load	[Ton]	164.07	0.00	DL	0.00	Eq. J3-6

Lc-end = Max(0.0, Le - dh/2)

= Max(0.0, 5.5[cm] - 2.718[cm]/2)

= 4.141[cm]	Sec. J3.10

Lc-spa = Max(0.0, s - dh)

= Max(0.0, 15.522[cm] - 2.718[cm])

= 12.805[cm]	Sec. J3.10

Rn = *(min(k1*Lc-end, k2*d) + min(k1*Lc-spa, k2*d)*(n - 1))*tp*Fu*nc

= 0.75*(min(1.2*4.141[cm], 2.4*2.4[cm]) + min(1.2*12.805[cm], 2.4*2.4[cm])*(2 - 1))*2.5[cm]*4077.78[kg/cm2]*2

= 164.072[T]	Eq. J3-6

Shear yielding	[Ton]	85.42	0.00	DL	0.00	DG4 Eq. 3.12

Rn = *0.6*Fyp*bp*tp

= 0.9*0.6*2531.04[kg/cm2]*25[cm]*2.5[cm]

= 85.423[T]	DG4 Eq. 3.12

Rn = *0.6*Fyp*bp*tp

= 0.9*0.6*2531.04[kg/cm2]*25[cm]*2.5[cm]

= 85.423[T]	DG4 Eq. 3.12

Shear rupture	[Ton]	88.30	0.00	DL	0.00	DG4 Eq 3.14,

AISC 358 Eq. 6.9-12,

DG4 Eq. 3.13

Lh = dh + 1/16 [in]

= 2.718[cm] + 1/16 [in]

= 2.876[cm]	Sec. D3-2

An = (bp - 2*Lh)*tp

= (25[cm] - 2*2.876[cm])*2.5[cm]

= 48.119[cm2]	DG4 Eq 3.14,

AISC 358 Eq. 6.9-12

Rn = *0.6*Fup*An

= 0.75*0.6*4077.78[kg/cm2]*48.119[cm2]

= 88.298[T]	DG4 Eq. 3.13

Beam

Web weld shear strength	[Ton]	45.59	0.00	DL	0.00	Eq. J2-4

Fw = 0.6*FEXX

= 0.6*4921.46[kg/cm2]

= 2952.88[kg/cm2]	Sec. J2.4

Aw = (2)1/2/2*D/16 [in]*L

= (2)1/2/2*6/16 [in]*15.281[cm]

= 10.292[cm2]	Sec. J2.4

Rn = 2 * (*Fw*Aw)

= 2 * (0.75*2952.88[kg/cm2]*10.292[cm2])

= 45.586[T]	Eq. J2-4

Web weld strength to reach yield stress	[Ton/m]	443.39	253.10	DL	0.57	Eq. J2-4,

Eq. J4-1

LoadAngleFactor = 1 + 0.5*(sin())1.5

= 1 + 0.5*(sin(1.763))1.5

= 1.486	p. 8-9

Fw = 0.6*FEXX*LoadAngleFactor

= 0.6*4921.46[kg/cm2]*1.486

= 4388.81[kg/cm2]	Sec. J2.5

Rw = 2 * (*Fw*(2)1/2/2*D/16 [in])

= 2 * (0.75*4388.81[kg/cm2]*(2)1/2/2*6/16 [in])

= 4.434[T/cm]	Eq. J2-4

Rn = *Fy*tw

= 0.9*3515.33[kg/cm2]*0.8[cm]

= 2.531[T/cm]	Eq. J4-1

Shear yielding	[Ton]	54.67	0.00	DL	0.00	Eq. J4-3

Ag = Lp*tp

= 32.4[cm]*0.8[cm]

= 25.92[cm2]	Sec. D3-1

Rn = *0.60*Fy*Ag

= 1*0.60*3515.33[kg/cm2]*25.92[cm2]

= 54.67[T]	Eq. J4-3

Global critical strength ratio	0.57

NOTATION

Ab:	Nominal bolt area

Ag:	Gross area

ai:	Distance from the interior bolt centerline to the prying force

An:	Net area

ao:	Distance from the outer bolt centerline to the prying force

Aw:	Effective area of the weld

bfb:	Beam flange breadth

bp:	Plate width

C:	Bolt group coefficient

C2:	Edge distance increment

d:	Nominal bolt diameter

d0:	Distance from the center of the beam compression flange to the outer bolt centerline in extended end-plate configurations

d1:	Distance from the center of the beam compression flange to the farthest inner load-carrying bolt centerline

d2:	Distance from the center of the beam compression flange to the second farthest inner load-carrying bolt centerline

d3:	Distance from the center of the beam compression flange to the third farthest inner load-carrying bolt centerline

dbmax:	Maximum bolt diameter

de:	Distance from the first bolt row to the top plate edge

dh:	Nominal hole dimension

discr:	Discriminant under the root sign for the calculation of Qmaxi, Qmaxo

D:	Number of sixteenths of an inch in the weld size

E:	Elastic modulus

FEXX:	Electrode classification number

Fnt:	Nominal tensile stress

Fnv:	Nominal shear stress

Fi':	Flange force per bolt at the thin plate limit when calculating Qmaxi for end-plate configurations with large inner pitch distances

Fo':	Flange force per bolt at the thin plate limit when calculating Qmaxo for end-plate configurations with large inner pitch distances

Fu:	Specified minimum tensile strength

Fup:	Specified minimum tensile strength of the plate

Fw:	Nominal strength of the weld metal per unit area

Fy:	Specified minimum yield stress

Fyb:	Specified minimum yield stress of beam, plate or branch material

Fyp:	Specified minimum yield stress of plate

Fys:	Specified minimum yield stress of stiffener material

g:	Transversal gage between bolts

gmax:	Maximum bolt gage

gmin:	Minimum bolt gage

r:	Load factor to limit connection rotation at ultimate moment to 10% of simple span rotation

h0:	Distance from the compression side of the beam to the outer bolt centerline in extended end-plate configurations

h1:	Distance from the compression side of the beam to the farthest inner load-carrying bolt line

hst:	Stiffener height

IsFlushConnection:	Is flush connection

k1:	Bearing factor

k1c:	Distance from column web centerline to flange toe of fillet

k2:	Bearing factor

Lc-end:	Clear distance

Le:	Edge distance

Lemax:	Maximum edge distance

Lemin:	Minimum edge distance

Lh:	Hole dimension for tension and shear net area

Lp:	Plate length

L:	Length of weld

LoadAngleFactor:	Load angle factor

Mnp:	No prying moment

Mpl:	End plate or column flange flexural strength

Mq:	Connection strength for the limit state of bolt fracture with prying action

edmin:	Minimum edge distance

n:	Bolts rows number

nc:	Number of bolt columns

pext:	End-plate extension beyond the exterior face of the beam tension flange

pf0:	Distance from the inside of a beam tension flange to the nearest outside bolt row

pfi:	Distance from the inside of a beam tension flange to the nearest inside bolt row

pfmin:	Minimum distance from the inside of a beam tension flange to the nearest inside bolt row

Pt:	Bolt tensile strength

:	Design factors

b:	Design factor for bending

Mn:	Design or allowable strength

Rn:	Design or allowable strength

Rn:	Design or allowable strength per unit length

Rw:	Fillet weld capacity per unit length

Qmaxi:	Maximum possible prying force for interior bolts

Qmaxo:	Maximum possible prying force for outer bolts

s:	Distance from the most inside or outside tension bolt row to the edge of a yield line

smin:	Minimum spacing

s:	Longitudinal bolt spacing

Lc-spa:	Distance between adjacent holes edges

dn:	Sum of all distances from centerline of compression flange to the nth bolt row

tp:	Thickness of the connected material

Tb:	Minimum fastener pretension

tp:	Plate thickness

tsmin:	Minimum plate stiffener thickness

tw:	Web thickness

twb:	Thickness of beam web

:	Load angle

ThickPlateSmallerBoltsBehaviorApply:	Thick plate behavior controled by bolt rupturwe without prying action apply

wmin:	Minimum weld size required

w':	Width of end-plate per bolt minus the bolt hole diameter

w:	Weld size

Yp:	Yield line mechanism parameter

## CONNECTIONS (rafter to column)

Current Date: 4/16/2024 10:28 AM

Units system: Metric

File name: D:\farajian\PROJECT\01-BINAK\08-Chemical Injection\D04\RAM\BASE PLATE.rcnx

Steel connections

Results

Connection name	:	MEP_BCF_DG16_F_1PL_2B_2B1 1/4

Connection ID	:	3

Family: Beam - Column flange (BCF)

Type: Moment end plate

Design code: AISC 360-16 LRFD

DEMANDS

Beam			Right beam			Left beam			Column			Panel

Description	Ru	Pu	Mu	PufTop	PufBot	PufTop	PufBot	Pu	Vu	Load type

[T]	[T]	[T*m]	[T]	[T]	[T]	[T]	[T]	[T]

DL	11.29	2.19	11.50	-35.08	37.28	0.00	0.00	0.00	37.28	Design

GEOMETRIC CONSIDERATIONS

Dimensions	Unit	Value	Min. value	Max. value	Sta.	References

Extended end plate

End plate stiffener thickness	[cm]	1.00	0.80	--		DG4 Eq. 3.15,

AISC 358-10 Eq. 6.10-9,

Eq. 6.10-10

Vertical edge distance	[cm]	7.00	2.84	15.24		Sec. J3.5

Horizontal edge distance	[cm]	6.00	2.84	15.24		Sec. J3.5

Vertical bolt spacing (external flange)	[cm]	12.22	5.87	--		Sec. J3.3

Vertical bolt spacing (internal flange)	[cm]	12.22	5.87	--		Sec. J3.3

Horizontal center-to-center spacing (gage)	[cm]	9.00	5.87	20.00		Sec. J3.3,

DG4 Sec. 2.4,

DG4 Sec. 2.1,

2.4,

DG16 Sec. 2.5

Outer bolt distance (external flange)	[cm]	5.00	3.47	--		DG4 Sec. 2.1

Inner bolt distance (external flange)	[cm]	6.00	3.47	--		DG4 Sec. 2.1

Outer bolt distance (internal flange)	[cm]	5.00	3.47	--		DG4 Sec. 2.1

Inner bolt distance (internal flange)	[cm]	6.00	3.47	--		DG4 Sec. 2.1

Bolt diameter	[cm]	2.20	--	3.81		DG4 Sec. 1.1

- Use CJP weld for the end plate stiffener

Beam

Web	[1/16in]	8	3	--		table J2.4

Support

Horizontal edge distance	[cm]	5.50	2.84	14.40		Sec. J3.5

Transverse stiffeners

Length	[cm]	33.00	16.50	33.00		Sec. J10.8

Width	[cm]	12.00	6.60	--		Sec. J10.8

PLATE / COLUMN BEHAVIOR

End plate behaviour (external flange)

Thick plate behavior controlled by no prying bolt rupture

End plate behaviour (internal flange)

Thick plate behavior controlled by no prying bolt rupture

Column flange behavior (external flange)

Thin plate behavior controlled by plate yielding

Column flange behavior (internal flange)

Thin plate behavior controlled by plate yielding

DESIGN CHECK

Verification	Unit	Capacity	Demand	Ctrl EQ	Ratio	References

Moment end plate (external flange)

Flexural yielding	[Ton*m]	53.52	0.00	DL	0.00	DG16 Sec 2.5

No prying bolt moment strength	[Ton*m]	22.57	0.00	DL	0.00	DG16 Sec 2.5

Bolts shear	[Ton]	43.30	11.29	DL	0.26	Tables (7-1..14)

Bolt bearing under shear load	[Ton]	146.52	0.00	DL	0.00	Eq. J3-6

Shear yielding	[Ton]	68.04	17.54	DL	0.26	DG4 Eq. 3.12

Shear rupture	[Ton]	66.45	17.54	DL	0.26	DG4 Eq 3.14,

AISC 358 Eq. 6.9-12,

DG4 Eq. 3.13

Moment end plate (internal flange)

Flexural yielding	[Ton*m]	53.52	11.85	DL	0.22	DG16 Sec 2.5

No prying bolt moment strength	[Ton*m]	22.57	11.85	DL	0.52	DG16 Sec 2.5

Bolts shear	[Ton]	43.30	0.00	DL	0.00	Tables (7-1..14)

Bolt bearing under shear load	[Ton]	146.52	11.29	DL	0.08	Eq. J3-6

Shear yielding	[Ton]	68.04	18.64	DL	0.27	DG4 Eq. 3.12

Shear rupture	[Ton]	66.45	18.64	DL	0.28	DG4 Eq 3.14,

AISC 358 Eq. 6.9-12,

DG4 Eq. 3.13

Beam

Web weld shear strength	[Ton]	60.78	11.29	DL	0.19	Eq. J2-4

Web weld strength to reach yield stress	[Ton/m]	591.19	172.80	DL	0.29	Eq. J2-4,

Eq. J4-1

Shear yielding	[Ton]	37.32	11.29	DL	0.30	Eq. J4-3

Support

Flexural yielding (external flange)	[Ton*m]	11.97	0.00	DL	0.00	DG4 Eq. 3.20,

Sec. 2.2.3,

DG4 Eq. 3.21

Bolt rupture with prying moment strength	[Ton*m]	18.55	0.00	DL	0.00	DG16 Sec 2.5

Support bolt bearing (external flange)	[Ton]	70.33	0.00	DL	0.00	Eq. J3-6

Flexural yielding (internal flange)	[Ton*m]	11.97	11.85	DL	0.99	DG4 Eq. 3.20,

Sec. 2.2.3,

DG4 Eq. 3.21

Bolt rupture with prying moment strength	[Ton*m]	18.55	11.85	DL	0.64	DG16 Sec 2.5

Support bolt bearing (internal flange)	[Ton]	70.33	11.29	DL	0.16	Eq. J3-6

Panel web shear	[Ton]	58.32	37.28	DL	0.64	Sec. J10-6,

Eq. J10-9,

Sec. J4.4

Support - right side

Local web yielding	[Ton]	73.25	37.28	DL	0.51	DG4 eq. 3.24,

DG13 Eq. 4.3-1,

Sec. J10

Transverse stiffeners - top

Yielding strength due to axial load	[Ton]	47.52	0.00	DL	0.00	Eq. J4-1

Compression	[Ton]	36.36	9.36	DL	0.26	Sec. J4.4

Transverse stiffeners - bottom

Yielding strength due to axial load	[Ton]	47.52	11.55	DL	0.24	Eq. J4-1

Compression	[Ton]	36.36	0.00	DL	0.00	Sec. J4.4

Diagonal stiffeners

Yielding strength due to axial load	[Ton]	53.30	0.83	DL	0.02	Eq. J4-1,

Sec. J10-6,

Eq. J10-9

Compression	[Ton]	31.16	0.00	DL	0.00	Sec. J4.4

Flange weld capacity	[Ton]	36.35	0.83	DL	0.02	Eq. J2-4,

Sec. J10-6,

Eq. J10-9

Web weld capacity	[Ton]	125.00	0.83	DL	0.01	Eq. J2-4,

Sec. J10-6,

Eq. J10-9

Global critical strength ratio	0.99

## PURLIN DESIGN

Property of PURLIN (UNP 140)

## Roof bracing Design

According to INBC No.10 section 10-2-3-4 for tensile member :

Roof brace =∅20

∅tPn=∅tFyAg=0.9×4000×3.14=11304 kg

According to sap model maximum tensile force is 495 kg & it’s OK.

| TABLE: Element Forces - Frames |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Frame | Station | OutputCase | CaseType | StepType | P |
| Text | m | Text | Text | Text | Kgf |
| 10 | 0 | Envelope Strength | Combination | Max | 432 |
| 10 | 3.55581 | Envelope Strength | Combination | Max | 433.28 |
| 10 | 7.11161 | Envelope Strength | Combination | Max | 434.56 |
| 10 | 0 | Envelope Strength | Combination | Min | -1.28 |
| 10 | 3.55581 | Envelope Strength | Combination | Min | -0.000126 |
| 10 | 7.11161 | Envelope Strength | Combination | Min | 1.01 |
| 11 | 0 | Envelope Strength | Combination | Max | 465.92 |
| 11 | 3.55581 | Envelope Strength | Combination | Max | 467.24 |
| 11 | 7.11161 | Envelope Strength | Combination | Max | 468.55 |
| 11 | 0 | Envelope Strength | Combination | Min | 37.95 |
| 11 | 3.55581 | Envelope Strength | Combination | Min | 38.99 |
| 11 | 7.11161 | Envelope Strength | Combination | Min | 40.03 |
| 12 | 0 | Envelope Strength | Combination | Max | 411.69 |
| 12 | 3.55581 | Envelope Strength | Combination | Max | 410.35 |
| 12 | 7.11161 | Envelope Strength | Combination | Max | 409.02 |
| 12 | 0 | Envelope Strength | Combination | Min | 1.05 |
| 12 | 3.55581 | Envelope Strength | Combination | Min | -0.0001027 |
| 12 | 7.11161 | Envelope Strength | Combination | Min | -1.34 |
| 13 | 0 | Envelope Strength | Combination | Max | 495.93 |
| 13 | 3.55581 | Envelope Strength | Combination | Max | 494.63 |
| 13 | 7.11161 | Envelope Strength | Combination | Max | 493.34 |
| 13 | 0 | Envelope Strength | Combination | Min | 1.02 |
| 13 | 3.55581 | Envelope Strength | Combination | Min | -0.00005286 |
| 13 | 7.11161 | Envelope Strength | Combination | Min | -1.02 |

## FOUNDATION DESIGN

The characteristic of the soil under the foundation according to the geotechnical report no. BK-GCS-PEDCO-120-GT-RT-0001 is as follows.

- Table 33- SUBSTRATE REACTION MODULUS

| (kg/cm3) Substrate reaction modulus |  |  |  | B(m) |
| --- | --- | --- | --- | --- |
| L/B=10 | L/B=5 | L/B=2 | L/B=1 |  |
| 1.09 | 1.14 | 1.33 | 1.69 | 1.0 |
| 0.77 | 0.78 | 0.85 | 1.00 | 2.0 |
| 0.64 | 0.65 | 0.69 | 0.78 | 3.0 |
| 0.57 | 0.57 | 0.60 | 0.68 | 4.0 |
| 0.53 | 0.53 | 0.55 | 0.61 | 5.0 |

Table 34- LOAD COMBINATION FOR SOIL CONTROL. (TRANSFORMER ROOM)

| TABLE: Load Cases 06 - Loads Applied |  |  |
| --- | --- | --- |
| LoadCase | LoadPat | SF |
| Text | Text | Unitless |
| ASDA100-1crane-NL-NL | DEAD | 1 |
| ASDA100-1crane-NL-NL | CRv | 1 |
| ASDA100-1crane-NL-NL | TL | 1 |
| ASDA100-1crane-NL-NL | FL | -1 |
| ASDA100-1crane-NL-NL | WLYP | 0.6 |
| ASDA100-1crane-NL-NL | Live | 0.75 |
| ASDA100-1crane-NL-NL | S | 0.75 |
| ASDA100-1crane-NL-NL | NotionalX(DL) | 1 |
| ASDA100-1crane-NL-NL | NotionalY(DL) | 1 |
| ASDA100-1crane-NL-NL | NotionalX(LL) | 0.75 |
| ASDA100-1crane-NL-NL | NotionalY(LL) | 0.75 |
| ASDA100crane-NL-NL | DEAD | 1 |
| ASDA100crane-NL-NL | CRv | 1 |
| ASDA100crane-NL-NL | TL | 1 |
| ASDA100crane-NL-NL | FL | -1 |
| ASDA100crane-NL-NL | WLXP | 0.6 |
| ASDA100crane-NL-NL | Live | 0.75 |
| ASDA100crane-NL-NL | S | 0.75 |
| ASDA100crane-NL-NL | NotionalX(DL) | 1 |
| ASDA100crane-NL-NL | NotionalY(DL) | 1 |
| ASDA100crane-NL-NL | NotionalX(LL) | 0.75 |
| ASDA100crane-NL-NL | NotionalY(LL) | 0.75 |
| ASDA101-1crane-NL-NL | DEAD | 1 |
| ASDA101-1crane-NL-NL | CRv | 1 |
| ASDA101-1crane-NL-NL | TL | 1 |
| ASDA101-1crane-NL-NL | FL | 1 |
| ASDA101-1crane-NL-NL | WLYP | -0.6 |
| ASDA101-1crane-NL-NL | Live | 0.75 |
| ASDA101-1crane-NL-NL | S | 0.75 |
| ASDA101-1crane-NL-NL | NotionalX(DL) | 1 |
| ASDA101-1crane-NL-NL | NotionalY(DL) | 1 |
| ASDA101-1crane-NL-NL | NotionalX(LL) | 0.75 |
| ASDA101-1crane-NL-NL | NotionalY(LL) | 0.75 |
| ASDA101crane-NL-NL | DEAD | 1 |
| ASDA101crane-NL-NL | CRv | 1 |
| ASDA101crane-NL-NL | TL | 1 |
| ASDA101crane-NL-NL | FL | 1 |
| ASDA101crane-NL-NL | WLXP | -0.6 |
| ASDA101crane-NL-NL | Live | 0.75 |
| ASDA101crane-NL-NL | S | 0.75 |
| ASDA101crane-NL-NL | NotionalX(DL) | 1 |
| ASDA101crane-NL-NL | NotionalY(DL) | 1 |
| ASDA101crane-NL-NL | NotionalX(LL) | 0.75 |
| ASDA101crane-NL-NL | NotionalY(LL) | 0.75 |
| ASDA102-1crane-NL-NL | DEAD | 1 |
| ASDA102-1crane-NL-NL | CRv | 1 |
| ASDA102-1crane-NL-NL | TL | 1 |
| ASDA102-1crane-NL-NL | FL | -1 |
| ASDA102-1crane-NL-NL | WLYP | -0.6 |
| ASDA102-1crane-NL-NL | Live | 0.75 |
| ASDA102-1crane-NL-NL | S | 0.75 |
| ASDA102-1crane-NL-NL | NotionalX(DL) | 1 |
| ASDA102-1crane-NL-NL | NotionalY(DL) | 1 |
| ASDA102-1crane-NL-NL | NotionalX(LL) | 0.75 |
| ASDA102-1crane-NL-NL | NotionalY(LL) | 0.75 |
| ASDA102crane-NL-NL | DEAD | 1 |
| ASDA102crane-NL-NL | CRv | 1 |
| ASDA102crane-NL-NL | TL | 1 |
| ASDA102crane-NL-NL | FL | -1 |
| ASDA102crane-NL-NL | WLXP | -0.6 |
| ASDA102crane-NL-NL | Live | 0.75 |
| ASDA102crane-NL-NL | S | 0.75 |
| ASDA102crane-NL-NL | NotionalX(DL) | 1 |
| ASDA102crane-NL-NL | NotionalY(DL) | 1 |
| ASDA102crane-NL-NL | NotionalX(LL) | 0.75 |
| ASDA102crane-NL-NL | NotionalY(LL) | 0.75 |
| ASDA103-1-NL-NL | DEAD | 1 |
| ASDA103-1-NL-NL | CRv | 1 |
| ASDA103-1-NL-NL | TL | 1 |
| ASDA103-1-NL-NL | WLYP | 0.6 |
| ASDA103-1-NL-NL | Live | 0.75 |
| ASDA103-1-NL-NL | S | 0.75 |
| ASDA103-1-NL-NL | NotionalX(DL) | 1 |
| ASDA103-1-NL-NL | NotionalY(DL) | 1 |
| ASDA103-1-NL-NL | NotionalX(LL) | 0.75 |
| ASDA103-1-NL-NL | NotionalY(LL) | 0.75 |
| ASDA103-NL-NL | DEAD | 1 |
| ASDA103-NL-NL | CRv | 1 |
| ASDA103-NL-NL | TL | 1 |
| ASDA103-NL-NL | WLXP | 0.6 |
| ASDA103-NL-NL | Live | 0.75 |
| ASDA103-NL-NL | S | 0.75 |
| ASDA103-NL-NL | NotionalX(DL) | 1 |
| ASDA103-NL-NL | NotionalY(DL) | 1 |
| ASDA103-NL-NL | NotionalX(LL) | 0.75 |
| ASDA103-NL-NL | NotionalY(LL) | 0.75 |
| ASDA105-1-NL-NL | DEAD | 1 |
| ASDA105-1-NL-NL | CRv | 1 |
| ASDA105-1-NL-NL | TL | 1 |
| ASDA105-1-NL-NL | WLYP | -0.6 |
| ASDA105-1-NL-NL | Live | 0.75 |
| ASDA105-1-NL-NL | S | 0.75 |
| ASDA105-1-NL-NL | NotionalX(DL) | 1 |
| ASDA105-1-NL-NL | NotionalY(DL) | 1 |
| ASDA105-1-NL-NL | NotionalX(LL) | 0.75 |
| ASDA105-1-NL-NL | NotionalY(LL) | 0.75 |
| ASDA105-NL-NL | DEAD | 1 |
| ASDA105-NL-NL | CRv | 1 |
| ASDA105-NL-NL | TL | 1 |
| ASDA105-NL-NL | WLXP | -0.6 |
| ASDA105-NL-NL | Live | 0.75 |
| ASDA105-NL-NL | S | 0.75 |
| ASDA105-NL-NL | NotionalX(DL) | 1 |
| ASDA105-NL-NL | NotionalY(DL) | 1 |
| ASDA105-NL-NL | NotionalX(LL) | 0.75 |
| ASDA105-NL-NL | NotionalY(LL) | 0.75 |
| ASDA107-1crane-NL-NL | DEAD | 1 |
| ASDA107-1crane-NL-NL | CRv | 1 |
| ASDA107-1crane-NL-NL | TL | 1 |
| ASDA107-1crane-NL-NL | FT | 1 |
| ASDA107-1crane-NL-NL | WLYP | 0.6 |
| ASDA107-1crane-NL-NL | Live | 0.75 |
| ASDA107-1crane-NL-NL | S | 0.75 |
| ASDA107-1crane-NL-NL | NotionalX(DL) | 1 |
| ASDA107-1crane-NL-NL | NotionalY(DL) | 1 |
| ASDA107-1crane-NL-NL | NotionalX(LL) | 0.75 |
| ASDA107-1crane-NL-NL | NotionalY(LL) | 0.75 |
| ASDA107crane-NL-NL | DEAD | 1 |
| ASDA107crane-NL-NL | CRv | 1 |
| ASDA107crane-NL-NL | TL | 1 |
| ASDA107crane-NL-NL | FT | 1 |
| ASDA107crane-NL-NL | WLXP | 0.6 |
| ASDA107crane-NL-NL | Live | 0.75 |
| ASDA107crane-NL-NL | S | 0.75 |
| ASDA107crane-NL-NL | NotionalX(DL) | 1 |
| ASDA107crane-NL-NL | NotionalY(DL) | 1 |
| ASDA107crane-NL-NL | NotionalX(LL) | 0.75 |
| ASDA107crane-NL-NL | NotionalY(LL) | 0.75 |
| ASDA108-1crane-NL-NL | DEAD | 1 |
| ASDA108-1crane-NL-NL | CRv | 1 |
| ASDA108-1crane-NL-NL | TL | 1 |
| ASDA108-1crane-NL-NL | FT | -1 |
| ASDA108-1crane-NL-NL | WLYP | 0.6 |
| ASDA108-1crane-NL-NL | Live | 0.75 |
| ASDA108-1crane-NL-NL | S | 0.75 |
| ASDA108-1crane-NL-NL | NotionalX(DL) | 1 |
| ASDA108-1crane-NL-NL | NotionalY(DL) | 1 |
| ASDA108-1crane-NL-NL | NotionalX(LL) | 0.75 |
| ASDA108-1crane-NL-NL | NotionalY(LL) | 0.75 |
| ASDA108crane-NL-NL | DEAD | 1 |
| ASDA108crane-NL-NL | CRv | 1 |
| ASDA108crane-NL-NL | TL | 1 |
| ASDA108crane-NL-NL | FT | -1 |
| ASDA108crane-NL-NL | WLXP | 0.6 |
| ASDA108crane-NL-NL | Live | 0.75 |
| ASDA108crane-NL-NL | S | 0.75 |
| ASDA108crane-NL-NL | NotionalX(DL) | 1 |
| ASDA108crane-NL-NL | NotionalY(DL) | 1 |
| ASDA108crane-NL-NL | NotionalX(LL) | 0.75 |
| ASDA108crane-NL-NL | NotionalY(LL) | 0.75 |
| ASDA109-1crane-NL-NL | DEAD | 1 |
| ASDA109-1crane-NL-NL | CRv | 1 |
| ASDA109-1crane-NL-NL | TL | 1 |
| ASDA109-1crane-NL-NL | FT | 1 |
| ASDA109-1crane-NL-NL | WLYP | -0.6 |
| ASDA109-1crane-NL-NL | Live | 0.75 |
| ASDA109-1crane-NL-NL | S | 0.75 |
| ASDA109-1crane-NL-NL | NotionalX(DL) | 1 |
| ASDA109-1crane-NL-NL | NotionalY(DL) | 1 |
| ASDA109-1crane-NL-NL | NotionalX(LL) | 0.75 |
| ASDA109-1crane-NL-NL | NotionalY(LL) | 0.75 |
| ASDA109crane-NL-NL | DEAD | 1 |
| ASDA109crane-NL-NL | CRv | 1 |
| ASDA109crane-NL-NL | TL | 1 |
| ASDA109crane-NL-NL | FT | 1 |
| ASDA109crane-NL-NL | WLXP | -0.6 |
| ASDA109crane-NL-NL | Live | 0.75 |
| ASDA109crane-NL-NL | S | 0.75 |
| ASDA109crane-NL-NL | NotionalX(DL) | 1 |
| ASDA109crane-NL-NL | NotionalY(DL) | 1 |
| ASDA109crane-NL-NL | NotionalX(LL) | 0.75 |
| ASDA109crane-NL-NL | NotionalY(LL) | 0.75 |
| ASDA110-1crane-NL-NL | DEAD | 1 |
| ASDA110-1crane-NL-NL | CRv | 1 |
| ASDA110-1crane-NL-NL | TL | 1 |
| ASDA110-1crane-NL-NL | FT | -1 |
| ASDA110-1crane-NL-NL | WLYP | -0.6 |
| ASDA110-1crane-NL-NL | Live | 0.75 |
| ASDA110-1crane-NL-NL | S | 0.75 |
| ASDA110-1crane-NL-NL | NotionalX(DL) | 1 |
| ASDA110-1crane-NL-NL | NotionalY(DL) | 1 |
| ASDA110-1crane-NL-NL | NotionalX(LL) | 0.75 |
| ASDA110-1crane-NL-NL | NotionalY(LL) | 0.75 |
| ASDA110crane-NL-NL | DEAD | 1 |
| ASDA110crane-NL-NL | CRv | 1 |
| ASDA110crane-NL-NL | TL | 1 |
| ASDA110crane-NL-NL | FT | -1 |
| ASDA110crane-NL-NL | WLXP | -0.6 |
| ASDA110crane-NL-NL | Live | 0.75 |
| ASDA110crane-NL-NL | S | 0.75 |
| ASDA110crane-NL-NL | NotionalX(DL) | 1 |
| ASDA110crane-NL-NL | NotionalY(DL) | 1 |
| ASDA110crane-NL-NL | NotionalX(LL) | 0.75 |
| ASDA110crane-NL-NL | NotionalY(LL) | 0.75 |
| ASDA111-1-NL-NL | DEAD | 1 |
| ASDA111-1-NL-NL | CRv | 1 |
| ASDA111-1-NL-NL | TL | 1 |
| ASDA111-1-NL-NL | WLYP | 0.6 |
| ASDA111-1-NL-NL | Live | 0.75 |
| ASDA111-1-NL-NL | S | 0.75 |
| ASDA111-1-NL-NL | NotionalX(DL) | 1 |
| ASDA111-1-NL-NL | NotionalY(DL) | 1 |
| ASDA111-1-NL-NL | NotionalX(LL) | 0.75 |
| ASDA111-1-NL-NL | NotionalY(LL) | 0.75 |
| ASDA111-NL-NL | DEAD | 1 |
| ASDA111-NL-NL | CRv | 1 |
| ASDA111-NL-NL | TL | 1 |
| ASDA111-NL-NL | WLXP | 0.6 |
| ASDA111-NL-NL | Live | 0.75 |
| ASDA111-NL-NL | S | 0.75 |
| ASDA111-NL-NL | NotionalX(DL) | 1 |
| ASDA111-NL-NL | NotionalY(DL) | 1 |
| ASDA111-NL-NL | NotionalX(LL) | 0.75 |
| ASDA111-NL-NL | NotionalY(LL) | 0.75 |
| ASDA113-1-NL-NL | DEAD | 1 |
| ASDA113-1-NL-NL | CRv | 1 |
| ASDA113-1-NL-NL | TL | 1 |
| ASDA113-1-NL-NL | WLYP | -0.6 |
| ASDA113-1-NL-NL | Live | 0.75 |
| ASDA113-1-NL-NL | S | 0.75 |
| ASDA113-1-NL-NL | NotionalX(DL) | 1 |
| ASDA113-1-NL-NL | NotionalY(DL) | 1 |
| ASDA113-1-NL-NL | NotionalX(LL) | 0.75 |
| ASDA113-1-NL-NL | NotionalY(LL) | 0.75 |
| ASDA113-NL-NL | DEAD | 1 |
| ASDA113-NL-NL | CRv | 1 |
| ASDA113-NL-NL | TL | 1 |
| ASDA113-NL-NL | WLXP | -0.6 |
| ASDA113-NL-NL | Live | 0.75 |
| ASDA113-NL-NL | S | 0.75 |
| ASDA113-NL-NL | NotionalX(DL) | 1 |
| ASDA113-NL-NL | NotionalY(DL) | 1 |
| ASDA113-NL-NL | NotionalX(LL) | 0.75 |
| ASDA113-NL-NL | NotionalY(LL) | 0.75 |
| ASDA115-1crane-NL-NL | DEAD | 0.6 |
| ASDA115-1crane-NL-NL | CRv | 0.6 |
| ASDA115-1crane-NL-NL | TL | 1 |
| ASDA115-1crane-NL-NL | FL | 1 |
| ASDA115-1crane-NL-NL | WLYP | 0.6 |
| ASDA115-1crane-NL-NL | NotionalX(DL) | 0.6 |
| ASDA115-1crane-NL-NL | NotionalY(DL) | 0.6 |
| ASDA115crane-NL-NL | DEAD | 0.6 |
| ASDA115crane-NL-NL | CRv | 0.6 |
| ASDA115crane-NL-NL | TL | 1 |
| ASDA115crane-NL-NL | FL | 1 |
| ASDA115crane-NL-NL | WLXP | 0.6 |
| ASDA115crane-NL-NL | NotionalX(DL) | 0.6 |
| ASDA115crane-NL-NL | NotionalY(DL) | 0.6 |
| ASDA116-1crane-NL-NL | DEAD | 0.6 |
| ASDA116-1crane-NL-NL | CRv | 0.6 |
| ASDA116-1crane-NL-NL | TL | 1 |
| ASDA116-1crane-NL-NL | FL | -1 |
| ASDA116-1crane-NL-NL | WLYP | 0.6 |
| ASDA116-1crane-NL-NL | NotionalX(DL) | 0.6 |
| ASDA116-1crane-NL-NL | NotionalY(DL) | 0.6 |
| ASDA116crane-NL-NL | DEAD | 0.6 |
| ASDA116crane-NL-NL | CRv | 0.6 |
| ASDA116crane-NL-NL | TL | 1 |
| ASDA116crane-NL-NL | FL | -1 |
| ASDA116crane-NL-NL | WLXP | 0.6 |
| ASDA116crane-NL-NL | NotionalX(DL) | 0.6 |
| ASDA116crane-NL-NL | NotionalY(DL) | 0.6 |
| ASDA117-1crane-NL-NL | DEAD | 0.6 |
| ASDA117-1crane-NL-NL | CRv | 0.6 |
| ASDA117-1crane-NL-NL | TL | 1 |
| ASDA117-1crane-NL-NL | FL | 1 |
| ASDA117-1crane-NL-NL | WLYP | -0.6 |
| ASDA117-1crane-NL-NL | NotionalX(DL) | 0.6 |
| ASDA117-1crane-NL-NL | NotionalY(DL) | 0.6 |
| ASDA117crane-NL-NL | DEAD | 0.6 |
| ASDA117crane-NL-NL | CRv | 0.6 |
| ASDA117crane-NL-NL | TL | 1 |
| ASDA117crane-NL-NL | FL | 1 |
| ASDA117crane-NL-NL | WLXP | -0.6 |
| ASDA117crane-NL-NL | NotionalX(DL) | 0.6 |
| ASDA117crane-NL-NL | NotionalY(DL) | 0.6 |
| ASDA118-1crane-NL-NL | DEAD | 0.6 |
| ASDA118-1crane-NL-NL | CRv | 0.6 |
| ASDA118-1crane-NL-NL | TL | 1 |
| ASDA118-1crane-NL-NL | FL | -1 |
| ASDA118-1crane-NL-NL | WLYP | -0.6 |
| ASDA118-1crane-NL-NL | NotionalX(DL) | 0.6 |
| ASDA118-1crane-NL-NL | NotionalY(DL) | 0.6 |
| ASDA118crane-NL-NL | DEAD | 0.6 |
| ASDA118crane-NL-NL | CRv | 0.6 |
| ASDA118crane-NL-NL | TL | 1 |
| ASDA118crane-NL-NL | FL | -1 |
| ASDA118crane-NL-NL | WLXP | -0.6 |
| ASDA118crane-NL-NL | NotionalX(DL) | 0.6 |
| ASDA118crane-NL-NL | NotionalY(DL) | 0.6 |
| ASDA119-1-NL-NL | DEAD | 0.6 |
| ASDA119-1-NL-NL | CRv | 0.6 |
| ASDA119-1-NL-NL | TL | 1 |
| ASDA119-1-NL-NL | WLYP | 0.6 |
| ASDA119-1-NL-NL | NotionalX(DL) | 0.6 |
| ASDA119-1-NL-NL | NotionalY(DL) | 0.6 |
| ASDA119-NL-NL | DEAD | 0.6 |
| ASDA119-NL-NL | CRv | 0.6 |
| ASDA119-NL-NL | TL | 1 |
| ASDA119-NL-NL | WLXP | 0.6 |
| ASDA119-NL-NL | NotionalX(DL) | 0.6 |
| ASDA119-NL-NL | NotionalY(DL) | 0.6 |
| ASDA121-1-NL-NL | DEAD | 0.6 |
| ASDA121-1-NL-NL | CRv | 0.6 |
| ASDA121-1-NL-NL | TL | 1 |
| ASDA121-1-NL-NL | WLYP | -0.6 |
| ASDA121-1-NL-NL | NotionalX(DL) | 0.6 |
| ASDA121-1-NL-NL | NotionalY(DL) | 0.6 |
| ASDA121-NL-NL | DEAD | 0.6 |
| ASDA121-NL-NL | CRv | 0.6 |
| ASDA121-NL-NL | TL | 1 |
| ASDA121-NL-NL | WLXP | -0.6 |
| ASDA121-NL-NL | NotionalX(DL) | 0.6 |
| ASDA121-NL-NL | NotionalY(DL) | 0.6 |
| ASDA123-1crane-NL-NL | DEAD | 0.6 |
| ASDA123-1crane-NL-NL | CRv | 0.6 |
| ASDA123-1crane-NL-NL | TL | 1 |
| ASDA123-1crane-NL-NL | FT | 1 |
| ASDA123-1crane-NL-NL | WLYP | 0.6 |
| ASDA123-1crane-NL-NL | NotionalX(DL) | 0.6 |
| ASDA123-1crane-NL-NL | NotionalY(DL) | 0.6 |
| ASDA123crane-NL-NL | DEAD | 0.6 |
| ASDA123crane-NL-NL | CRv | 0.6 |
| ASDA123crane-NL-NL | TL | 1 |
| ASDA123crane-NL-NL | FT | 1 |
| ASDA123crane-NL-NL | WLXP | 0.6 |
| ASDA123crane-NL-NL | NotionalX(DL) | 0.6 |
| ASDA123crane-NL-NL | NotionalY(DL) | 0.6 |
| ASDA124-1crane-NL-NL | DEAD | 0.6 |
| ASDA124-1crane-NL-NL | CRv | 0.6 |
| ASDA124-1crane-NL-NL | TL | 1 |
| ASDA124-1crane-NL-NL | FT | -1 |
| ASDA124-1crane-NL-NL | WLYP | 0.6 |
| ASDA124-1crane-NL-NL | NotionalX(DL) | 0.6 |
| ASDA124-1crane-NL-NL | NotionalY(DL) | 0.6 |
| ASDA124crane-NL-NL | DEAD | 0.6 |
| ASDA124crane-NL-NL | CRv | 0.6 |
| ASDA124crane-NL-NL | TL | 1 |
| ASDA124crane-NL-NL | FT | -1 |
| ASDA124crane-NL-NL | WLXP | 0.6 |
| ASDA124crane-NL-NL | NotionalX(DL) | 0.6 |
| ASDA124crane-NL-NL | NotionalY(DL) | 0.6 |
| ASDA125-1crane-NL-NL | DEAD | 0.6 |
| ASDA125-1crane-NL-NL | CRv | 0.6 |
| ASDA125-1crane-NL-NL | TL | 1 |
| ASDA125-1crane-NL-NL | FT | 1 |
| ASDA125-1crane-NL-NL | WLYP | -0.6 |
| ASDA125-1crane-NL-NL | NotionalX(DL) | 0.6 |
| ASDA125-1crane-NL-NL | NotionalY(DL) | 0.6 |
| ASDA125crane-NL-NL | DEAD | 0.6 |
| ASDA125crane-NL-NL | CRv | 0.6 |
| ASDA125crane-NL-NL | TL | 1 |
| ASDA125crane-NL-NL | FT | 1 |
| ASDA125crane-NL-NL | WLXP | -0.6 |
| ASDA125crane-NL-NL | NotionalX(DL) | 0.6 |
| ASDA125crane-NL-NL | NotionalY(DL) | 0.6 |
| ASDA126-1crane-NL-NL | DEAD | 0.6 |
| ASDA126-1crane-NL-NL | CRv | 0.6 |
| ASDA126-1crane-NL-NL | TL | 1 |
| ASDA126-1crane-NL-NL | FT | -1 |
| ASDA126-1crane-NL-NL | WLYP | -0.6 |
| ASDA126-1crane-NL-NL | NotionalX(DL) | 0.6 |
| ASDA126-1crane-NL-NL | NotionalY(DL) | 0.6 |
| ASDA126crane-NL-NL | DEAD | 0.6 |
| ASDA126crane-NL-NL | CRv | 0.6 |
| ASDA126crane-NL-NL | TL | 1 |
| ASDA126crane-NL-NL | FT | -1 |
| ASDA126crane-NL-NL | WLXP | -0.6 |
| ASDA126crane-NL-NL | NotionalX(DL) | 0.6 |
| ASDA126crane-NL-NL | NotionalY(DL) | 0.6 |
| ASDA127-1-NL-NL | DEAD | 0.6 |
| ASDA127-1-NL-NL | CRv | 0.6 |
| ASDA127-1-NL-NL | TL | 1 |
| ASDA127-1-NL-NL | WLYP | 0.6 |
| ASDA127-1-NL-NL | NotionalX(DL) | 0.6 |
| ASDA127-1-NL-NL | NotionalY(DL) | 0.6 |
| ASDA127-NL-NL | DEAD | 0.6 |
| ASDA127-NL-NL | CRv | 0.6 |
| ASDA127-NL-NL | TL | 1 |
| ASDA127-NL-NL | WLXP | 0.6 |
| ASDA127-NL-NL | NotionalX(DL) | 0.6 |
| ASDA127-NL-NL | NotionalY(DL) | 0.6 |
| ASDA129-1-NL-NL | DEAD | 0.6 |
| ASDA129-1-NL-NL | CRv | 0.6 |
| ASDA129-1-NL-NL | TL | 1 |
| ASDA129-1-NL-NL | WLYP | -0.6 |
| ASDA129-1-NL-NL | NotionalX(DL) | 0.6 |
| ASDA129-1-NL-NL | NotionalY(DL) | 0.6 |
| ASDA129-NL-NL | DEAD | 0.6 |
| ASDA129-NL-NL | CRv | 0.6 |
| ASDA129-NL-NL | TL | 1 |
| ASDA129-NL-NL | WLXP | -0.6 |
| ASDA129-NL-NL | NotionalX(DL) | 0.6 |
| ASDA129-NL-NL | NotionalY(DL) | 0.6 |
| ASDA74-NL-NL | DEAD | 1 |
| ASDA74-NL-NL | CRv | 1 |
| ASDA74-NL-NL | NotionalX(DL) | 1 |
| ASDA74-NL-NL | NotionalY(DL) | 1 |
| ASDA75crane-NL-NL | DEAD | 1 |
| ASDA75crane-NL-NL | CRv | 1 |
| ASDA75crane-NL-NL | Live | 1 |
| ASDA75crane-NL-NL | S | 1 |
| ASDA75crane-NL-NL | TL | 1 |
| ASDA75crane-NL-NL | FL | 1 |
| ASDA75crane-NL-NL | NotionalX(DL) | 1 |
| ASDA75crane-NL-NL | NotionalY(DL) | 1 |
| ASDA75crane-NL-NL | NotionalX(LL) | 1 |
| ASDA75crane-NL-NL | NotionalY(LL) | 1 |
| ASDA76crane-NL-NL | DEAD | 1 |
| ASDA76crane-NL-NL | CRv | 1 |
| ASDA76crane-NL-NL | Live | 1 |
| ASDA76crane-NL-NL | S | 1 |
| ASDA76crane-NL-NL | TL | 1 |
| ASDA76crane-NL-NL | FL | -1 |
| ASDA76crane-NL-NL | NotionalX(DL) | 1 |
| ASDA76crane-NL-NL | NotionalY(DL) | 1 |
| ASDA76crane-NL-NL | NotionalX(LL) | 1 |
| ASDA76crane-NL-NL | NotionalY(LL) | 1 |
| ASDA78-NL-NL | DEAD | 1 |
| ASDA78-NL-NL | CRv | 1 |
| ASDA78-NL-NL | Live | 1 |
| ASDA78-NL-NL | S | 1 |
| ASDA78-NL-NL | TL | 1 |
| ASDA78-NL-NL | NotionalX(DL) | 1 |
| ASDA78-NL-NL | NotionalY(DL) | 1 |
| ASDA78-NL-NL | NotionalX(LL) | 1 |
| ASDA78-NL-NL | NotionalY(LL) | 1 |
| ASDA79crane-NL-NL | DEAD | 1 |
| ASDA79crane-NL-NL | CRv | 1 |
| ASDA79crane-NL-NL | Live | 1 |
| ASDA79crane-NL-NL | S | 1 |
| ASDA79crane-NL-NL | TL | 1 |
| ASDA79crane-NL-NL | FT | 1 |
| ASDA79crane-NL-NL | NotionalX(DL) | 1 |
| ASDA79crane-NL-NL | NotionalY(DL) | 1 |
| ASDA79crane-NL-NL | NotionalX(LL) | 1 |
| ASDA79crane-NL-NL | NotionalY(LL) | 1 |
| ASDA80crane-NL-NL | DEAD | 1 |
| ASDA80crane-NL-NL | CRv | 1 |
| ASDA80crane-NL-NL | Live | 1 |
| ASDA80crane-NL-NL | S | 1 |
| ASDA80crane-NL-NL | TL | 1 |
| ASDA80crane-NL-NL | FT | -1 |
| ASDA80crane-NL-NL | NotionalX(DL) | 1 |
| ASDA80crane-NL-NL | NotionalY(DL) | 1 |
| ASDA80crane-NL-NL | NotionalX(LL) | 1 |
| ASDA80crane-NL-NL | NotionalY(LL) | 1 |
| ASDA82-NL-NL | DEAD | 1 |
| ASDA82-NL-NL | CRv | 1 |
| ASDA82-NL-NL | Live | 1 |
| ASDA82-NL-NL | S | 1 |
| ASDA82-NL-NL | TL | 1 |
| ASDA82-NL-NL | NotionalX(DL) | 1 |
| ASDA82-NL-NL | NotionalY(DL) | 1 |
| ASDA82-NL-NL | NotionalX(LL) | 1 |
| ASDA82-NL-NL | NotionalY(LL) | 1 |
| ASDA83-1crane-NL-NL | DEAD | 1 |
| ASDA83-1crane-NL-NL | CRv | 1 |
| ASDA83-1crane-NL-NL | TL | 1 |
| ASDA83-1crane-NL-NL | FL | 1 |
| ASDA83-1crane-NL-NL | WLYP | 0.6 |
| ASDA83-1crane-NL-NL | NotionalX(DL) | 1 |
| ASDA83-1crane-NL-NL | NotionalY(DL) | 1 |
| ASDA83crane-NL-NL | DEAD | 1 |
| ASDA83crane-NL-NL | CRv | 1 |
| ASDA83crane-NL-NL | TL | 1 |
| ASDA83crane-NL-NL | FL | 1 |
| ASDA83crane-NL-NL | WLXP | 0.6 |
| ASDA83crane-NL-NL | NotionalX(DL) | 1 |
| ASDA83crane-NL-NL | NotionalY(DL) | 1 |
| ASDA84-1crane-NL-NL | DEAD | 1 |
| ASDA84-1crane-NL-NL | CRv | 1 |
| ASDA84-1crane-NL-NL | TL | 1 |
| ASDA84-1crane-NL-NL | FL | -1 |
| ASDA84-1crane-NL-NL | WLYP | 0.6 |
| ASDA84-1crane-NL-NL | NotionalX(DL) | 1 |
| ASDA84-1crane-NL-NL | NotionalY(DL) | 1 |
| ASDA84crane-NL-NL | DEAD | 1 |
| ASDA84crane-NL-NL | CRv | 1 |
| ASDA84crane-NL-NL | TL | 1 |
| ASDA84crane-NL-NL | FL | -1 |
| ASDA84crane-NL-NL | WLXP | 0.6 |
| ASDA84crane-NL-NL | NotionalX(DL) | 1 |
| ASDA84crane-NL-NL | NotionalY(DL) | 1 |
| ASDA85-1crane-NL-NL | DEAD | 1 |
| ASDA85-1crane-NL-NL | CRv | 1 |
| ASDA85-1crane-NL-NL | TL | 1 |
| ASDA85-1crane-NL-NL | FL | 1 |
| ASDA85-1crane-NL-NL | WLYP | -0.6 |
| ASDA85-1crane-NL-NL | NotionalX(DL) | 1 |
| ASDA85-1crane-NL-NL | NotionalY(DL) | 1 |
| ASDA85crane-NL-NL | DEAD | 1 |
| ASDA85crane-NL-NL | CRv | 1 |
| ASDA85crane-NL-NL | TL | 1 |
| ASDA85crane-NL-NL | FL | 1 |
| ASDA85crane-NL-NL | WLXP | -0.6 |
| ASDA85crane-NL-NL | NotionalX(DL) | 1 |
| ASDA85crane-NL-NL | NotionalY(DL) | 1 |
| ASDA86-1crane-NL-NL | DEAD | 1 |
| ASDA86-1crane-NL-NL | CRv | 1 |
| ASDA86-1crane-NL-NL | TL | 1 |
| ASDA86-1crane-NL-NL | FL | -1 |
| ASDA86-1crane-NL-NL | WLYP | -0.6 |
| ASDA86-1crane-NL-NL | NotionalX(DL) | 1 |
| ASDA86-1crane-NL-NL | NotionalY(DL) | 1 |
| ASDA86crane-NL-NL | DEAD | 1 |
| ASDA86crane-NL-NL | CRv | 1 |
| ASDA86crane-NL-NL | TL | 1 |
| ASDA86crane-NL-NL | FL | -1 |
| ASDA86crane-NL-NL | WLXP | -0.6 |
| ASDA86crane-NL-NL | NotionalX(DL) | 1 |
| ASDA86crane-NL-NL | NotionalY(DL) | 1 |
| ASDA87-1-NL-NL | DEAD | 1 |
| ASDA87-1-NL-NL | CRv | 1 |
| ASDA87-1-NL-NL | TL | 1 |
| ASDA87-1-NL-NL | WLYP | 0.6 |
| ASDA87-1-NL-NL | NotionalX(DL) | 1 |
| ASDA87-1-NL-NL | NotionalY(DL) | 1 |
| ASDA87-NL-NL | DEAD | 1 |
| ASDA87-NL-NL | CRv | 1 |
| ASDA87-NL-NL | TL | 1 |
| ASDA87-NL-NL | WLXP | 0.6 |
| ASDA87-NL-NL | NotionalX(DL) | 1 |
| ASDA87-NL-NL | NotionalY(DL) | 1 |
| ASDA89-1-NL-NL | DEAD | 1 |
| ASDA89-1-NL-NL | CRv | 1 |
| ASDA89-1-NL-NL | TL | 1 |
| ASDA89-1-NL-NL | WLYP | -0.6 |
| ASDA89-1-NL-NL | NotionalX(DL) | 1 |
| ASDA89-1-NL-NL | NotionalY(DL) | 1 |
| ASDA89-NL-NL | DEAD | 1 |
| ASDA89-NL-NL | CRv | 1 |
| ASDA89-NL-NL | TL | 1 |
| ASDA89-NL-NL | WLXP | -0.6 |
| ASDA89-NL-NL | NotionalX(DL) | 1 |
| ASDA89-NL-NL | NotionalY(DL) | 1 |
| ASDA91-1crane-NL-NL | DEAD | 1 |
| ASDA91-1crane-NL-NL | CRv | 1 |
| ASDA91-1crane-NL-NL | TL | 1 |
| ASDA91-1crane-NL-NL | FT | 1 |
| ASDA91-1crane-NL-NL | WLYP | 0.6 |
| ASDA91-1crane-NL-NL | NotionalX(DL) | 1 |
| ASDA91-1crane-NL-NL | NotionalY(DL) | 1 |
| ASDA91crane-NL-NL | DEAD | 1 |
| ASDA91crane-NL-NL | CRv | 1 |
| ASDA91crane-NL-NL | TL | 1 |
| ASDA91crane-NL-NL | FT | 1 |
| ASDA91crane-NL-NL | WLXP | 0.6 |
| ASDA91crane-NL-NL | NotionalX(DL) | 1 |
| ASDA91crane-NL-NL | NotionalY(DL) | 1 |
| ASDA92-1crane-NL-NL | DEAD | 1 |
| ASDA92-1crane-NL-NL | CRv | 1 |
| ASDA92-1crane-NL-NL | TL | 1 |
| ASDA92-1crane-NL-NL | FT | -1 |
| ASDA92-1crane-NL-NL | WLYP | 0.6 |
| ASDA92-1crane-NL-NL | NotionalX(DL) | 1 |
| ASDA92-1crane-NL-NL | NotionalY(DL) | 1 |
| ASDA92crane-NL-NL | DEAD | 1 |
| ASDA92crane-NL-NL | CRv | 1 |
| ASDA92crane-NL-NL | TL | 1 |
| ASDA92crane-NL-NL | FT | -1 |
| ASDA92crane-NL-NL | WLXP | 0.6 |
| ASDA92crane-NL-NL | NotionalX(DL) | 1 |
| ASDA92crane-NL-NL | NotionalY(DL) | 1 |
| ASDA93-1crane-NL-NL | DEAD | 1 |
| ASDA93-1crane-NL-NL | CRv | 1 |
| ASDA93-1crane-NL-NL | TL | 1 |
| ASDA93-1crane-NL-NL | FT | 1 |
| ASDA93-1crane-NL-NL | WLYP | -0.6 |
| ASDA93-1crane-NL-NL | NotionalX(DL) | 1 |
| ASDA93-1crane-NL-NL | NotionalY(DL) | 1 |
| ASDA93crane-NL-NL | DEAD | 1 |
| ASDA93crane-NL-NL | CRv | 1 |
| ASDA93crane-NL-NL | TL | 1 |
| ASDA93crane-NL-NL | FT | 1 |
| ASDA93crane-NL-NL | WLXP | -0.6 |
| ASDA93crane-NL-NL | NotionalX(DL) | 1 |
| ASDA93crane-NL-NL | NotionalY(DL) | 1 |
| ASDA94-1crane-NL-NL | DEAD | 1 |
| ASDA94-1crane-NL-NL | CRv | 1 |
| ASDA94-1crane-NL-NL | TL | 1 |
| ASDA94-1crane-NL-NL | FT | -1 |
| ASDA94-1crane-NL-NL | WLYP | -0.6 |
| ASDA94-1crane-NL-NL | NotionalX(DL) | 1 |
| ASDA94-1crane-NL-NL | NotionalY(DL) | 1 |
| ASDA94crane-NL-NL | DEAD | 1 |
| ASDA94crane-NL-NL | CRv | 1 |
| ASDA94crane-NL-NL | TL | 1 |
| ASDA94crane-NL-NL | FT | -1 |
| ASDA94crane-NL-NL | WLXP | -0.6 |
| ASDA94crane-NL-NL | NotionalX(DL) | 1 |
| ASDA94crane-NL-NL | NotionalY(DL) | 1 |
| ASDA95-1-NL-NL | DEAD | 1 |
| ASDA95-1-NL-NL | CRv | 1 |
| ASDA95-1-NL-NL | TL | 1 |
| ASDA95-1-NL-NL | WLYP | 0.6 |
| ASDA95-1-NL-NL | NotionalX(DL) | 1 |
| ASDA95-1-NL-NL | NotionalY(DL) | 1 |
| ASDA95-NL-NL | DEAD | 1 |
| ASDA95-NL-NL | CRv | 1 |
| ASDA95-NL-NL | TL | 1 |
| ASDA95-NL-NL | WLXP | 0.6 |
| ASDA95-NL-NL | NotionalX(DL) | 1 |
| ASDA95-NL-NL | NotionalY(DL) | 1 |
| ASDA97-1-NL-NL | DEAD | 1 |
| ASDA97-1-NL-NL | CRv | 1 |
| ASDA97-1-NL-NL | TL | 1 |
| ASDA97-1-NL-NL | WLYP | -0.6 |
| ASDA97-1-NL-NL | NotionalX(DL) | 1 |
| ASDA97-1-NL-NL | NotionalY(DL) | 1 |
| ASDA97-NL-NL | DEAD | 1 |
| ASDA97-NL-NL | CRv | 1 |
| ASDA97-NL-NL | TL | 1 |
| ASDA97-NL-NL | WLXP | -0.6 |
| ASDA97-NL-NL | NotionalX(DL) | 1 |
| ASDA97-NL-NL | NotionalY(DL) | 1 |
| ASDA99-1crane-NL-NL | DEAD | 1 |
| ASDA99-1crane-NL-NL | CRv | 1 |
| ASDA99-1crane-NL-NL | TL | 1 |
| ASDA99-1crane-NL-NL | FL | 1 |
| ASDA99-1crane-NL-NL | WLYP | 0.6 |
| ASDA99-1crane-NL-NL | Live | 0.75 |
| ASDA99-1crane-NL-NL | S | 0.75 |
| ASDA99-1crane-NL-NL | NotionalX(DL) | 1 |
| ASDA99-1crane-NL-NL | NotionalY(DL) | 1 |
| ASDA99-1crane-NL-NL | NotionalX(LL) | 0.75 |
| ASDA99-1crane-NL-NL | NotionalY(LL) | 0.75 |
| ASDA99crane-NL-NL | DEAD | 1 |
| ASDA99crane-NL-NL | CRv | 1 |
| ASDA99crane-NL-NL | TL | 1 |
| ASDA99crane-NL-NL | FL | 1 |
| ASDA99crane-NL-NL | WLXP | 0.6 |
| ASDA99crane-NL-NL | Live | 0.75 |
| ASDA99crane-NL-NL | S | 0.75 |
| ASDA99crane-NL-NL | NotionalX(DL) | 1 |
| ASDA99crane-NL-NL | NotionalY(DL) | 1 |
| ASDA99crane-NL-NL | NotionalX(LL) | 0.75 |
| ASDA99crane-NL-NL | NotionalY(LL) | 0.75 |
| ASDD131-NL-NL | DEAD | 1 |
| ASDD131-NL-NL | CRv | 1 |
| ASDD131-NL-NL | TL | 1 |
| ASDD131-NL-NL | EQX | 0.7 |
| ASDD131-NL-NL | EQY | 0.21 |
| ASDD131-NL-NL | Ev | 1 |
| ASDD131-NL-NL | NotionalX(DL) | 1 |
| ASDD131-NL-NL | NotionalY(DL) | 1 |
| ASDD132-NL-NL | DEAD | 1 |
| ASDD132-NL-NL | CRv | 1 |
| ASDD132-NL-NL | TL | 1 |
| ASDD132-NL-NL | EQX | -0.7 |
| ASDD132-NL-NL | EQY | 0.21 |
| ASDD132-NL-NL | Ev | 1 |
| ASDD132-NL-NL | NotionalX(DL) | 1 |
| ASDD132-NL-NL | NotionalY(DL) | 1 |
| ASDD133-NL-NL | DEAD | 1 |
| ASDD133-NL-NL | CRv | 1 |
| ASDD133-NL-NL | TL | 1 |
| ASDD133-NL-NL | EQX | 0.7 |
| ASDD133-NL-NL | EQY | -0.21 |
| ASDD133-NL-NL | Ev | 1 |
| ASDD133-NL-NL | NotionalX(DL) | 1 |
| ASDD133-NL-NL | NotionalY(DL) | 1 |
| ASDD134-NL-NL | DEAD | 1 |
| ASDD134-NL-NL | CRv | 1 |
| ASDD134-NL-NL | TL | 1 |
| ASDD134-NL-NL | EQX | -0.7 |
| ASDD134-NL-NL | EQY | -0.21 |
| ASDD134-NL-NL | Ev | 1 |
| ASDD134-NL-NL | NotionalX(DL) | 1 |
| ASDD134-NL-NL | NotionalY(DL) | 1 |
| ASDD135-NL-NL | DEAD | 1 |
| ASDD135-NL-NL | CRv | 1 |
| ASDD135-NL-NL | TL | 1 |
| ASDD135-NL-NL | EQY | 0.7 |
| ASDD135-NL-NL | EQX | 0.21 |
| ASDD135-NL-NL | Ev | 1 |
| ASDD135-NL-NL | NotionalX(DL) | 1 |
| ASDD135-NL-NL | NotionalY(DL) | 1 |
| ASDD136-NL-NL | DEAD | 1 |
| ASDD136-NL-NL | CRv | 1 |
| ASDD136-NL-NL | TL | 1 |
| ASDD136-NL-NL | EQY | -0.7 |
| ASDD136-NL-NL | EQX | 0.21 |
| ASDD136-NL-NL | Ev | 1 |
| ASDD136-NL-NL | NotionalX(DL) | 1 |
| ASDD136-NL-NL | NotionalY(DL) | 1 |
| ASDD137-NL-NL | DEAD | 1 |
| ASDD137-NL-NL | CRv | 1 |
| ASDD137-NL-NL | TL | 1 |
| ASDD137-NL-NL | EQY | 0.7 |
| ASDD137-NL-NL | EQX | -0.21 |
| ASDD137-NL-NL | Ev | 1 |
| ASDD137-NL-NL | NotionalX(DL) | 1 |
| ASDD137-NL-NL | NotionalY(DL) | 1 |
| ASDD138-NL-NL | DEAD | 1 |
| ASDD138-NL-NL | CRv | 1 |
| ASDD138-NL-NL | TL | 1 |
| ASDD138-NL-NL | EQY | -0.7 |
| ASDD138-NL-NL | EQX | -0.21 |
| ASDD138-NL-NL | Ev | 1 |
| ASDD138-NL-NL | NotionalX(DL) | 1 |
| ASDD138-NL-NL | NotionalY(DL) | 1 |
| ASDD139-NL-NL | DEAD | 1 |
| ASDD139-NL-NL | CRv | 1 |
| ASDD139-NL-NL | TL | 1 |
| ASDD139-NL-NL | EQX | 0.525 |
| ASDD139-NL-NL | EQY | 0.1575 |
| ASDD139-NL-NL | Live | 0.75 |
| ASDD139-NL-NL | S | 0.75 |
| ASDD139-NL-NL | Ev | 1 |
| ASDD139-NL-NL | NotionalX(DL) | 1 |
| ASDD139-NL-NL | NotionalY(DL) | 1 |
| ASDD139-NL-NL | NotionalX(LL) | 0.75 |
| ASDD139-NL-NL | NotionalY(LL) | 0.75 |
| ASDD140-NL-NL | DEAD | 1 |
| ASDD140-NL-NL | CRv | 1 |
| ASDD140-NL-NL | TL | 1 |
| ASDD140-NL-NL | EQX | -0.525 |
| ASDD140-NL-NL | EQY | 0.1575 |
| ASDD140-NL-NL | Live | 0.75 |
| ASDD140-NL-NL | S | 0.75 |
| ASDD140-NL-NL | Ev | 1 |
| ASDD140-NL-NL | NotionalX(DL) | 1 |
| ASDD140-NL-NL | NotionalY(DL) | 1 |
| ASDD140-NL-NL | NotionalX(LL) | 0.75 |
| ASDD140-NL-NL | NotionalY(LL) | 0.75 |
| ASDD141-NL-NL | DEAD | 1 |
| ASDD141-NL-NL | CRv | 1 |
| ASDD141-NL-NL | TL | 1 |
| ASDD141-NL-NL | EQX | 0.525 |
| ASDD141-NL-NL | EQY | -0.1575 |
| ASDD141-NL-NL | Live | 0.75 |
| ASDD141-NL-NL | S | 0.75 |
| ASDD141-NL-NL | Ev | 1 |
| ASDD141-NL-NL | NotionalX(DL) | 1 |
| ASDD141-NL-NL | NotionalY(DL) | 1 |
| ASDD141-NL-NL | NotionalX(LL) | 0.75 |
| ASDD141-NL-NL | NotionalY(LL) | 0.75 |
| ASDD142-NL-NL | DEAD | 1 |
| ASDD142-NL-NL | CRv | 1 |
| ASDD142-NL-NL | TL | 1 |
| ASDD142-NL-NL | EQX | -0.525 |
| ASDD142-NL-NL | EQY | -0.1575 |
| ASDD142-NL-NL | Live | 0.75 |
| ASDD142-NL-NL | S | 0.75 |
| ASDD142-NL-NL | Ev | 1 |
| ASDD142-NL-NL | NotionalY(DL) | 1 |
| ASDD142-NL-NL | NotionalX(DL) | 1 |
| ASDD142-NL-NL | NotionalX(LL) | 0.75 |
| ASDD142-NL-NL | NotionalY(LL) | 0.75 |
| ASDD143-NL-NL | DEAD | 1 |
| ASDD143-NL-NL | CRv | 1 |
| ASDD143-NL-NL | TL | 1 |
| ASDD143-NL-NL | EQY | 0.525 |
| ASDD143-NL-NL | EQX | 0.1575 |
| ASDD143-NL-NL | Live | 0.75 |
| ASDD143-NL-NL | S | 0.75 |
| ASDD143-NL-NL | Ev | 1 |
| ASDD143-NL-NL | NotionalX(DL) | 1 |
| ASDD143-NL-NL | NotionalY(DL) | 1 |
| ASDD143-NL-NL | NotionalX(LL) | 0.75 |
| ASDD143-NL-NL | NotionalY(LL) | 0.75 |
| ASDD144-NL-NL | DEAD | 1 |
| ASDD144-NL-NL | CRv | 1 |
| ASDD144-NL-NL | TL | 1 |
| ASDD144-NL-NL | EQY | -0.525 |
| ASDD144-NL-NL | EQX | 0.1575 |
| ASDD144-NL-NL | Live | 0.75 |
| ASDD144-NL-NL | S | 0.75 |
| ASDD144-NL-NL | Ev | 1 |
| ASDD144-NL-NL | NotionalX(DL) | 1 |
| ASDD144-NL-NL | NotionalY(DL) | 1 |
| ASDD144-NL-NL | NotionalX(LL) | 0.75 |
| ASDD144-NL-NL | NotionalY(LL) | 0.75 |
| ASDD145-NL-NL | DEAD | 1 |
| ASDD145-NL-NL | CRv | 1 |
| ASDD145-NL-NL | TL | 1 |
| ASDD145-NL-NL | EQY | 0.525 |
| ASDD145-NL-NL | EQX | -0.1575 |
| ASDD145-NL-NL | Live | 0.75 |
| ASDD145-NL-NL | S | 0.75 |
| ASDD145-NL-NL | Ev | 1 |
| ASDD145-NL-NL | NotionalX(DL) | 1 |
| ASDD145-NL-NL | NotionalY(DL) | 1 |
| ASDD145-NL-NL | NotionalX(LL) | 0.75 |
| ASDD145-NL-NL | NotionalY(LL) | 0.75 |
| ASDD146-NL-NL | DEAD | 1 |
| ASDD146-NL-NL | CRv | 1 |
| ASDD146-NL-NL | TL | 1 |
| ASDD146-NL-NL | EQY | -0.525 |
| ASDD146-NL-NL | EQX | -0.1575 |
| ASDD146-NL-NL | Live | 0.75 |
| ASDD146-NL-NL | S | 0.75 |
| ASDD146-NL-NL | Ev | 1 |
| ASDD146-NL-NL | NotionalX(DL) | 1 |
| ASDD146-NL-NL | NotionalY(DL) | 1 |
| ASDD146-NL-NL | NotionalX(LL) | 0.75 |
| ASDD146-NL-NL | NotionalY(LL) | 0.75 |
| ASDD147-NL-NL | DEAD | 0.6 |
| ASDD147-NL-NL | CRv | 0.6 |
| ASDD147-NL-NL | TL | 1 |
| ASDD147-NL-NL | EQX | 0.7 |
| ASDD147-NL-NL | EQY | 0.21 |
| ASDD147-NL-NL | Ev | 1 |
| ASDD147-NL-NL | NotionalX(DL) | 0.6 |
| ASDD147-NL-NL | NotionalY(DL) | 0.6 |
| ASDD148-NL-NL | DEAD | 0.6 |
| ASDD148-NL-NL | CRv | 0.6 |
| ASDD148-NL-NL | TL | 1 |
| ASDD148-NL-NL | EQX | -0.7 |
| ASDD148-NL-NL | EQY | 0.21 |
| ASDD148-NL-NL | Ev | 1 |
| ASDD148-NL-NL | NotionalX(DL) | 0.6 |
| ASDD148-NL-NL | NotionalY(DL) | 0.6 |
| ASDD149-NL-NL | DEAD | 0.6 |
| ASDD149-NL-NL | CRv | 0.6 |
| ASDD149-NL-NL | TL | 1 |
| ASDD149-NL-NL | EQX | 0.7 |
| ASDD149-NL-NL | EQY | -0.21 |
| ASDD149-NL-NL | Ev | 1 |
| ASDD149-NL-NL | NotionalX(DL) | 0.6 |
| ASDD149-NL-NL | NotionalY(DL) | 0.6 |
| ASDD150-NL-NL | DEAD | 0.6 |
| ASDD150-NL-NL | CRv | 0.6 |
| ASDD150-NL-NL | TL | 1 |
| ASDD150-NL-NL | EQX | -0.7 |
| ASDD150-NL-NL | EQY | -0.21 |
| ASDD150-NL-NL | Ev | 1 |
| ASDD150-NL-NL | NotionalX(DL) | 0.6 |
| ASDD150-NL-NL | NotionalY(DL) | 0.6 |
| ASDD151-NL-NL | DEAD | 0.6 |
| ASDD151-NL-NL | CRv | 0.6 |
| ASDD151-NL-NL | TL | 1 |
| ASDD151-NL-NL | EQY | 0.7 |
| ASDD151-NL-NL | EQX | 0.21 |
| ASDD151-NL-NL | Ev | 1 |
| ASDD151-NL-NL | NotionalX(DL) | 0.6 |
| ASDD151-NL-NL | NotionalY(DL) | 0.6 |
| ASDD152-NL-NL | DEAD | 0.6 |
| ASDD152-NL-NL | CRv | 0.6 |
| ASDD152-NL-NL | TL | 1 |
| ASDD152-NL-NL | EQY | -0.7 |
| ASDD152-NL-NL | EQX | 0.21 |
| ASDD152-NL-NL | Ev | 1 |
| ASDD152-NL-NL | NotionalX(DL) | 0.6 |
| ASDD152-NL-NL | NotionalY(DL) | 0.6 |
| ASDD153-NL-NL | DEAD | 0.6 |
| ASDD153-NL-NL | CRv | 0.6 |
| ASDD153-NL-NL | TL | 1 |
| ASDD153-NL-NL | EQY | 0.7 |
| ASDD153-NL-NL | EQX | -0.21 |
| ASDD153-NL-NL | Ev | 1 |
| ASDD153-NL-NL | NotionalX(DL) | 0.6 |
| ASDD153-NL-NL | NotionalY(DL) | 0.6 |
| ASDD154-NL-NL | DEAD | 0.6 |
| ASDD154-NL-NL | CRv | 0.6 |
| ASDD154-NL-NL | TL | 1 |
| ASDD154-NL-NL | EQY | -0.7 |
| ASDD154-NL-NL | EQX | -0.21 |
| ASDD154-NL-NL | Ev | 1 |
| ASDD154-NL-NL | NotionalX(DL) | 0.6 |
| ASDD154-NL-NL | NotionalY(DL) | 0.6 |

Figure 42- DEFORMED SHAPE (ENV COM – CM)

The maximum deformation of the foundation is 0.27 cm, the deformation shown is much less than 5 cm.

Figure 43- SOIL STRESS UNDER THE FOUNDATION

The maximum soil stress under the foundation is 0.3 kg/cm^2.

Figure 44- X DIRECTION REINFORCEMENT DESIGN

Use Ø16@20cm

Figure 45- Y DIRECTION REINFORCEMENT DESIGN

Use Ø16@20cm