## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-PPL-PEDCO-320-IN-DW-0001 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1061 |  |  | Transmital Date: 11-JUN-2022
Document Title: Typical Instrument Installation Drawing |  |  |  |  | PEDCO Tr. No.:BK-PEDCO-NISOC-0005-IN-TR-1061 |  |  | Transmital Date: 11-Jun-2022
[5 empty] | CRS No: PEDCO-CRS-BK-PPL-PEDCO-320-IN-DW-0001_D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | سايز stand pipe ها، 3" در نظر گرفته شود |  | BK-SUR-ENG- INS-01-04839 | 2022-06-22 | مدرک به صورت کامل و با توجه به تجهیزات لازم در بسته کاری بروزرسانی گردید.
2 | نحوه اتصال به زمين كردن Tray ها بر اساس استاندارد IPS-E-In-190 بررسي و در مدرك منعكس گردد. |  | BK-SUR-ENG- INS-01-04839 | 2022-06-22
3 | الزامات IPS جهت جهت جداسازي انواع مختلف سيگنال در نظر گرفته شود |  | BK-SUR-ENG- INS-01-04839 | 2022-06-22
4 | الزامات IPS براي كاندوئيت ها جهت انتقال سيگنال الكتريكي در نظر گرفته شود. |  | BK-SUR-ENG- INS-01-04839 | 2022-06-22
5 | با توجه به امكان تغيير مدارك مرتبط و بند 13 قرارداد، مسئوليت مالي و زماني تمامي موارد بر عهده پيمانكار مرتبط مي باشد. |  | BK-SUR-ENG- INS-01-04839 | 2022-06-22 | ملاحظه گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: |  |  |  |  | Date: