## Sheet1
N.I.S.O.C |  | Binak Project
REPLY SHEET
Document No: BK-GCS-PEDCO-120-EL-SL-0004 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-2179 |  |  | Transmital Date: 6/7/2023
Document Title: Distribution & Lighting Panels Single Line Diagram |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0201-EL-TR-2179 |  |  | Transmital Date: 6/7/2023
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-EL-SL-0004_D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | کابل های عبوری از مناطق فرآیندی مربوط به تغذیه اصلی تابلو های توزیع روشنایی می بایست بصورت روکش دار سربی انتخاب گردند. |  | 1402-2294-162057 | 1402/04/26 | در مدرک لیست کابل، ذکر شده است که کابلهای ناحیه فرآیندی با روکش غلاف سربی می باشد. همچنین در جدول مربوط به هر تابلوی توزیع، مشخصات کابل ورودی عنوان شده است.
2 | محل استفاده تابلو های روشنایی در پایین هر صفحه درج گردد. |  | 1402-2294-162057 | 1402/04/26 | اعمال گردیده است.
3 | عملکرد ترموستات نصب شده در تابلو های روشنایی اصلاح و در بخش Legend نقشه نیز درج گردد. |  | 1402-2294-162057 | 1402/04/26 | در لجند اضافه شده و نحوه عملکرد آن اصلاح گردید. لازم به ذکر است با توجه به رطوبت منطقه از هیگروستات به جای ترموستات استفاده شده است.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: |  |  |  |  | Date: