## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-IN-BD-0001 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-2511 |  |  | Transmital Date:11/26/2023
Document Title: Control/ESD/F&G System Block Diagram Configuration |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-IN-TR-2511 |  |  | Transmital Date: 11/26/2023
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-PEDCO-120-IN-BD-0001_D07 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | Connection from this package to F&G and from ESD to be shown. |  | BK-SUR-ENG-INS-02-08202 | 2023-08-01 | ارتباطی با سیستم ESD وجود ندارد.
2 | Type of package to be added. |  | BK-SUR-ENG-INS-02-08202 | 2023-08-01 | تایپ پکیج از نوع A میباشد و اضافه گردید.
D07
1 | ارتباط بین LCP برای Electr Gas Compressor و MCC در مدرک در نظر گرفته شود |  | BK-SUR-ENG-INS-02-08881 | 2023-12-13 | بین UCP و MCC ارتباط لازم دیده شده است. لازم به ذکر است که ارتباط تغذیه برقی بین LCP و MCC وجود دارد که در مدارک بخش برق قابل مشاهده است.
2 | ارتباط بین LCP برای Dehydration Burner و MCC در مدرک در نظر گرفته شود |  | BK-SUR-ENG-INS-02-08881 | 2023-12-13
3 | ارتباط بین Field و UCP برای پکیج Dehydration در مدرک در نظر گرفته شود. |  | BK-SUR-ENG-INS-02-08881 | 2023-12-13 | در مدرک در نظر گرفته شده است.
4 | ارتباط بین Field و UCP برای پکیج Compressor در مدرک در نظر گرفته شود. |  | BK-SUR-ENG-INS-02-08881 | 2023-12-13 | با توجه به تاکید کارفرما بر نمایش سه تایی LCP ها , UCP ها در پکیج کمپرسور، نمایش جزئیات در این مدرک به سختی امکان پذیر است. لذا تنها برای رفع ابهام نوت لازم برای رجوع به مدارک سازنده اضافه شد.
5 | برای پکیج Dehydration ارتباط HW بررسی و اضافه گردد. |  | BK-SUR-ENG-INS-02-08881 | 2023-12-13 | مدرک اصلاح گردید.
6 | ارتباط بین Flare LCP و ESD در مدرک مشخص شود. |  | BK-SUR-ENG-INS-02-08881 | 2023-12-13 | مدرک اصلاح گردید.
7 | ارتباط بین N2و Air و ESD در مدرک مشخص شود. |  | BK-SUR-ENG-INS-02-08881 | 2023-12-13 | مدرک اصلاح گردید.
8 | لپ تاپ برای انواع پکیج ها مشخص گردد. |  | BK-SUR-ENG-INS-02-08881 | 2023-12-13 | مدرک اصلاح گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: |  |  |  |  | Date: